## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_406-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_406-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_406-1_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_406-1_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_406-1_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_406-1_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_406-1_0_3_node_274 | 0.4 | n |  | TRUE
7 | bus_LV_406-1_0_3_node_275 | 0.4 | n |  | TRUE
8 | bus_LV_406-1_0_3_node_270 | 0.4 | n |  | TRUE
9 | bus_LV_406-1_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_406-1_0_3_node_273 | 0.4 | n |  | TRUE
11 | bus_LV_406-1_0_3_node_86 | 0.4 | n |  | TRUE
12 | bus_LV_406-1_0_3_node_262 | 0.4 | n |  | TRUE
13 | bus_LV_406-1_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_406-1_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_406-1_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_406-1_0_3_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_406-1_0_3_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_406-1_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_406-1_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_406-1_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_406-1_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_406-1_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_406-1_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_406-1_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_406-1_0_3_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_406-1_0_3_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_406-1_0_3_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_406-1_0_3_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_406-1_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_406-1_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_406-1_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_406-1_0_3_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_406-1_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_406-1_0_3_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_406-1_0_3_node_282 | 0.4 | n |  | TRUE
36 | bus_LV_406-1_0_3_node_60 | 0.4 | n |  | TRUE
37 | bus_LV_406-1_0_3_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_406-1_0_3_node_128 | 0.4 | n |  | TRUE
39 | bus_LV_406-1_0_3_node_130 | 0.4 | n |  | TRUE
40 | bus_LV_406-1_0_3_node_129 | 0.4 | n |  | TRUE
41 | bus_LV_406-1_0_3_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_406-1_0_3_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_406-1_0_3_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_406-1_0_3_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_406-1_0_3_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_406-1_0_3_node_163 | 0.4 | n |  | TRUE
47 | bus_LV_406-1_0_3_node_131 | 0.4 | n |  | TRUE
48 | bus_LV_406-1_0_3_node_92 | 0.4 | n |  | TRUE
49 | bus_LV_406-1_0_3_node_133 | 0.4 | n |  | TRUE
50 | bus_LV_406-1_0_3_node_162 | 0.4 | n |  | TRUE
51 | bus_LV_406-1_0_3_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_406-1_0_3_node_59 | 0.4 | n |  | TRUE
53 | bus_LV_406-1_0_3_node_61 | 0.4 | n |  | TRUE
54 | bus_LV_406-1_0_3_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_406-1_0_3_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_406-1_0_3_node_78 | 0.4 | n |  | TRUE
57 | bus_LV_406-1_0_3_node_69 | 0.4 | n |  | TRUE
58 | bus_LV_406-1_0_3_node_65 | 0.4 | n |  | TRUE
59 | bus_LV_406-1_0_3_node_76 | 0.4 | n |  | TRUE
60 | bus_LV_406-1_0_3_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_406-1_0_3_node_87 | 0.4 | n |  | TRUE
62 | bus_LV_406-1_0_3_node_66 | 0.4 | n |  | TRUE
63 | bus_LV_406-1_0_3_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_406-1_0_3_node_67 | 0.4 | n |  | TRUE
65 | bus_LV_406-1_0_3_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_406-1_0_3_node_79 | 0.4 | n |  | TRUE
67 | bus_LV_406-1_0_3_node_277 | 0.4 | n |  | TRUE
68 | bus_LV_406-1_0_3_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_406-1_0_3_node_279 | 0.4 | n |  | TRUE
70 | bus_LV_406-1_0_3_node_276 | 0.4 | n |  | TRUE
71 | bus_LV_406-1_0_3_node_88 | 0.4 | n |  | TRUE
72 | bus_LV_406-1_0_3_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_406-1_0_3_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_406-1_0_3_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_406-1_0_3_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_406-1_0_3_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_406-1_0_3_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_406-1_0_3_node_288 | 0.4 | n |  | TRUE
79 | bus_LV_406-1_0_3_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_406-1_0_3_node_287 | 0.4 | n |  | TRUE
81 | bus_LV_406-1_0_3_node_283 | 0.4 | n |  | TRUE
82 | bus_LV_406-1_0_3_node_286 | 0.4 | n |  | TRUE
83 | bus_LV_406-1_0_3_node_284 | 0.4 | n |  | TRUE
84 | bus_LV_406-1_0_3_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_406-1_0_3_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_406-1_0_3_node_239 | 0.4 | n |  | TRUE
87 | bus_LV_406-1_0_3_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_406-1_0_3_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_406-1_0_3_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_406-1_0_3_node_289 | 0.4 | n |  | TRUE
91 | bus_LV_406-1_0_3_node_240 | 0.4 | n |  | TRUE
92 | bus_LV_406-1_0_3_node_241 | 0.4 | n |  | TRUE
93 | bus_LV_406-1_0_3_node_232 | 0.4 | n |  | TRUE
94 | bus_LV_406-1_0_3_node_233 | 0.4 | n |  | TRUE
95 | bus_LV_406-1_0_3_node_290 | 0.4 | n |  | TRUE
96 | bus_LV_406-1_0_3_node_125 | 0.4 | n |  | TRUE
97 | bus_LV_406-1_0_3_node_126 | 0.4 | n |  | TRUE
98 | bus_LV_406-1_0_3_node_127 | 0.4 | n |  | TRUE
99 | bus_LV_406-1_0_3_node_316 | 0.4 | n |  | TRUE
100 | bus_LV_406-1_0_3_node_134 | 0.4 | n |  | TRUE
101 | bus_LV_406-1_0_3_node_135 | 0.4 | n |  | TRUE
102 | bus_LV_406-1_0_3_node_137 | 0.4 | n |  | TRUE
103 | bus_LV_406-1_0_3_node_139 | 0.4 | n |  | TRUE
104 | bus_LV_406-1_0_3_node_140 | 0.4 | n |  | TRUE
105 | bus_LV_406-1_0_3_node_144 | 0.4 | n |  | TRUE
106 | bus_LV_406-1_0_3_node_148 | 0.4 | n |  | TRUE
107 | bus_LV_406-1_0_3_node_141 | 0.4 | n |  | TRUE
108 | bus_LV_406-1_0_3_node_142 | 0.4 | n |  | TRUE
109 | bus_LV_406-1_0_3_node_143 | 0.4 | n |  | TRUE
110 | bus_LV_406-1_0_3_node_145 | 0.4 | n |  | TRUE
111 | bus_LV_406-1_0_3_node_146 | 0.4 | n |  | TRUE
112 | bus_LV_406-1_0_3_node_321 | 0.4 | n |  | TRUE
113 | bus_LV_406-1_0_3_node_301 | 0.4 | n |  | TRUE
114 | bus_LV_406-1_0_3_node_147 | 0.4 | n |  | TRUE
115 | bus_LV_406-1_0_3_node_299 | 0.4 | n |  | TRUE
116 | bus_LV_406-1_0_3_node_149 | 0.4 | n |  | TRUE
117 | bus_LV_406-1_0_3_node_168 | 0.4 | n |  | TRUE
118 | bus_LV_406-1_0_3_node_169 | 0.4 | n |  | TRUE
119 | bus_LV_406-1_0_3_node_170 | 0.4 | n |  | TRUE
120 | bus_LV_406-1_0_3_node_172 | 0.4 | n |  | TRUE
121 | bus_LV_406-1_0_3_node_173 | 0.4 | n |  | TRUE
122 | bus_LV_406-1_0_3_node_190 | 0.4 | n |  | TRUE
123 | bus_LV_406-1_0_3_node_211 | 0.4 | n |  | TRUE
124 | bus_LV_406-1_0_3_node_221 | 0.4 | n |  | TRUE
125 | bus_LV_406-1_0_3_node_212 | 0.4 | n |  | TRUE
126 | bus_LV_406-1_0_3_node_210 | 0.4 | n |  | TRUE
127 | bus_LV_406-1_0_3_node_222 | 0.4 | n |  | TRUE
128 | bus_LV_406-1_0_3_node_219 | 0.4 | n |  | TRUE
129 | bus_LV_406-1_0_3_node_220 | 0.4 | n |  | TRUE
130 | bus_LV_406-1_0_3_node_242 | 0.4 | n |  | TRUE
131 | bus_LV_406-1_0_3_node_209 | 0.4 | n |  | TRUE
132 | bus_LV_406-1_0_3_node_230 | 0.4 | n |  | TRUE
133 | bus_LV_406-1_0_3_node_207 | 0.4 | n |  | TRUE
134 | bus_LV_406-1_0_3_node_208 | 0.4 | n |  | TRUE
135 | bus_LV_406-1_0_3_node_235 | 0.4 | n |  | TRUE
136 | bus_LV_406-1_0_3_node_234 | 0.4 | n |  | TRUE
137 | bus_LV_406-1_0_3_node_227 | 0.4 | n |  | TRUE
138 | bus_LV_406-1_0_3_node_228 | 0.4 | n |  | TRUE
139 | bus_LV_406-1_0_3_node_229 | 0.4 | n |  | TRUE
140 | bus_LV_406-1_0_3_node_231 | 0.4 | n |  | TRUE
141 | bus_LV_406-1_0_3_node_238 | 0.4 | n |  | TRUE
142 | bus_LV_406-1_0_3_node_236 | 0.4 | n |  | TRUE
143 | bus_LV_406-1_0_3_node_237 | 0.4 | n |  | TRUE
144 | bus_LV_406-1_0_3_node_260 | 0.4 | n |  | TRUE
145 | bus_LV_406-1_0_3_node_261 | 0.4 | n |  | TRUE
146 | bus_LV_406-1_0_3_node_263 | 0.4 | n |  | TRUE
147 | bus_LV_406-1_0_3_node_264 | 0.4 | n |  | TRUE
148 | bus_LV_406-1_0_3_node_265 | 0.4 | n |  | TRUE
149 | bus_LV_406-1_0_3_node_271 | 0.4 | n |  | TRUE
150 | bus_LV_406-1_0_3_node_272 | 0.4 | n |  | TRUE
151 | bus_LV_406-1_0_3_node_266 | 0.4 | n |  | TRUE
152 | bus_LV_406-1_0_3_node_267 | 0.4 | n |  | TRUE
153 | bus_LV_406-1_0_3_node_268 | 0.4 | n |  | TRUE
154 | bus_LV_406-1_0_3_node_269 | 0.4 | n |  | TRUE
155 | bus_LV_406-1_0_3_node_278 | 0.4 | n |  | TRUE
156 | bus_LV_406-1_0_3_node_280 | 0.4 | n |  | TRUE
157 | bus_LV_406-1_0_3_node_281 | 0.4 | n |  | TRUE
158 | bus_LV_406-1_0_3_node_285 | 0.4 | n |  | TRUE
159 | bus_LV_406-1_0_3_node_291 | 0.4 | n |  | TRUE
160 | bus_LV_406-1_0_3_node_292 | 0.4 | n |  | TRUE
161 | bus_LV_406-1_0_3_node_300 | 0.4 | n |  | TRUE
162 | bus_LV_406-1_0_3_node_298 | 0.4 | n |  | TRUE
163 | bus_LV_406-1_0_3_node_295 | 0.4 | n |  | TRUE
164 | bus_LV_406-1_0_3_node_293 | 0.4 | n |  | TRUE
165 | bus_LV_406-1_0_3_node_294 | 0.4 | n |  | TRUE
166 | bus_LV_406-1_0_3_node_296 | 0.4 | n |  | TRUE
167 | bus_LV_406-1_0_3_node_297 | 0.4 | n |  | TRUE
168 | bus_MV_181_0_node_216 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_406-1_0_3_load_0 | 0 | 0.00076195 | 0.00019096 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_406-1_0_3_load_5 | 4 | 0.00091708 | 0.00022984 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_406-1_0_3_load_6 | 5 | 0.0017864 | 0.00044772 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_406-1_0_3_load_274 | 6 | 0.00066103 | 0.00016567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_406-1_0_3_load_275 | 7 | 0.00060301 | 0.00015113 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_406-1_0_3_load_270 | 8 | 0.0003759 | 9.4209e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_406-1_0_3_load_273 | 10 | 0.00034175 | 8.565e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_406-1_0_3_load_86 | 11 | 0.0020526 | 0.00051443 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_406-1_0_3_load_262 | 12 | 0.00075437 | 0.00018906 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_406-1_0_3_load_8 | 13 | 0.00092941 | 0.00023293 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_406-1_0_3_load_10 | 14 | 0.00088681 | 0.00022226 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_406-1_0_3_load_21 | 17 | 0.00031016 | 7.7734e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_406-1_0_3_load_18 | 18 | 0.00040267 | 0.00010092 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_406-1_0_3_load_12 | 19 | 0.0026984 | 0.0006763 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_406-1_0_3_load_13 | 20 | 0.00081853 | 0.00020514 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_406-1_0_3_load_16 | 23 | 0.0034419 | 0.00086262 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_406-1_0_3_load_17 | 24 | 0.0012077 | 0.00030268 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_406-1_0_3_load_51 | 27 | 0.0012231 | 0.00030653 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_406-1_0_3_load_30 | 28 | 0.00073509 | 0.00018423 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_406-1_0_3_load_27 | 29 | 0.00031372 | 7.8626e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_406-1_0_3_load_25 | 30 | 0.012189 | 0.0030548 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_406-1_0_3_load_26 | 31 | 0.0056561 | 0.0014176 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_406-1_0_3_load_52 | 32 | 0.00094835 | 0.00023768 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_406-1_0_3_load_28 | 33 | 0.0010195 | 0.0002555 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_406-1_0_3_load_282 | 35 | 0.0058924 | 0.0014768 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_406-1_0_3_load_128 | 38 | 0.00046322 | 0.00011609 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_406-1_0_3_load_130 | 39 | 0.00017587 | 4.4076e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_406-1_0_3_load_129 | 40 | 0.0014401 | 0.00036092 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_406-1_0_3_load_53 | 41 | 0.0012087 | 0.00030293 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_406-1_0_3_load_54 | 42 | 0.001966 | 0.00049273 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_406-1_0_3_load_57 | 45 | 0.001077 | 0.00026992 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_406-1_0_3_load_131 | 47 | 0.00028959 | 7.2578e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_406-1_0_3_load_92 | 48 | 0.00073728 | 0.00018478 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_406-1_0_3_load_133 | 49 | 0.0008794 | 0.0002204 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_406-1_0_3_load_162 | 50 | 0.00078213 | 0.00019602 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_406-1_0_3_load_58 | 51 | 0.0014462 | 0.00036244 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_406-1_0_3_load_59 | 52 | 0.00069343 | 0.00017379 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_406-1_0_3_load_61 | 53 | 0.00067583 | 0.00016938 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_406-1_0_3_load_63 | 55 | 0.0011323 | 0.00028377 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_406-1_0_3_load_78 | 56 | 0.0016046 | 0.00040214 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_406-1_0_3_load_69 | 57 | 0.00099602 | 0.00024963 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_406-1_0_3_load_65 | 58 | 0.0040606 | 0.0010177 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_406-1_0_3_load_76 | 59 | 0.0010244 | 0.00025674 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_406-1_0_3_load_82 | 60 | 0.0015814 | 0.00039634 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_406-1_0_3_load_67 | 64 | 0.001862 | 0.00046666 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_406-1_0_3_load_68 | 65 | 0.0019658 | 0.00049268 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_406-1_0_3_load_79 | 66 | 0.0014489 | 0.00036313 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_406-1_0_3_load_279 | 69 | 0.0011454 | 0.00028706 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_406-1_0_3_load_276 | 70 | 0.0013779 | 0.00034534 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_406-1_0_3_load_88 | 71 | 0.00036272 | 9.0905e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_406-1_0_3_load_89 | 72 | 0.0014764 | 0.00037003 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_406-1_0_3_load_70 | 73 | 0.0038355 | 0.00096126 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_406-1_0_3_load_71 | 74 | 0.00056704 | 0.00014211 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_406-1_0_3_load_73 | 76 | 0.0014801 | 0.00037094 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_406-1_0_3_load_75 | 77 | 0.0010266 | 0.0002573 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_406-1_0_3_load_288 | 78 | 0.0017074 | 0.00042793 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_406-1_0_3_load_77 | 79 | 0.0034209 | 0.00085735 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_406-1_0_3_load_287 | 80 | 0.001139 | 0.00028545 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_406-1_0_3_load_283 | 81 | 0.00097673 | 0.00024479 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_406-1_0_3_load_286 | 82 | 0.0011407 | 0.00028589 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_406-1_0_3_load_284 | 83 | 0.00086436 | 0.00021663 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_406-1_0_3_load_81 | 84 | 0.0012505 | 0.00031341 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_406-1_0_3_load_85 | 85 | 0.0012514 | 0.00031362 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_406-1_0_3_load_83 | 87 | 0.0014671 | 0.00036768 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_406-1_0_3_load_84 | 88 | 0.0012473 | 0.00031259 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_406-1_0_3_load_90 | 89 | 0.0012403 | 0.00031086 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_406-1_0_3_load_289 | 90 | 0.0028484 | 0.00071388 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_406-1_0_3_load_240 | 91 | 0.0019382 | 0.00048575 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_406-1_0_3_load_232 | 93 | 0.0017564 | 0.0004402 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_406-1_0_3_load_125 | 96 | 0.00021704 | 5.4395e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_406-1_0_3_load_316 | 99 | 6.1605e-05 | 1.544e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_406-1_0_3_load_134 | 100 | 9.1497e-05 | 2.2931e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_406-1_0_3_load_135 | 101 | 0.00065143 | 0.00016326 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_406-1_0_3_load_139 | 103 | 0.00010567 | 2.6482e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_406-1_0_3_load_140 | 104 | 0.00011599 | 2.9071e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_406-1_0_3_load_141 | 107 | 0.00062055 | 0.00015552 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_406-1_0_3_load_142 | 108 | 0.00039772 | 9.9679e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_406-1_0_3_load_321 | 112 | 6.8086e-05 | 1.7064e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_406-1_0_3_load_301 | 113 | 0.0030055 | 0.00075324 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_406-1_0_3_load_147 | 114 | 0.00011055 | 2.7706e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_406-1_0_3_load_149 | 116 | 0.00017684 | 4.4321e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_406-1_0_3_load_168 | 117 | 0.00030742 | 7.7046e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_406-1_0_3_load_170 | 119 | 0.001137 | 0.00028496 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_406-1_0_3_load_172 | 120 | 0.0013361 | 0.00033486 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_406-1_0_3_load_173 | 121 | 0.00074483 | 0.00018667 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_406-1_0_3_load_221 | 124 | 0.00018815 | 4.7155e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_406-1_0_3_load_212 | 125 | 0.00027767 | 6.9591e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_406-1_0_3_load_210 | 126 | 0.00046789 | 0.00011726 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_406-1_0_3_load_222 | 127 | 0.0013783 | 0.00034542 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_406-1_0_3_load_220 | 129 | 0.00029175 | 7.3121e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_406-1_0_3_load_242 | 130 | 0.00049693 | 0.00012454 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_406-1_0_3_load_209 | 131 | 0.00072546 | 0.00018182 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_406-1_0_3_load_207 | 133 | 0.00029209 | 7.3204e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_406-1_0_3_load_235 | 135 | 0.00090212 | 0.00022609 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_406-1_0_3_load_227 | 137 | 0.00016287 | 4.082e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_406-1_0_3_load_228 | 138 | 0.0011526 | 0.00028887 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_406-1_0_3_load_229 | 139 | 0.00023374 | 5.858e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_406-1_0_3_load_236 | 142 | 0.00049792 | 0.00012479 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_406-1_0_3_load_237 | 143 | 0.00074011 | 0.00018549 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_406-1_0_3_load_260 | 144 | 0.00072145 | 0.00018081 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_406-1_0_3_load_261 | 145 | 0.00037418 | 9.3779e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_406-1_0_3_load_263 | 146 | 0.00075027 | 0.00018803 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_406-1_0_3_load_264 | 147 | 0.00079436 | 0.00019908 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_406-1_0_3_load_265 | 148 | 0.0006008 | 0.00015057 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_406-1_0_3_load_271 | 149 | 0.0010622 | 0.0002662 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_406-1_0_3_load_272 | 150 | 0.00082886 | 0.00020773 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_406-1_0_3_load_266 | 151 | 0.00096077 | 0.00024079 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_406-1_0_3_load_278 | 155 | 0.00089075 | 0.00022324 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_406-1_0_3_load_280 | 156 | 0.00079342 | 0.00019885 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_406-1_0_3_load_281 | 157 | 0.00075953 | 0.00019036 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_406-1_0_3_load_285 | 158 | 0.0016811 | 0.00042131 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_406-1_0_3_load_300 | 161 | 0.00067653 | 0.00016956 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_406-1_0_3_load_298 | 162 | 0.0013387 | 0.00033552 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_406-1_0_3_load_295 | 163 | 0.001106 | 0.00027718 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_406-1_0_3_load_293 | 164 | 0.0013323 | 0.00033389 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_406-1_0_3_load_296 | 166 | 0.00027632 | 6.9252e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_406-1_0_3_load_297 | 167 | 0.00072248 | 0.00018107 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_406-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_406-1_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.23881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_406-1_0_3_line_2 | NAYY 4x150 SE | 2 | 6 | 0.022472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_406-1_0_3_line_3 | NAYY 4x150 SE | 2 | 7 | 0.013822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_406-1_0_3_line_4 | NAYY 4x150 SE | 2 | 8 | 0.053501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_406-1_0_3_line_5 | NAYY 4x150 SE | 3 | 4 | 0.056904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_406-1_0_3_line_6 | NAYY 4x150 SE | 3 | 5 | 0.028919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_406-1_0_3_line_7 | NAYY 4x150 SE | 4 | 9 | 0.020802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_406-1_0_3_line_8 | NAYY 4x150 SE | 6 | 10 | 0.033198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_406-1_0_3_line_9 | NAYY 4x150 SE | 7 | 11 | 0.034847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_406-1_0_3_line_10 | NAYY 4x150 SE | 8 | 12 | 0.020061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_406-1_0_3_line_11 | NAYY 4x150 SE | 9 | 13 | 0.10793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_406-1_0_3_line_12 | NAYY 4x150 SE | 10 | 154 | 0.0068367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_406-1_0_3_line_13 | NAYY 4x150 SE | 12 | 145 | 0.016312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_406-1_0_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.020832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_406-1_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.18148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_406-1_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.081476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_406-1_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.011894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_406-1_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.04279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_406-1_0_3_line_19 | NAYY 4x150 SE | 17 | 22 | 0.036139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_406-1_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.02826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_406-1_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.19392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_406-1_0_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.060554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_406-1_0_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.026193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_406-1_0_3_line_24 | NAYY 4x150 SE | 21 | 24 | 0.03444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_406-1_0_3_line_25 | NAYY 4x150 SE | 22 | 25 | 0.045381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_406-1_0_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.10814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_406-1_0_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.050396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_406-1_0_3_line_28 | NAYY 4x150 SE | 25 | 28 | 0.019235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_406-1_0_3_line_29 | NAYY 4x150 SE | 25 | 29 | 0.027691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_406-1_0_3_line_30 | NAYY 4x150 SE | 26 | 30 | 0.025829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_406-1_0_3_line_31 | NAYY 4x150 SE | 26 | 31 | 0.094472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_406-1_0_3_line_32 | NAYY 4x150 SE | 27 | 32 | 0.02818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_406-1_0_3_line_33 | NAYY 4x150 SE | 29 | 33 | 0.00084651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_406-1_0_3_line_34 | NAYY 4x150 SE | 31 | 34 | 0.033649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_406-1_0_3_line_35 | NAYY 4x150 SE | 32 | 41 | 0.041219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_406-1_0_3_line_36 | NAYY 4x150 SE | 33 | 37 | 0.016059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_406-1_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.008617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_406-1_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.071893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_406-1_0_3_line_39 | NAYY 4x150 SE | 36 | 54 | 0.015849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_406-1_0_3_line_40 | NAYY 4x150 SE | 36 | 55 | 0.020377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_406-1_0_3_line_41 | NAYY 4x150 SE | 36 | 51 | 0.013558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_406-1_0_3_line_42 | NAYY 4x150 SE | 37 | 38 | 0.043784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_406-1_0_3_line_43 | NAYY 4x150 SE | 39 | 40 | 0.034591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_406-1_0_3_line_44 | NAYY 4x150 SE | 40 | 47 | 0.011427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_406-1_0_3_line_45 | NAYY 4x150 SE | 40 | 48 | 0.16645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_406-1_0_3_line_46 | NAYY 4x150 SE | 41 | 42 | 0.00033366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_406-1_0_3_line_47 | NAYY 4x150 SE | 42 | 43 | 0.012066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_406-1_0_3_line_48 | NAYY 4x150 SE | 43 | 44 | 0.016011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_406-1_0_3_line_49 | NAYY 4x150 SE | 43 | 45 | 0.012219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_406-1_0_3_line_50 | NAYY 4x150 SE | 44 | 46 | 0.24925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_406-1_0_3_line_51 | NAYY 4x150 SE | 46 | 50 | 0.23607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_406-1_0_3_line_52 | NAYY 4x150 SE | 47 | 49 | 0.26674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_406-1_0_3_line_53 | NAYY 4x150 SE | 49 | 50 | 0.018938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_406-1_0_3_line_54 | NAYY 4x150 SE | 51 | 52 | 0.003367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_406-1_0_3_line_55 | NAYY 4x150 SE | 52 | 53 | 0.029203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_406-1_0_3_line_56 | NAYY 4x150 SE | 53 | 56 | 0.011625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_406-1_0_3_line_57 | NAYY 4x150 SE | 54 | 57 | 0.023643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_406-1_0_3_line_58 | NAYY 4x150 SE | 54 | 58 | 0.026625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_406-1_0_3_line_59 | NAYY 4x150 SE | 55 | 59 | 0.024174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_406-1_0_3_line_60 | NAYY 4x150 SE | 56 | 60 | 0.016059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_406-1_0_3_line_61 | NAYY 4x150 SE | 57 | 61 | 0.11281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_406-1_0_3_line_62 | NAYY 4x150 SE | 58 | 62 | 0.009755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_406-1_0_3_line_63 | NAYY 4x150 SE | 59 | 63 | 0.0144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_406-1_0_3_line_64 | NAYY 4x150 SE | 60 | 84 | 0.0025664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_406-1_0_3_line_65 | NAYY 4x150 SE | 61 | 71 | 0.09402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_406-1_0_3_line_66 | NAYY 4x150 SE | 61 | 72 | 0.10684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_406-1_0_3_line_67 | NAYY 4x150 SE | 62 | 64 | 0.023466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_406-1_0_3_line_68 | NAYY 4x150 SE | 62 | 65 | 0.055416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_406-1_0_3_line_69 | NAYY 4x150 SE | 63 | 79 | 0.020136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_406-1_0_3_line_70 | NAYY 4x150 SE | 63 | 75 | 0.011712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_406-1_0_3_line_71 | NAYY 4x150 SE | 64 | 66 | 0.072829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_406-1_0_3_line_72 | NAYY 4x150 SE | 65 | 67 | 0.006604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_406-1_0_3_line_73 | NAYY 4x150 SE | 66 | 68 | 0.04164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_406-1_0_3_line_74 | NAYY 4x150 SE | 67 | 69 | 0.030486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_406-1_0_3_line_75 | NAYY 4x150 SE | 67 | 70 | 0.017058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_406-1_0_3_line_76 | NAYY 4x150 SE | 68 | 85 | 0.21045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_406-1_0_3_line_77 | NAYY 4x150 SE | 69 | 157 | 0.00084556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_406-1_0_3_line_78 | NAYY 4x150 SE | 70 | 153 | 0.0065388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_406-1_0_3_line_79 | NAYY 4x150 SE | 72 | 93 | 0.14006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_406-1_0_3_line_80 | NAYY 4x150 SE | 73 | 74 | 0.006365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_406-1_0_3_line_81 | NAYY 4x150 SE | 73 | 75 | 0.015933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_406-1_0_3_line_82 | NAYY 4x150 SE | 74 | 76 | 0.034442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_406-1_0_3_line_83 | NAYY 4x150 SE | 75 | 77 | 0.0411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_406-1_0_3_line_84 | NAYY 4x150 SE | 76 | 78 | 0.022789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_406-1_0_3_line_85 | NAYY 4x150 SE | 77 | 80 | 0.0078139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_406-1_0_3_line_86 | NAYY 4x150 SE | 79 | 81 | 0.01336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_406-1_0_3_line_87 | NAYY 4x150 SE | 80 | 82 | 0.022542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_406-1_0_3_line_88 | NAYY 4x150 SE | 81 | 83 | 0.014548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_406-1_0_3_line_89 | NAYY 4x150 SE | 82 | 121 | 0.074802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_406-1_0_3_line_90 | NAYY 4x150 SE | 83 | 158 | 0.0064764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_406-1_0_3_line_91 | NAYY 4x150 SE | 84 | 87 | 0.028394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_406-1_0_3_line_92 | NAYY 4x150 SE | 85 | 86 | 0.082602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_406-1_0_3_line_93 | NAYY 4x150 SE | 86 | 91 | 0.0095223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_406-1_0_3_line_94 | NAYY 4x150 SE | 86 | 92 | 0.005456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_406-1_0_3_line_95 | NAYY 4x150 SE | 87 | 88 | 0.025615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_406-1_0_3_line_96 | NAYY 4x150 SE | 88 | 89 | 0.02236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_406-1_0_3_line_97 | NAYY 4x150 SE | 89 | 90 | 0.029414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_406-1_0_3_line_98 | NAYY 4x150 SE | 90 | 95 | 0.09247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_406-1_0_3_line_99 | NAYY 4x150 SE | 92 | 130 | 0.28495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_406-1_0_3_line_100 | NAYY 4x150 SE | 93 | 94 | 0.007624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_406-1_0_3_line_101 | NAYY 4x150 SE | 94 | 136 | 0.20266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_406-1_0_3_line_102 | NAYY 4x150 SE | 95 | 159 | 0.049921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_406-1_0_3_line_103 | NAYY 4x150 SE | 95 | 160 | 0.013071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_406-1_0_3_line_104 | NAYY 4x150 SE | 96 | 97 | 0.11077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_406-1_0_3_line_105 | NAYY 4x150 SE | 97 | 98 | 0.20711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_406-1_0_3_line_106 | NAYY 4x150 SE | 98 | 99 | 0.18766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_406-1_0_3_line_107 | NAYY 4x150 SE | 99 | 100 | 0.41546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_406-1_0_3_line_108 | NAYY 4x150 SE | 100 | 101 | 0.037989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_406-1_0_3_line_109 | NAYY 4x150 SE | 101 | 102 | 0.036541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_406-1_0_3_line_110 | NAYY 4x150 SE | 102 | 103 | 0.005595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_406-1_0_3_line_111 | NAYY 4x150 SE | 102 | 104 | 0.054698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_406-1_0_3_line_112 | NAYY 4x150 SE | 104 | 105 | 0.06189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_406-1_0_3_line_113 | NAYY 4x150 SE | 105 | 106 | 0.023088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_406-1_0_3_line_114 | NAYY 4x150 SE | 106 | 114 | 0.010733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_406-1_0_3_line_115 | NAYY 4x150 SE | 106 | 110 | 0.038652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_406-1_0_3_line_116 | NAYY 4x150 SE | 107 | 108 | 0.036809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_406-1_0_3_line_117 | NAYY 4x150 SE | 107 | 109 | 0.059621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_406-1_0_3_line_118 | NAYY 4x150 SE | 109 | 110 | 0.029398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_406-1_0_3_line_119 | NAYY 4x150 SE | 109 | 111 | 0.013739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_406-1_0_3_line_120 | NAYY 4x150 SE | 110 | 112 | 0.009678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_406-1_0_3_line_121 | NAYY 4x150 SE | 111 | 113 | 0.058898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_406-1_0_3_line_122 | NAYY 4x150 SE | 113 | 115 | 0.1601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_406-1_0_3_line_123 | NAYY 4x150 SE | 114 | 116 | 0.046553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_406-1_0_3_line_124 | NAYY 4x150 SE | 115 | 162 | 0.12347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_406-1_0_3_line_125 | NAYY 4x150 SE | 117 | 118 | 0.01502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_406-1_0_3_line_126 | NAYY 4x150 SE | 118 | 119 | 0.053842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_406-1_0_3_line_127 | NAYY 4x150 SE | 119 | 120 | 0.21304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_406-1_0_3_line_128 | NAYY 4x150 SE | 120 | 121 | 0.0045801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_406-1_0_3_line_129 | NAYY 4x150 SE | 122 | 123 | 0.018875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_406-1_0_3_line_130 | NAYY 4x150 SE | 122 | 124 | 0.0081751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_406-1_0_3_line_131 | NAYY 4x150 SE | 123 | 125 | 0.0051797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_406-1_0_3_line_132 | NAYY 4x150 SE | 123 | 126 | 0.0094545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_406-1_0_3_line_133 | NAYY 4x150 SE | 124 | 127 | 0.014144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_406-1_0_3_line_134 | NAYY 4x150 SE | 125 | 128 | 0.20464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_406-1_0_3_line_135 | NAYY 4x150 SE | 128 | 129 | 0.082621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_406-1_0_3_line_136 | NAYY 4x150 SE | 129 | 135 | 0.038728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_406-1_0_3_line_137 | NAYY 4x150 SE | 130 | 131 | 0.14405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_406-1_0_3_line_138 | NAYY 4x150 SE | 130 | 132 | 0.094542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_406-1_0_3_line_139 | NAYY 4x150 SE | 131 | 134 | 0.26285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_406-1_0_3_line_140 | NAYY 4x150 SE | 132 | 138 | 0.038738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_406-1_0_3_line_141 | NAYY 4x150 SE | 133 | 134 | 0.0020505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_406-1_0_3_line_142 | NAYY 4x150 SE | 135 | 136 | 0.23485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_406-1_0_3_line_143 | NAYY 4x150 SE | 137 | 138 | 0.027207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_406-1_0_3_line_144 | NAYY 4x150 SE | 137 | 139 | 0.044426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_406-1_0_3_line_145 | NAYY 4x150 SE | 139 | 140 | 0.24227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_406-1_0_3_line_146 | NAYY 4x150 SE | 140 | 141 | 0.054495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_406-1_0_3_line_147 | NAYY 4x150 SE | 141 | 142 | 0.010703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_406-1_0_3_line_148 | NAYY 4x150 SE | 142 | 143 | 0.011508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_406-1_0_3_line_149 | NAYY 4x150 SE | 144 | 145 | 0.034837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_406-1_0_3_line_150 | NAYY 4x150 SE | 146 | 147 | 0.0027653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_406-1_0_3_line_151 | NAYY 4x150 SE | 147 | 148 | 0.015117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_406-1_0_3_line_152 | NAYY 4x150 SE | 148 | 149 | 0.011705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_406-1_0_3_line_153 | NAYY 4x150 SE | 149 | 150 | 0.0078249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_406-1_0_3_line_154 | NAYY 4x150 SE | 150 | 154 | 0.022376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_406-1_0_3_line_155 | NAYY 4x150 SE | 151 | 152 | 0.036258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_406-1_0_3_line_156 | NAYY 4x150 SE | 152 | 153 | 0.025928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_406-1_0_3_line_157 | NAYY 4x150 SE | 152 | 154 | 0.047805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_406-1_0_3_line_158 | NAYY 4x150 SE | 153 | 155 | 0.013003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_406-1_0_3_line_159 | NAYY 4x150 SE | 155 | 156 | 0.019498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_406-1_0_3_line_160 | NAYY 4x150 SE | 159 | 161 | 0.02233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_406-1_0_3_line_161 | NAYY 4x150 SE | 159 | 162 | 0.010991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_406-1_0_3_line_162 | NAYY 4x150 SE | 160 | 163 | 0.017479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_406-1_0_3_line_163 | NAYY 4x150 SE | 160 | 164 | 0.0035002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_406-1_0_3_line_164 | NAYY 4x150 SE | 164 | 165 | 0.057015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_406-1_0_3_line_165 | NAYY 4x150 SE | 165 | 166 | 0.016058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_406-1_0_3_line_166 | NAYY 4x150 SE | 165 | 167 | 0.033375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_406-1_0_3_trafo_64 | 0.25 MVA 20/0.4 kV | 168 | 34 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28
0 | 2614269.6835 | 1205194.6034 | 2614251.3469 | 1205193.9928 | 2614247.5583 | 1205194.3285 | 2614243.1546 | 1205197.453 | 2614241.303 | 1205202.0401 | 2614241.1983 | 1205209.2575
1 | 2614263.0656 | 1205431.4286 | 2614260.2482 | 1205391.2332 | 2614260.317 | 1205387.9093 | 2614260.6862 | 1205382.9408 | 2614262.895 | 1205365.6477 | 2614265.7683 | 1205296.0831 | 2614267.6655 | 1205275.5208 | 2614267.8695 | 1205260.0906 | 2614267.2511 | 1205248.2826 | 2614265.9037 | 1205239.1967 | 2614262.6854 | 1205223.6249 | 2614262.3627 | 1205218.5881 | 2614263.6366 | 1205213.8552 | 2614269.6835 | 1205194.6034
2 | 2614263.0656 | 1205431.4286 | 2614264.0922 | 1205453.8768
3 | 2614263.0656 | 1205431.4286 | 2614272.1859 | 1205434.1407 | 2614276.4825 | 1205434.4399
4 | 2614263.0656 | 1205431.4286 | 2614255.4896 | 1205431.6996 | 2614242.1362 | 1205433.9691 | 2614235.6538 | 1205441.3467 | 2614231.6019 | 1205456.5454 | 2614227.8396 | 1205462.2393
5 | 2614100.8114 | 1205351.2343 | 2614100.8288 | 1205350.3227 | 2614102.6036 | 1205333.0285 | 2614103.1475 | 1205324.9031 | 2614102.6566 | 1205316.9532 | 2614101.2135 | 1205306.3884 | 2614099.3358 | 1205296.2785 | 2614098.8755 | 1205294.7953
6 | 2614100.8114 | 1205351.2343 | 2614096.0931 | 1205339.4612 | 2614093.6404 | 1205328.038 | 2614092.7089 | 1205326.3238 | 2614091.5088 | 1205325.6428 | 2614090.3141 | 1205325.8957
7 | 2614087.398 | 1205278.663 | 2614089.3287 | 1205279.1456 | 2614091.6753 | 1205280.6964 | 2614094.9282 | 1205284.973 | 2614097.1845 | 1205289.3474 | 2614098.8755 | 1205294.7953
8 | 2614264.0922 | 1205453.8768 | 2614265.6088 | 1205487.04
9 | 2614276.4825 | 1205434.4399 | 2614276.4825 | 1205434.4399 | 2614279.4959 | 1205433.769 | 2614281.6742 | 1205432.4957 | 2614283.8548 | 1205430.2441 | 2614286.4879 | 1205426.4149 | 2614288.3533 | 1205422.3727 | 2614289.7716 | 1205417.6513 | 2614290.6689 | 1205414.5517 | 2614290.8136 | 1205411.2947 | 2614290.5138 | 1205405.716
10 | 2614216.7801 | 1205478.9765 | 2614227.8396 | 1205462.2393
11 | 2614087.398 | 1205278.663 | 2614084.4847 | 1205278.734 | 2614076.2812 | 1205280.5935 | 2614070.8318 | 1205282.1371 | 2614065.3045 | 1205284.4365 | 2614059.5008 | 1205287.8581 | 2614051.6391 | 1205293.1537 | 2614039.3439 | 1205301.3627 | 2614024.4027 | 1205309.2654 | 2614019.1804 | 1205311.2543 | 2614013.6843 | 1205313.2537 | 2613988.8961 | 1205319.7042
12 | 2614265.9212 | 1205493.8696 | 2614265.6088 | 1205487.04
13 | 2614207.8624 | 1205492.634 | 2614209.4813 | 1205490.0224 | 2614216.7801 | 1205478.9765
14 | 2613972.9992 | 1205331.7639 | 2613978.0014 | 1205324.6767 | 2613981.0646 | 1205322.2714 | 2613984.384 | 1205320.8784 | 2613988.8961 | 1205319.7042
15 | 2613838.4088 | 1205381.762 | 2613844.8238 | 1205380.3094 | 2613850.841 | 1205379.8786 | 2613858.98 | 1205379.5416 | 2613869.127 | 1205379.1204 | 2613884.2737 | 1205377.5657 | 2613899.4526 | 1205375.2774 | 2613904.8261 | 1205373.6223 | 2613908.5346 | 1205371.6854 | 2613911.7416 | 1205369.5694 | 2613915.329 | 1205367.3654 | 2613919.0898 | 1205365.84 | 2613923.5396 | 1205365.6724 | 2613928.8194 | 1205368.3306 | 2613935.4607 | 1205374.2604 | 2613945.7763 | 1205379.8875 | 2613954.2734 | 1205382.5309 | 2613953.5863 | 1205364.0303 | 2613966.6643 | 1205352.6656 | 2613969.1494 | 1205337.2185 | 2613972.9992 | 1205331.7639
16 | 2613763.5321 | 1205384.1466 | 2613770.3622 | 1205377.492 | 2613775.2158 | 1205373.701 | 2613776.6402 | 1205372.7704 | 2613778.2231 | 1205372.3739 | 2613779.5308 | 1205372.577 | 2613782.966 | 1205373.7188 | 2613791.5895 | 1205377.6519 | 2613798.3079 | 1205379.8686 | 2613805.6728 | 1205382.0868 | 2613813.8078 | 1205383.4507 | 2613819.5179 | 1205384.2532 | 2613824.8643 | 1205384.4656 | 2613828.987 | 1205384.2861 | 2613834.4431 | 1205383.098 | 2613838.4088 | 1205381.762
17 | 2613763.5321 | 1205384.1466 | 2613770.8882 | 1205390.2112 | 2613772.8264 | 1205391.558
18 | 2613763.5321 | 1205384.1466 | 2613757.916 | 1205378.8308 | 2613749.2521 | 1205369.3168 | 2613741.6223 | 1205359.8719 | 2613735.8342 | 1205351.659
19 | 2613803.7829 | 1205410.1089 | 2613792.9807 | 1205404.3809 | 2613783.7138 | 1205399.1234 | 2613772.8264 | 1205391.558
20 | 2613857.6653 | 1205437.7389 | 2613882.6662 | 1205450.9146
21 | 2614062.8714 | 1205520.7492 | 2613994.4522 | 1205500.8783 | 2613957.5881 | 1205487.674 | 2613930.8882 | 1205476.3279 | 2613882.6662 | 1205450.9146
22 | 2613803.7829 | 1205410.1089 | 2613856.0941 | 1205436.9108 | 2613857.6653 | 1205437.7389
23 | 2614062.8714 | 1205520.7492 | 2614087.6533 | 1205529.2312
24 | 2614062.8714 | 1205520.7492 | 2614052.5268 | 1205543.8821 | 2614047.5863 | 1205551.5238
25 | 2613803.7829 | 1205410.1089 | 2613788.1766 | 1205439.5558 | 2613780.4204 | 1205448.8208
26 | 2614183.3199 | 1205579.176 | 2614111.8018 | 1205538.6073 | 2614097.4414 | 1205532.5813 | 2614087.6533 | 1205529.2312
27 | 2614018.1964 | 1205592.1615 | 2614018.1964 | 1205592.1615 | 2614029.5485 | 1205580.4039 | 2614041.1304 | 1205561.5095 | 2614047.5863 | 1205551.5238
28 | 2613762.0202 | 1205443.0421 | 2613780.4204 | 1205448.8208
29 | 2613780.4204 | 1205448.8208 | 2613759.7456 | 1205467.2425
30 | 2614183.3199 | 1205579.176 | 2614181.5385 | 1205583.1073 | 2614178.8311 | 1205589.4599 | 2614180.6106 | 1205595.9677 | 2614185.9283 | 1205601.7724
31 | 2614183.3199 | 1205579.176 | 2614206.8768 | 1205590.8938 | 2614222.9546 | 1205597.4132 | 2614270.571 | 1205615.1499
32 | 2614018.1964 | 1205592.1615 | 2614002.3731 | 1205603.5975 | 2613993.8851 | 1205605.2983
33 | 2613759.1136 | 1205467.8056 | 2613759.7456 | 1205467.2425
34 | 2614302.1032 | 1205626.8954 | 2614270.571 | 1205615.1499
35 | 2613954.9409 | 1205617.9191 | 2613965.8832 | 1205612.8286 | 2613973.1086 | 1205609.5103 | 2613982.3004 | 1205607.6196 | 2613993.8851 | 1205605.2983
36 | 2613747.8363 | 1205479.2294 | 2613757.1983 | 1205469.5122 | 2613759.1136 | 1205467.8056
37 | 2614302.1032 | 1205626.8954 | 2614298.8594 | 1205634.881
38 | 2614302.1032 | 1205626.8954 | 2614317.6612 | 1205634.4256 | 2614333.2776 | 1205642.9342 | 2614355.6835 | 1205658.7076 | 2614363.5115 | 1205664.2182
39 | 2614368.5289 | 1205649.2554 | 2614367.7437 | 1205653.189 | 2614364.9682 | 1205659.3413 | 2614363.5115 | 1205664.2182
40 | 2614363.5115 | 1205664.2182 | 2614360.3527 | 1205668.4685 | 2614356.2285 | 1205672.4942 | 2614348.806 | 1205678.1276
41 | 2614363.5115 | 1205664.2182 | 2614374.5974 | 1205672.0235
42 | 2613747.8363 | 1205479.2294 | 2613748.1457 | 1205486.9232 | 2613749.4589 | 1205491.362 | 2613751.7557 | 1205494.7357 | 2613754.7474 | 1205496.8437 | 2613759.164 | 1205497.8322 | 2613765.7348 | 1205498.0363 | 2613771.881 | 1205497.6613 | 2613778.1372 | 1205495.7857
43 | 2613560.8995 | 1205914.4862 | 2613543.4409 | 1205900.5621 | 2613532.7062 | 1205894.6411
44 | 2613569.8081 | 1205921.6427 | 2613562.2145 | 1205915.5349 | 2613560.8995 | 1205914.4862
45 | 2613560.8995 | 1205914.4862 | 2613654.3393 | 1205776.7345
46 | 2613954.6384 | 1205618.0599 | 2613954.9409 | 1205617.9191
47 | 2613945.0463 | 1205625.0201 | 2613949.2625 | 1205620.5608 | 2613954.6384 | 1205618.0599
48 | 2613945.0463 | 1205625.0201 | 2613940.8687 | 1205629.2238 | 2613936.2161 | 1205638.1846
49 | 2613945.0463 | 1205625.0201 | 2613939.0995 | 1205614.3463
50 | 2613936.2161 | 1205638.1846 | 2613982.0606 | 1205883.1813
51 | 2613982.0606 | 1205883.1813 | 2613977.9849 | 1205895.9788 | 2613969.7659 | 1205911.3681 | 2613950.8836 | 1205933.7253 | 2613930.3116 | 1205953.4883 | 2613914.9433 | 1205972.4964 | 2613908.1969 | 1205979.3957 | 2613896.5495 | 1205987.7066 | 2613886.5458 | 1205992.3526 | 2613875.496 | 1205995.5288 | 2613863.2112 | 1205996.7121 | 2613849.5306 | 1205996.3803 | 2613836.1781 | 1205992.2695 | 2613824.6017 | 1205983.06 | 2613817.0172 | 1205977.495 | 2613809.7419 | 1205967.6098
52 | 2613569.8081 | 1205921.6427 | 2613574.6338 | 1205925.5241 | 2613576.0156 | 1205946.6721 | 2613586.2573 | 1205964.5051 | 2613591.5676 | 1205970.3092 | 2613599.0057 | 1205973.4945 | 2613609.7035 | 1205974.5749 | 2613623.8505 | 1205973.8288 | 2613658.0767 | 1205972.2391 | 2613678.3963 | 1205972.6968 | 2613695.1455 | 1205974.7473 | 2613715.6054 | 1205977.0064 | 2613735.0217 | 1205976.7284 | 2613747.2908 | 1205975.7449 | 2613758.9663 | 1205974.9379 | 2613766.3946 | 1205972.4425 | 2613776.3572 | 1205965.7839 | 2613783.284 | 1205959.7965 | 2613789.3973 | 1205956.9979 | 2613795.9413 | 1205955.401 | 2613795.9413 | 1205955.401
53 | 2613809.7419 | 1205967.6098 | 2613805.5922 | 1205961.9713 | 2613801.6624 | 1205957.7932 | 2613795.9413 | 1205955.401
54 | 2614374.5974 | 1205672.0235 | 2614377.3505 | 1205673.9619
55 | 2614377.3505 | 1205673.9619 | 2614401.2286 | 1205690.7738
56 | 2614410.7338 | 1205697.4662 | 2614401.2286 | 1205690.7738
57 | 2614368.5289 | 1205649.2554 | 2614376.2432 | 1205648.2511 | 2614383.8244 | 1205648.8696 | 2614391.806 | 1205650.9849
58 | 2614368.5289 | 1205649.2554 | 2614368.9315 | 1205633.6255 | 2614368.0028 | 1205622.6745
59 | 2614348.806 | 1205678.1276 | 2614344.8682 | 1205681.1162 | 2614332.2537 | 1205692.659 | 2614331.0491 | 1205694.4175
60 | 2614410.7338 | 1205697.4662 | 2614423.8645 | 1205706.7112
61 | 2614483.9288 | 1205714.2576 | 2614480.8071 | 1205712.5602 | 2614475.2647 | 1205708.6113 | 2614453.4786 | 1205688.3476 | 2614426.6331 | 1205668.7723 | 2614403.0007 | 1205653.9518 | 2614391.806 | 1205650.9849
62 | 2614367.1785 | 1205612.9544 | 2614368.0028 | 1205622.6745
63 | 2614328.4211 | 1205708.3585 | 2614328.7877 | 1205701.3222 | 2614329.2583 | 1205698.5551 | 2614330.2312 | 1205695.6114 | 2614331.0491 | 1205694.4175
64 | 2614425.963 | 1205708.1887 | 2614423.8645 | 1205706.7112
65 | 2614483.9288 | 1205714.2576 | 2614485.7757 | 1205717.9196 | 2614487.4598 | 1205719.6802 | 2614490.7605 | 1205722.8455 | 2614524.3976 | 1205745.3614 | 2614536.3433 | 1205752.5388 | 2614540.9037 | 1205756.8299 | 2614546.094 | 1205761.6785 | 2614552.0675 | 1205766.5401 | 2614558.3849 | 1205770.7578
66 | 2614483.9288 | 1205714.2576 | 2614487.3555 | 1205715.6221 | 2614492.4931 | 1205717.1132 | 2614497.2821 | 1205718.1253 | 2614503.3043 | 1205718.6179 | 2614510.3164 | 1205718.6238 | 2614517.2165 | 1205717.7733 | 2614524.8862 | 1205716.3578 | 2614535.8594 | 1205713.7719 | 2614546.8504 | 1205710.0854 | 2614554.4556 | 1205707.0133 | 2614563.167 | 1205702.5764 | 2614584.2345 | 1205690.557
67 | 2614367.1785 | 1205612.9544 | 2614372.9052 | 1205590.1975
68 | 2614367.1785 | 1205612.9544 | 2614341.1926 | 1205586.6889 | 2614328.5301 | 1205573.2452
69 | 2614328.4211 | 1205708.3585 | 2614343.1723 | 1205722.0648
70 | 2614327.4425 | 1205720.0181 | 2614328.0386 | 1205715.6394 | 2614328.4211 | 1205708.3585
71 | 2614372.9052 | 1205590.1975 | 2614379.4721 | 1205564.1016 | 2614372.879 | 1205528.822 | 2614372.0866 | 1205518.8238
72 | 2614324.0021 | 1205568.4378 | 2614328.5301 | 1205573.2452
73 | 2614368.9031 | 1205477.3064 | 2614369.1953 | 1205482.3432 | 2614372.0866 | 1205518.8238
74 | 2614324.0021 | 1205568.4378 | 2614307.466 | 1205594.0498
75 | 2614324.0021 | 1205568.4378 | 2614310.4689 | 1205558.0545
76 | 2614368.9031 | 1205477.3064 | 2614382.0047 | 1205446.8433 | 2614391.3547 | 1205410.9239 | 2614406.68 | 1205379.4212 | 2614442.3782 | 1205352.3811 | 2614477.4461 | 1205334.5448 | 2614490.8654 | 1205320.8808 | 2614492.5533 | 1205320.1025
77 | 2614307.0074 | 1205594.7602 | 2614307.466 | 1205594.0498
78 | 2614305.2811 | 1205554.0742 | 2614310.4689 | 1205558.0545
79 | 2614657.643 | 1205576.6272 | 2614645.1721 | 1205601.354 | 2614640.6263 | 1205612.8714 | 2614631.2105 | 1205644.11 | 2614622.6478 | 1205659.2641 | 2614610.408 | 1205672.8306 | 2614595.6871 | 1205684.0231 | 2614584.2345 | 1205690.557
80 | 2614308.6683 | 1205707.9886 | 2614314.0275 | 1205711.4225
81 | 2614327.4425 | 1205720.0181 | 2614314.0275 | 1205711.4225
82 | 2614279.6684 | 1205689.4072 | 2614308.6683 | 1205707.9886
83 | 2614327.4425 | 1205720.0181 | 2614324.9019 | 1205729.7507 | 2614321.8118 | 1205740.2602 | 2614320.6134 | 1205748.473 | 2614320.8851 | 1205752.5203 | 2614321.9718 | 1205756.047 | 2614324.1083 | 1205759.4762 | 2614324.1083 | 1205759.4762
84 | 2614260.4807 | 1205677.1127 | 2614279.6684 | 1205689.4072
85 | 2614328.7846 | 1205765.7364 | 2614324.1083 | 1205759.4762
86 | 2614343.1723 | 1205722.0648 | 2614352.9595 | 1205731.1586
87 | 2614344.1645 | 1205782.147 | 2614342.7675 | 1205780.2989 | 2614336.5752 | 1205774.6032 | 2614330.1731 | 1205767.5952 | 2614328.7846 | 1205765.7364
88 | 2614352.9595 | 1205731.1586 | 2614363.6173 | 1205741.0615
89 | 2614344.1645 | 1205782.147 | 2614345.8152 | 1205784.3307 | 2614347.442 | 1205787.792 | 2614348.3402 | 1205790.6402 | 2614348.251 | 1205792.9634 | 2614347.4544 | 1205795.3184 | 2614346.0822 | 1205796.6825 | 2614343.9652 | 1205797.8448 | 2614341.2956 | 1205797.9051 | 2614337.9207 | 1205797.141 | 2614333.7036 | 1205795.5523 | 2614319.9685 | 1205789.2049 | 2614308.6848 | 1205784.9534 | 2614300.9635 | 1205782.5892 | 2614296.9949 | 1205782.0128 | 2614293.9671 | 1205782.3835 | 2614291.0592 | 1205783.5439 | 2614291.0592 | 1205783.5439
90 | 2614363.6173 | 1205741.0615 | 2614368.3618 | 1205745.4698
91 | 2614425.963 | 1205708.1887 | 2614434.9042 | 1205714.4839 | 2614449.1799 | 1205724.5355
92 | 2614567.5651 | 1205285.5139 | 2614492.5533 | 1205320.1025
93 | 2614567.5651 | 1205285.5139 | 2614563.7975 | 1205283.5148 | 2614558.783 | 1205284.4031 | 2614558.6208 | 1205284.4314
94 | 2614572.5525 | 1205283.2693 | 2614567.5651 | 1205285.5139
95 | 2614470.1238 | 1205739.2822 | 2614449.1799 | 1205724.5355
96 | 2614470.1238 | 1205739.2822 | 2614478.7429 | 1205745.351 | 2614487.9109 | 1205752.81
97 | 2614487.9109 | 1205752.81 | 2614505.2485 | 1205766.9158 | 2614510.4557 | 1205771.6879
98 | 2614578.628 | 1205834.164 | 2614510.4557 | 1205771.6879
99 | 2614572.5525 | 1205283.2693 | 2614603.6142 | 1205267.992 | 2614607.2701 | 1205265.8998 | 2614610.3183 | 1205263.517 | 2614621.7146 | 1205253.1058 | 2614667.9312 | 1205214.6309 | 2614681.4801 | 1205204.225 | 2614692.903 | 1205195.4593 | 2614697.1113 | 1205191.4563 | 2614703.4321 | 1205185.1906 | 2614709.7264 | 1205180.4145 | 2614714.2281 | 1205177.7463 | 2614719.2002 | 1205175.5907 | 2614725.83 | 1205173.5836 | 2614743.7198 | 1205170.3258 | 2614750.7512 | 1205168.9535 | 2614778.8517 | 1205161.2407 | 2614784.5127 | 1205160.3986 | 2614793.9459 | 1205159.7215 | 2614806.4644 | 1205160.1526 | 2614814.3201 | 1205160.6946 | 2614819.198 | 1205161.5144
100 | 2614661.0763 | 1205569.82 | 2614657.643 | 1205576.6272
101 | 2614804.8575 | 1205431.8976 | 2614781.0638 | 1205451.6164 | 2614718.0525 | 1205491.1275 | 2614704.2016 | 1205503.945 | 2614692.229 | 1205520.0133 | 2614666.0943 | 1205561.1497 | 2614661.0763 | 1205569.82
102 | 2614578.628 | 1205834.164 | 2614593.2933 | 1205845.6282 | 2614619.4432 | 1205863.0126
103 | 2614578.628 | 1205834.164 | 2614570.0405 | 1205844.0374
104 | 2614663.9281 | 1206722.7828 | 2614652.0564 | 1206723.5097 | 2614635.834 | 1206721.6024 | 2614614.3191 | 1206716.5693 | 2614597.1727 | 1206710.0017 | 2614578.7732 | 1206705.9103 | 2614557.2597 | 1206697.142
105 | 2614512.3968 | 1206583.5708 | 2614548.7946 | 1206625.8489 | 2614583.758 | 1206663.588 | 2614620.2138 | 1206694.1269 | 2614643.1987 | 1206710.6254 | 2614655.53 | 1206717.8595 | 2614663.9281 | 1206722.7828
106 | 2614512.3968 | 1206583.5708 | 2614518.3586 | 1206583.5741 | 2614525.4111 | 1206585.2921 | 2614534.649 | 1206588.9499 | 2614543.4043 | 1206590.9166 | 2614557.0351 | 1206592.4061 | 2614583.8001 | 1206593.1938 | 2614613.7419 | 1206591.5769 | 2614648.0661 | 1206588.9926 | 2614655.2299 | 1206588.7655 | 2614668.2767 | 1206595.8013 | 2614683.5593 | 1206605.8998 | 2614688.8625 | 1206610.8489 | 2614691.555 | 1206612.3401
107 | 2614854.8977 | 1206230.3321 | 2614691.555 | 1206612.3401
108 | 2614854.8977 | 1206230.3321 | 2614858.6118 | 1206227.3785 | 2614859.0071 | 1206218.2189 | 2614853.1542 | 1206207.9543 | 2614850.9822 | 1206195.8883
109 | 2614833.4882 | 1206165.0042 | 2614838.55 | 1206169.2747 | 2614844.7753 | 1206176.6163 | 2614850.2511 | 1206191.8271 | 2614850.9822 | 1206195.8883
110 | 2614833.4882 | 1206165.0042 | 2614829.8536 | 1206169.2579
111 | 2614833.4882 | 1206165.0042 | 2614837.8355 | 1206159.9233 | 2614845.5756 | 1206151.3377 | 2614853.6631 | 1206149.8903 | 2614860.6434 | 1206150.2745 | 2614874.7509 | 1206165.3289 | 2614875.1104 | 1206165.8263
112 | 2614900.3901 | 1206136.4211 | 2614901.2582 | 1206148.1742 | 2614897.1674 | 1206166.2962 | 2614890.9012 | 1206175.4412 | 2614886.2985 | 1206176.1635 | 2614880.9807 | 1206173.9491 | 2614875.1104 | 1206165.8263
113 | 2614890.0218 | 1206116.1842 | 2614896.3502 | 1206124.9047 | 2614900.1915 | 1206133.708 | 2614900.3901 | 1206136.4211
114 | 2614890.0218 | 1206116.1842 | 2614879.8305 | 1206119.5496
115 | 2614883.5057 | 1206078.9364 | 2614882.4956 | 1206081.4575 | 2614885.0301 | 1206095.9385 | 2614887.5586 | 1206112.7985 | 2614890.0218 | 1206116.1842
116 | 2614927.5722 | 1206110.246 | 2614928.9068 | 1206112.5345 | 2614936.2161 | 1206127.3831 | 2614943.387 | 1206143.4667
117 | 2614901.7597 | 1206056.614 | 2614907.3304 | 1206070.3465 | 2614917.5632 | 1206093.0844 | 2614927.5722 | 1206110.246
118 | 2614901.7597 | 1206056.614 | 2614899.276 | 1206058.4199 | 2614886.7503 | 1206070.8512 | 2614883.5057 | 1206078.9364
119 | 2614912.921 | 1206048.5595 | 2614901.7597 | 1206056.614
120 | 2614883.5057 | 1206078.9364 | 2614878.6506 | 1206077.1456 | 2614874.6906 | 1206079.337
121 | 2614912.921 | 1206048.5595 | 2614898.9954 | 1206036.7295 | 2614890.1899 | 1206030.1596 | 2614879.735 | 1206023.2854 | 2614869.3544 | 1206017.0785 | 2614864.8926 | 1206014.7506
122 | 2614716.7672 | 1205955.5904 | 2614725.3009 | 1205961.4368 | 2614736.913 | 1205967.9578 | 2614745.6105 | 1205972.1481 | 2614755.0996 | 1205976.0069 | 2614839.9026 | 1206003.8871 | 2614858.7136 | 1206011.5268 | 2614864.8926 | 1206014.7506
123 | 2614865.3616 | 1206099.9141 | 2614861.319 | 1206098.6256 | 2614856.165 | 1206103.9268 | 2614855.9639 | 1206111.4304 | 2614859.0767 | 1206116.5743 | 2614867.335 | 1206119.8855 | 2614879.8305 | 1206119.5496
124 | 2614716.7672 | 1205955.5904 | 2614709.6551 | 1205949.9698 | 2614701.0422 | 1205942.3112 | 2614694.1147 | 1205935.8017 | 2614671.8798 | 1205913.1237 | 2614652.4147 | 1205892.8316 | 2614643.7127 | 1205884.2056 | 2614633.8027 | 1205875.0431 | 2614627.8682 | 1205870.0711
125 | 2614376.2038 | 1206035.6081 | 2614390.5854 | 1206039.9421
126 | 2614376.2038 | 1206035.6081 | 2614375.2048 | 1206027.2678 | 2614373.5912 | 1206018.3145 | 2614371.3692 | 1206009.3598 | 2614371.72 | 1205999.433 | 2614372.1521 | 1205990.4847 | 2614372.2357 | 1205982.2581
127 | 2614289.475 | 1205787.6646 | 2614290.297 | 1205790.5904 | 2614292.7894 | 1205794.6764 | 2614299.1207 | 1205802.6848 | 2614304.5099 | 1205810.2684 | 2614308.9644 | 1205817.5386 | 2614313.5217 | 1205826.3877 | 2614316.1673 | 1205833.1755 | 2614322.3552 | 1205850.2107 | 2614337.3085 | 1205887.7115 | 2614349.9524 | 1205924.1062 | 2614359.6967 | 1205942.2283 | 2614366.8022 | 1205957.0869 | 2614369.4373 | 1205965.0309 | 2614371.454 | 1205973.9739 | 2614372.2517 | 1205980.6907 | 2614372.2357 | 1205982.2581
128 | 2614291.0592 | 1205783.5439 | 2614289.8005 | 1205785.1307 | 2614289.475 | 1205787.6646 | 2614289.475 | 1205787.6646
129 | 2614869.3594 | 1205803.6057 | 2614859.9652 | 1205807.3733 | 2614851.1798 | 1205807.9408
130 | 2614851.1798 | 1205807.9408 | 2614854.5042 | 1205800.4722
131 | 2614869.3594 | 1205803.6057 | 2614870.9866 | 1205798.6882
132 | 2614869.3594 | 1205803.6057 | 2614878.4552 | 1205806.1855
133 | 2614860.3565 | 1205787.5968 | 2614858.797 | 1205790.828 | 2614854.5042 | 1205800.4722
134 | 2614897.1573 | 1205607.5226 | 2614908.6916 | 1205618.0015 | 2614912.1613 | 1205632.6626 | 2614913.2067 | 1205652.6317 | 2614901.8853 | 1205715.6381 | 2614898.0578 | 1205740.9203 | 2614894.0804 | 1205753.0504 | 2614880.8167 | 1205771.4609 | 2614876.2845 | 1205783.4785 | 2614872.9762 | 1205792.6753 | 2614870.9866 | 1205798.6882
135 | 2614897.1573 | 1205607.5226 | 2614888.5064 | 1205605.8669 | 2614865.7573 | 1205615.5157 | 2614841.9532 | 1205621.2265 | 2614827.7347 | 1205622.7922 | 2614817.7168 | 1205620.3216
136 | 2614817.7168 | 1205620.3216 | 2614817.7168 | 1205620.3216 | 2614810.5651 | 1205612.1106 | 2614801.178 | 1205606.7289 | 2614792.8263 | 1205607.0974 | 2614785.0191 | 1205610.8412
137 | 2614819.198 | 1205161.5144 | 2614939.8959 | 1205240.1497
138 | 2614805.0687 | 1205124.7409 | 2614821.2736 | 1205135.4868 | 2614828.4485 | 1205140.6741 | 2614837.0174 | 1205148.0882 | 2614844.1647 | 1205155.1876 | 2614846.7876 | 1205158.7405 | 2614847.9533 | 1205161.0335 | 2614848.5181 | 1205163.325 | 2614848.4518 | 1205165.5038 | 2614847.1072 | 1205167.9018 | 2614845.3313 | 1205169.3871 | 2614842.0283 | 1205170.2016 | 2614838.5069 | 1205170.104 | 2614835.5886 | 1205169.1184 | 2614830.3405 | 1205166.026 | 2614826.1711 | 1205163.4587 | 2614821.0335 | 1205161.8229 | 2614819.198 | 1205161.5144
139 | 2615121.0864 | 1205384.3163 | 2615120.5438 | 1205382.3138 | 2615119.1743 | 1205379.4755 | 2615118.1024 | 1205376.2599 | 2615117.4196 | 1205372.5784 | 2615116.6114 | 1205349.2413 | 2615115.1759 | 1205330.3496 | 2615113.214 | 1205318.1379 | 2615108.7332 | 1205309.4663 | 2615102.9941 | 1205302.0812 | 2615090.2535 | 1205290.3204 | 2615080.8397 | 1205283.3373 | 2615069.758 | 1205277.2506 | 2615052.4004 | 1205271.5483 | 2615028.1286 | 1205266.0288 | 2615002.1959 | 1205261.5837 | 2614981.7952 | 1205256.1408 | 2614964.9172 | 1205250.2065 | 2614950.0165 | 1205244.3439 | 2614939.8959 | 1205240.1497
140 | 2614805.0687 | 1205124.7409 | 2614800.894 | 1205118.1603 | 2614779.4343 | 1205095.8659
141 | 2615121.0864 | 1205384.3163 | 2615123.0616 | 1205384.867
142 | 2614804.8575 | 1205431.8976 | 2614811.2281 | 1205436.1713 | 2614811.0182 | 1205444.1751 | 2614800.4355 | 1205457.7787 | 2614777.0633 | 1205494.7524 | 2614760.7578 | 1205528.3418 | 2614756.6571 | 1205547.3866 | 2614752.8915 | 1205594.0696 | 2614752.5411 | 1205609.7329 | 2614756.2277 | 1205616.7569 | 2614761.5232 | 1205618.9823 | 2614769.7848 | 1205618.1466 | 2614785.0191 | 1205610.8412
143 | 2614760.0733 | 1205076.894 | 2614760.5818 | 1205077.9167 | 2614762.69 | 1205080.4788 | 2614766.8341 | 1205084.091 | 2614777.6712 | 1205094.0343 | 2614779.4343 | 1205095.8659
144 | 2614760.0733 | 1205076.894 | 2614756.6083 | 1205069.9247 | 2614746.1274 | 1205051.1998 | 2614743.4757 | 1205046.9576 | 2614740.1366 | 1205043.8366 | 2614737.7062 | 1205042.3743 | 2614735.0664 | 1205041.5208
145 | 2614539.2531 | 1205117.4087 | 2614541.8876 | 1205119.3717 | 2614545.5187 | 1205121.2815 | 2614550.3155 | 1205122.3716 | 2614557.0759 | 1205122.9772 | 2614579.6644 | 1205123.6435 | 2614622.9546 | 1205125.172 | 2614645.5634 | 1205123.7709 | 2614656.7179 | 1205122.175 | 2614663.2024 | 1205120.4788 | 2614670.3734 | 1205118.0284 | 2614676.1074 | 1205115.3409 | 2614680.4879 | 1205112.4945 | 2614683.7348 | 1205109.7232 | 2614687.6548 | 1205105.4638 | 2614690.9831 | 1205100.5581 | 2614693.5596 | 1205095.1949 | 2614696.5796 | 1205085.7415 | 2614700.1416 | 1205072.3652 | 2614702.9126 | 1205065.2347 | 2614706.1323 | 1205058.0942 | 2614709.8729 | 1205052.5782 | 2614714.1682 | 1205047.2747 | 2614717.8491 | 1205044.371 | 2614722.1374 | 1205041.9358 | 2614725.8977 | 1205040.7777 | 2614729.1307 | 1205040.6078 | 2614733.6173 | 1205041.0524 | 2614735.0664 | 1205041.5208
146 | 2614539.2531 | 1205117.4087 | 2614537.8797 | 1205116.0268 | 2614535.6816 | 1205112.8753 | 2614529.4226 | 1205099.9864 | 2614524.1069 | 1205090.157 | 2614520.479 | 1205083.7781 | 2614515.5593 | 1205076.8735 | 2614510.7583 | 1205071.2144
147 | 2614510.7583 | 1205071.2144 | 2614505.9506 | 1205065.1883 | 2614504.961 | 1205062.3621
148 | 2614504.961 | 1205062.3621 | 2614504.8061 | 1205060.3718 | 2614505.4771 | 1205053.4029 | 2614505.9009 | 1205050.9281
149 | 2614189.5083 | 1205522.2433 | 2614207.8624 | 1205492.634
150 | 2614230.7261 | 1205541.9975 | 2614232.2645 | 1205539.6995
151 | 2614240.6742 | 1205527.1377 | 2614232.2645 | 1205539.6995
152 | 2614240.6742 | 1205527.1377 | 2614247.1858 | 1205517.4111
153 | 2614251.5389 | 1205510.9088 | 2614247.1858 | 1205517.4111
154 | 2614265.9212 | 1205493.8696 | 2614256.055 | 1205504.1629 | 2614251.5389 | 1205510.9088
155 | 2614285.9054 | 1205536.7852 | 2614265.9546 | 1205567.0613
156 | 2614305.2811 | 1205554.0742 | 2614285.9054 | 1205536.7852
157 | 2614265.9212 | 1205493.8696 | 2614270.1185 | 1205510.2552 | 2614278.213 | 1205525.3383 | 2614285.9054 | 1205536.7852
158 | 2614305.2811 | 1205554.0742 | 2614298.115 | 1205564.9241
159 | 2614298.115 | 1205564.9241 | 2614287.369 | 1205581.1941
160 | 2614619.4432 | 1205863.0126 | 2614608.0541 | 1205867.8319 | 2614601.2828 | 1205875.1972
161 | 2614619.4432 | 1205863.0126 | 2614627.8682 | 1205870.0711
162 | 2614556.5608 | 1205832.8652 | 2614570.0405 | 1205844.0374
163 | 2614570.0405 | 1205844.0374 | 2614572.5586 | 1205846.4686
164 | 2614558.0308 | 1205891.4676 | 2614560.1395 | 1205890.6167 | 2614562.3189 | 1205888.821 | 2614564.1653 | 1205886.3575 | 2614573.8856 | 1205870.339 | 2614580.57 | 1205861.1836 | 2614581.7076 | 1205859.352 | 2614581.9399 | 1205857.6627 | 2614581.5186 | 1205855.7718 | 2614580.5338 | 1205854.1685 | 2614572.5586 | 1205846.4686
165 | 2614558.0308 | 1205891.4676 | 2614560.8095 | 1205899.7011 | 2614564.3072 | 1205906.191
166 | 2614530.1827 | 1205875.0022 | 2614545.7799 | 1205887.9137 | 2614549.5689 | 1205890.3798 | 2614552.8444 | 1205891.3439 | 2614555.6647 | 1205891.8399 | 2614558.0308 | 1205891.4676

## bus_geodata
| x | y | coords
0 | 2614241.1983 | 1205209.2575
1 | 2614269.6835 | 1205194.6034
2 | 2614263.0656 | 1205431.4286
3 | 2614100.8114 | 1205351.2343
4 | 2614098.8755 | 1205294.7953
5 | 2614090.3141 | 1205325.8957
6 | 2614264.0922 | 1205453.8768
7 | 2614276.4825 | 1205434.4399
8 | 2614227.8396 | 1205462.2393
9 | 2614087.398 | 1205278.663
10 | 2614265.6088 | 1205487.04
11 | 2614290.5138 | 1205405.716
12 | 2614216.7801 | 1205478.9765
13 | 2613988.8961 | 1205319.7042
14 | 2613972.9992 | 1205331.7639
15 | 2613838.4088 | 1205381.762
16 | 2613763.5321 | 1205384.1466
17 | 2613772.8264 | 1205391.558
18 | 2613735.8342 | 1205351.659
19 | 2613882.6662 | 1205450.9146
20 | 2613857.6653 | 1205437.7389
21 | 2614062.8714 | 1205520.7492
22 | 2613803.7829 | 1205410.1089
23 | 2614087.6533 | 1205529.2312
24 | 2614047.5863 | 1205551.5238
25 | 2613780.4204 | 1205448.8208
26 | 2614183.3199 | 1205579.176
27 | 2614018.1964 | 1205592.1615
28 | 2613762.0202 | 1205443.0421
29 | 2613759.7456 | 1205467.2425
30 | 2614185.9283 | 1205601.7724
31 | 2614270.571 | 1205615.1499
32 | 2613993.8851 | 1205605.2983
33 | 2613759.1136 | 1205467.8056
34 | 2614302.1032 | 1205626.8954
35 | 2614298.8594 | 1205634.881
36 | 2614363.5115 | 1205664.2182
37 | 2613747.8363 | 1205479.2294
38 | 2613778.1372 | 1205495.7857
39 | 2613532.7062 | 1205894.6411
40 | 2613560.8995 | 1205914.4862
41 | 2613954.9409 | 1205617.9191
42 | 2613954.6384 | 1205618.0599
43 | 2613945.0463 | 1205625.0201
44 | 2613936.2161 | 1205638.1846
45 | 2613939.0995 | 1205614.3463
46 | 2613982.0606 | 1205883.1813
47 | 2613569.8081 | 1205921.6427
48 | 2613654.3393 | 1205776.7345
49 | 2613795.9413 | 1205955.401
50 | 2613809.7419 | 1205967.6098
51 | 2614374.5974 | 1205672.0235
52 | 2614377.3505 | 1205673.9619
53 | 2614401.2286 | 1205690.7738
54 | 2614368.5289 | 1205649.2554
55 | 2614348.806 | 1205678.1276
56 | 2614410.7338 | 1205697.4662
57 | 2614391.806 | 1205650.9849
58 | 2614368.0028 | 1205622.6745
59 | 2614331.0491 | 1205694.4175
60 | 2614423.8645 | 1205706.7112
61 | 2614483.9288 | 1205714.2576
62 | 2614367.1785 | 1205612.9544
63 | 2614328.4211 | 1205708.3585
64 | 2614372.9052 | 1205590.1975
65 | 2614328.5301 | 1205573.2452
66 | 2614372.0866 | 1205518.8238
67 | 2614324.0021 | 1205568.4378
68 | 2614368.9031 | 1205477.3064
69 | 2614307.466 | 1205594.0498
70 | 2614310.4689 | 1205558.0545
71 | 2614558.3849 | 1205770.7578
72 | 2614584.2345 | 1205690.557
73 | 2614314.0275 | 1205711.4225
74 | 2614308.6683 | 1205707.9886
75 | 2614327.4425 | 1205720.0181
76 | 2614279.6684 | 1205689.4072
77 | 2614324.1083 | 1205759.4762
78 | 2614260.4807 | 1205677.1127
79 | 2614343.1723 | 1205722.0648
80 | 2614328.7846 | 1205765.7364
81 | 2614352.9595 | 1205731.1586
82 | 2614344.1645 | 1205782.147
83 | 2614363.6174 | 1205741.0615
84 | 2614425.963 | 1205708.1887
85 | 2614492.5533 | 1205320.1025
86 | 2614567.5651 | 1205285.5139
87 | 2614449.1799 | 1205724.5355
88 | 2614470.1238 | 1205739.2822
89 | 2614487.9109 | 1205752.81
90 | 2614510.4557 | 1205771.6879
91 | 2614558.6208 | 1205284.4314
92 | 2614572.5525 | 1205283.2693
93 | 2614657.643 | 1205576.6272
94 | 2614661.0763 | 1205569.82
95 | 2614578.628 | 1205834.164
96 | 2614557.2597 | 1206697.142
97 | 2614663.9281 | 1206722.7828
98 | 2614512.3968 | 1206583.5708
99 | 2614691.555 | 1206612.3401
100 | 2614854.8977 | 1206230.3321
101 | 2614850.9822 | 1206195.8883
102 | 2614833.4882 | 1206165.0042
103 | 2614829.8536 | 1206169.2579
104 | 2614875.1104 | 1206165.8263
105 | 2614900.3901 | 1206136.4211
106 | 2614890.0218 | 1206116.1842
107 | 2614927.5722 | 1206110.246
108 | 2614943.387 | 1206143.4667
109 | 2614901.7597 | 1206056.614
110 | 2614883.5057 | 1206078.9364
111 | 2614912.921 | 1206048.5595
112 | 2614874.6906 | 1206079.337
113 | 2614864.8926 | 1206014.7506
114 | 2614879.8305 | 1206119.5496
115 | 2614716.7672 | 1205955.5904
116 | 2614865.3616 | 1206099.9141
117 | 2614390.5854 | 1206039.9421
118 | 2614376.2038 | 1206035.6081
119 | 2614372.2357 | 1205982.2581
120 | 2614289.475 | 1205787.6646
121 | 2614291.0592 | 1205783.5439
122 | 2614851.1798 | 1205807.9408
123 | 2614869.3594 | 1205803.6057
124 | 2614854.5042 | 1205800.4722
125 | 2614870.9866 | 1205798.6882
126 | 2614878.4552 | 1205806.1855
127 | 2614860.3565 | 1205787.5968
128 | 2614897.1573 | 1205607.5226
129 | 2614817.7168 | 1205620.3216
130 | 2614819.198 | 1205161.5144
131 | 2614939.8959 | 1205240.1497
132 | 2614805.0687 | 1205124.7409
133 | 2615123.0616 | 1205384.867
134 | 2615121.0864 | 1205384.3163
135 | 2614785.0191 | 1205610.8412
136 | 2614804.8575 | 1205431.8976
137 | 2614760.0733 | 1205076.894
138 | 2614779.4343 | 1205095.8659
139 | 2614735.0664 | 1205041.5209
140 | 2614539.2531 | 1205117.4087
141 | 2614510.7583 | 1205071.2144
142 | 2614504.961 | 1205062.3621
143 | 2614505.9009 | 1205050.9281
144 | 2614189.5083 | 1205522.2433
145 | 2614207.8624 | 1205492.634
146 | 2614230.7261 | 1205541.9975
147 | 2614232.2645 | 1205539.6995
148 | 2614240.6742 | 1205527.1377
149 | 2614247.1858 | 1205517.4111
150 | 2614251.5389 | 1205510.9088
151 | 2614265.9546 | 1205567.0613
152 | 2614285.9054 | 1205536.7852
153 | 2614305.2811 | 1205554.0742
154 | 2614265.9212 | 1205493.8696
155 | 2614298.115 | 1205564.9241
156 | 2614287.369 | 1205581.1941
157 | 2614307.0074 | 1205594.7602
158 | 2614368.3618 | 1205745.4698
159 | 2614619.4432 | 1205863.0126
160 | 2614570.0405 | 1205844.0374
161 | 2614601.2828 | 1205875.1972
162 | 2614627.8682 | 1205870.0711
163 | 2614556.5608 | 1205832.8652
164 | 2614572.5586 | 1205846.4686
165 | 2614558.0308 | 1205891.4676
166 | 2614564.3072 | 1205906.191
167 | 2614530.1827 | 1205875.0022
168 | 2614298.8594 | 1205634.881

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1