## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5048-10_1_3_node_39 | 0.4 | n |  | TRUE
1 | bus_LV_5048-10_1_3_node_28 | 0.4 | n |  | TRUE
2 | bus_LV_5048-10_1_3_node_41 | 0.4 | n |  | TRUE
3 | bus_LV_5048-10_1_3_node_42 | 0.4 | n |  | TRUE
4 | bus_LV_5048-10_1_3_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_5048-10_1_3_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_5048-10_1_3_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_5048-10_1_3_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_5048-10_1_3_node_24 | 0.4 | n |  | TRUE
9 | bus_LV_5048-10_1_3_node_84 | 0.4 | n |  | TRUE
10 | bus_LV_5048-10_1_3_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_5048-10_1_3_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_5048-10_1_3_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_5048-10_1_3_node_25 | 0.4 | n |  | TRUE
14 | bus_LV_5048-10_1_3_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_5048-10_1_3_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_5048-10_1_3_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_5048-10_1_3_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_5048-10_1_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_5048-10_1_3_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_5048-10_1_3_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_5048-10_1_3_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_5048-10_1_3_node_46 | 0.4 | n |  | TRUE
23 | bus_LV_5048-10_1_3_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_5048-10_1_3_node_50 | 0.4 | n |  | TRUE
25 | bus_LV_5048-10_1_3_node_51 | 0.4 | n |  | TRUE
26 | bus_LV_5048-10_1_3_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_5048-10_1_3_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_5048-10_1_3_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_5048-10_1_3_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_5048-10_1_3_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_5048-10_1_3_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_5048-10_1_3_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_5048-10_1_3_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_5048-10_1_3_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_5048-10_1_3_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_5048-10_1_3_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_5048-10_1_3_node_63 | 0.4 | n |  | TRUE
38 | bus_LV_5048-10_1_3_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_5048-10_1_3_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_5048-10_1_3_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_5048-10_1_3_node_85 | 0.4 | n |  | TRUE
42 | bus_LV_5048-10_1_3_node_86 | 0.4 | n |  | TRUE
43 | bus_MV_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5048-10_1_3_load_39 | 0 | 0.0032522 | 0.00081508 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5048-10_1_3_load_41 | 2 | 0.0025994 | 0.00065147 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5048-10_1_3_load_42 | 3 | 0.00050915 | 0.0001276 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5048-10_1_3_load_20 | 4 | 0.0018399 | 0.00046113 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5048-10_1_3_load_21 | 5 | 0.0019073 | 0.00047801 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5048-10_1_3_load_22 | 6 | 0.0022776 | 0.00057081 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5048-10_1_3_load_23 | 7 | 0.0018698 | 0.00046861 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5048-10_1_3_load_24 | 8 | 0.0020265 | 0.00050788 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5048-10_1_3_load_83 | 10 | 0.0040624 | 0.0010181 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5048-10_1_3_load_40 | 11 | 0.0023238 | 0.0005824 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5048-10_1_3_load_29 | 12 | 0.0084819 | 0.0021258 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5048-10_1_3_load_25 | 13 | 0.005403 | 0.0013541 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5048-10_1_3_load_26 | 14 | 0.0037571 | 0.00094163 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5048-10_1_3_load_78 | 16 | 0.0052787 | 0.001323 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5048-10_1_3_load_47 | 17 | 0.00010673 | 2.675e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5048-10_1_3_load_44 | 18 | 0.012768 | 0.0032001 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5048-10_1_3_load_45 | 19 | 0.00012617 | 3.1621e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5048-10_1_3_load_43 | 20 | 0.00013291 | 3.331e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5048-10_1_3_load_48 | 21 | 0.00011189 | 2.8043e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5048-10_1_3_load_46 | 22 | 0.00010744 | 2.6927e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5048-10_1_3_load_50 | 24 | 9.2894e-05 | 2.3281e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5048-10_1_3_load_51 | 25 | 0.00017448 | 4.373e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5048-10_1_3_load_52 | 26 | 0.0017334 | 0.00043442 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5048-10_1_3_load_53 | 27 | 0.00041386 | 0.00010372 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5048-10_1_3_load_55 | 29 | 0.00012392 | 3.1057e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5048-10_1_3_load_57 | 30 | 0.00010012 | 2.5092e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5048-10_1_3_load_58 | 31 | 9.2985e-05 | 2.3304e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5048-10_1_3_load_59 | 32 | 0.00032273 | 8.0885e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5048-10_1_3_load_60 | 33 | 9.8986e-05 | 2.4808e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5048-10_1_3_load_61 | 34 | 0.00010667 | 2.6733e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5048-10_1_3_load_65 | 38 | 0.00079507 | 0.00019926 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5048-10_1_3_load_81 | 39 | 0.0009141 | 0.0002291 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5048-10_1_3_load_85 | 41 | 0.001014 | 0.00025412 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5048-10_1_3_load_86 | 42 | 0.0010035 | 0.00025151 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5048-10_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.048166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5048-10_1_3_line_1 | NAYY 4x150 SE | 1 | 14 | 0.01651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5048-10_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0094928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5048-10_1_3_line_3 | NAYY 4x150 SE | 3 | 20 | 0.10947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5048-10_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.011936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5048-10_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0036321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5048-10_1_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.00019216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5048-10_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.011868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5048-10_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5048-10_1_3_line_9 | NAYY 4x150 SE | 8 | 11 | 0.0071942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5048-10_1_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.18173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5048-10_1_3_line_11 | NAYY 4x150 SE | 10 | 40 | 0.049549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5048-10_1_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.024406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5048-10_1_3_line_13 | NAYY 4x150 SE | 12 | 15 | 0.17869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5048-10_1_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.027047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5048-10_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.23593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5048-10_1_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.28119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5048-10_1_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.36122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5048-10_1_3_line_18 | NAYY 4x150 SE | 17 | 21 | 0.18206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5048-10_1_3_line_19 | NAYY 4x150 SE | 17 | 22 | 0.023056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5048-10_1_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.015142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5048-10_1_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.0087713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5048-10_1_3_line_22 | NAYY 4x150 SE | 19 | 22 | 0.031592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5048-10_1_3_line_23 | NAYY 4x150 SE | 21 | 23 | 0.15247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5048-10_1_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.020805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5048-10_1_3_line_25 | NAYY 4x150 SE | 23 | 25 | 0.052044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5048-10_1_3_line_26 | NAYY 4x150 SE | 23 | 26 | 0.037166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5048-10_1_3_line_27 | NAYY 4x150 SE | 24 | 27 | 0.065883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5048-10_1_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.028117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5048-10_1_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.13715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5048-10_1_3_line_30 | NAYY 4x150 SE | 29 | 30 | 0.0022931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5048-10_1_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.01373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5048-10_1_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.018353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5048-10_1_3_line_33 | NAYY 4x150 SE | 32 | 33 | 0.020549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5048-10_1_3_line_34 | NAYY 4x150 SE | 33 | 34 | 0.010593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5048-10_1_3_line_35 | NAYY 4x150 SE | 34 | 35 | 0.037423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5048-10_1_3_line_36 | NAYY 4x150 SE | 35 | 36 | 0.015073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5048-10_1_3_line_37 | NAYY 4x150 SE | 36 | 39 | 0.056377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5048-10_1_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.029887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5048-10_1_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0041421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5048-10_1_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.11623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5048-10_1_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.014964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5048-10_1_3_trafo_27 | 0.25 MVA 20/0.4 kV | 43 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2715381.3306 | 1147250.0682 | 2715354.7005 | 1147244.5549 | 2715361.6327 | 1147224.7632
1 | 2715381.3306 | 1147250.0682 | 2715378.9618 | 1147266.4073
2 | 2714887.8153 | 1147310.3688 | 2714888.9576 | 1147319.7927
3 | 2714888.9576 | 1147319.7927 | 2714894.3527 | 1147364.3002 | 2714912.2268 | 1147391.0476 | 2714927.9561 | 1147419.4497
4 | 2715306.5805 | 1147739.6008 | 2715305.7347 | 1147727.6949
5 | 2715305.4773 | 1147724.072 | 2715305.7347 | 1147727.6949
6 | 2715306.5805 | 1147739.6008 | 2715306.5941 | 1147739.7924
7 | 2715304.6363 | 1147712.2338 | 2715305.4773 | 1147724.072
8 | 2715212.1611 | 1148054.9489 | 2715306.5941 | 1147739.7924
9 | 2715304.6363 | 1147712.2338 | 2715304.1265 | 1147705.0577
10 | 2715212.1611 | 1148054.9489 | 2715196.1241 | 1148078.9363 | 2715168.1944 | 1148177.7464 | 2715151.6873 | 1148225.1461
11 | 2715135.3917 | 1148271.9383 | 2715151.6873 | 1148225.1461
12 | 2715307.1322 | 1147681.0951 | 2715304.505 | 1147689.1587 | 2715303.8643 | 1147701.3657 | 2715304.1265 | 1147705.0577
13 | 2715300.9497 | 1147508.8479 | 2715309.8372 | 1147556.2607 | 2715323.2834 | 1147644.8438 | 2715323.1125 | 1147653.7687 | 2715321.0186 | 1147660.8223 | 2715307.1331 | 1147681.0925 | 2715307.1322 | 1147681.0951
14 | 2715378.9618 | 1147266.4073 | 2715376.6126 | 1147282.6108 | 2715375.0736 | 1147293.1732
15 | 2715300.9497 | 1147508.8479 | 2715299.644 | 1147491.1667 | 2715299.429 | 1147464.6671 | 2715301.8478 | 1147456.6969 | 2715306.4519 | 1147447.7456 | 2715335.4549 | 1147407.1177 | 2715348.1745 | 1147394.0078 | 2715354.1758 | 1147381.9034 | 2715367.5995 | 1147344.4686 | 2715375.0736 | 1147293.1732
16 | 2715375.0736 | 1147293.1732 | 2715624.4856 | 1147423.0224
17 | 2714939.9694 | 1147495.8127 | 2715300.9497 | 1147508.8479
18 | 2714939.9694 | 1147495.8127 | 2714944.9398 | 1147572.6035 | 2714839.8317 | 1147571.9434
19 | 2714938.4801 | 1147472.8046 | 2714939.9694 | 1147495.8127
20 | 2714932.2056 | 1147427.1228 | 2714935.9624 | 1147433.9064 | 2714936.4396 | 1147441.2782
21 | 2714932.2056 | 1147427.1228 | 2714927.9561 | 1147419.4497
22 | 2714936.4396 | 1147441.2782 | 2714938.4801 | 1147472.8046
23 | 2714687.3695 | 1147570.986 | 2714839.8317 | 1147571.9434
24 | 2714687.3695 | 1147570.986 | 2714692.961 | 1147585.9801 | 2714694.9098 | 1147590.3692
25 | 2714687.3695 | 1147570.986 | 2714679.9 | 1147557.3904 | 2714671.4678 | 1147545.9335 | 2714659.5458 | 1147533.3761 | 2714655.6221 | 1147530.2911
26 | 2714687.3695 | 1147570.986 | 2714707.6969 | 1147539.8715
27 | 2714721.6457 | 1147650.5835 | 2714694.9098 | 1147590.3692
28 | 2714733.0557 | 1147676.281 | 2714721.6457 | 1147650.5835
29 | 2714733.0557 | 1147676.281 | 2714772.4152 | 1147768.8142 | 2714784.732 | 1147791.6639 | 2714786.7086 | 1147797.183 | 2714787.4351 | 1147801.3885 | 2714787.4819 | 1147801.8894
30 | 2714787.4819 | 1147801.8894 | 2714787.6953 | 1147804.1725
31 | 2714787.6953 | 1147804.1725 | 2714787.8818 | 1147806.1669 | 2714787.7155 | 1147817.893
32 | 2714787.7155 | 1147817.893 | 2714787.5911 | 1147826.6639 | 2714787.8444 | 1147832.317 | 2714788.4769 | 1147836.1884
33 | 2714788.4769 | 1147836.1884 | 2714788.6425 | 1147837.2021 | 2714790.0788 | 1147842.4552 | 2714795.447 | 1147855.4677
34 | 2714799.4869 | 1147865.2604 | 2714795.447 | 1147855.4677
35 | 2714813.759 | 1147899.8555 | 2714799.4869 | 1147865.2604
36 | 2714806.9121 | 1147913.2785 | 2714809.9011 | 1147907.9986 | 2714813.759 | 1147899.8555
37 | 2714806.9121 | 1147913.2785 | 2714802.5418 | 1147915.6636 | 2714790.3392 | 1147917.8882 | 2714786.583 | 1147920.6964 | 2714784.8577 | 1147924.5661 | 2714784.3374 | 1147930.1043 | 2714784.6535 | 1147954.6078
38 | 2714806.9121 | 1147913.2785 | 2714822.1541 | 1147939.0082
39 | 2714822.1541 | 1147939.0082 | 2714822.5397 | 1147943.1324
40 | 2715135.3917 | 1148271.9383 | 2715139.2905 | 1148270.5007 | 2715161.2028 | 1148261.4021 | 2715168.1185 | 1148259.6664 | 2715172.6641 | 1148259.3531 | 2715176.3117 | 1148260.2122 | 2715181.249 | 1148262.7193 | 2715206.0096 | 1148282.2166 | 2715212.8182 | 1148286.0827 | 2715230.2149 | 1148292.186 | 2715239.1323 | 1148295.739
41 | 2715239.1323 | 1148295.739 | 2715246.3076 | 1148298.5979 | 2715249.8268 | 1148300.9445 | 2715251.9309 | 1148303.0974

## bus_geodata
| x | y | coords
0 | 2715361.6327 | 1147224.7632
1 | 2715381.3306 | 1147250.0682
2 | 2714887.8153 | 1147310.3688
3 | 2714888.9576 | 1147319.7927
4 | 2715305.7347 | 1147727.6949
5 | 2715306.5805 | 1147739.6008
6 | 2715305.4773 | 1147724.072
7 | 2715306.5941 | 1147739.7924
8 | 2715304.6363 | 1147712.2338
9 | 2715212.1611 | 1148054.9489
10 | 2715151.6873 | 1148225.1461
11 | 2715304.1265 | 1147705.0577
12 | 2715307.1322 | 1147681.0951
13 | 2715375.0736 | 1147293.1732
14 | 2715378.9618 | 1147266.4073
15 | 2715300.9497 | 1147508.8479
16 | 2715624.4856 | 1147423.0224
17 | 2714939.9694 | 1147495.8127
18 | 2714932.2056 | 1147427.1228
19 | 2714936.4396 | 1147441.2782
20 | 2714927.9561 | 1147419.4497
21 | 2714839.8317 | 1147571.9434
22 | 2714938.4801 | 1147472.8046
23 | 2714687.3695 | 1147570.986
24 | 2714694.9098 | 1147590.3692
25 | 2714655.6221 | 1147530.2911
26 | 2714707.6969 | 1147539.8715
27 | 2714721.6457 | 1147650.5835
28 | 2714733.0557 | 1147676.281
29 | 2714787.4819 | 1147801.8894
30 | 2714787.6953 | 1147804.1725
31 | 2714787.7155 | 1147817.893
32 | 2714788.4769 | 1147836.1884
33 | 2714795.447 | 1147855.4677
34 | 2714799.4869 | 1147865.2604
35 | 2714813.759 | 1147899.8555
36 | 2714806.9121 | 1147913.2785
37 | 2714822.1541 | 1147939.0082
38 | 2714822.5397 | 1147943.1324
39 | 2714784.6535 | 1147954.6078
40 | 2715135.3917 | 1148271.9383
41 | 2715239.1323 | 1148295.739
42 | 2715251.9309 | 1148303.0974
43 | 2715300.9497 | 1147508.8479

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1