## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5048-12_1_3_node_129 | 0.4 | n |  | TRUE
1 | bus_LV_5048-12_1_3_node_21 | 0.4 | n |  | TRUE
2 | bus_LV_5048-12_1_3_node_130 | 0.4 | n |  | TRUE
3 | bus_LV_5048-12_1_3_node_131 | 0.4 | n |  | TRUE
4 | bus_LV_5048-12_1_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_5048-12_1_3_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_5048-12_1_3_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_5048-12_1_3_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_5048-12_1_3_node_14 | 0.4 | n |  | TRUE
9 | bus_LV_5048-12_1_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_5048-12_1_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_5048-12_1_3_node_93 | 0.4 | n |  | TRUE
12 | bus_LV_5048-12_1_3_node_45 | 0.4 | n |  | TRUE
13 | bus_LV_5048-12_1_3_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_5048-12_1_3_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_5048-12_1_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_5048-12_1_3_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_5048-12_1_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_5048-12_1_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_5048-12_1_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_5048-12_1_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_5048-12_1_3_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_5048-12_1_3_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_5048-12_1_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_5048-12_1_3_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_5048-12_1_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_5048-12_1_3_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_5048-12_1_3_node_87 | 0.4 | n |  | TRUE
28 | bus_LV_5048-12_1_3_node_114 | 0.4 | n |  | TRUE
29 | bus_LV_5048-12_1_3_node_155 | 0.4 | n |  | TRUE
30 | bus_LV_5048-12_1_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_5048-12_1_3_node_54 | 0.4 | n |  | TRUE
32 | bus_LV_5048-12_1_3_node_55 | 0.4 | n |  | TRUE
33 | bus_LV_5048-12_1_3_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_5048-12_1_3_node_153 | 0.4 | n |  | TRUE
35 | bus_LV_5048-12_1_3_node_113 | 0.4 | n |  | TRUE
36 | bus_LV_5048-12_1_3_node_154 | 0.4 | n |  | TRUE
37 | bus_LV_5048-12_1_3_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_5048-12_1_3_node_96 | 0.4 | n |  | TRUE
39 | bus_LV_5048-12_1_3_node_156 | 0.4 | n |  | TRUE
40 | bus_LV_5048-12_1_3_node_84 | 0.4 | n |  | TRUE
41 | bus_LV_5048-12_1_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_5048-12_1_3_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_5048-12_1_3_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_5048-12_1_3_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_5048-12_1_3_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_5048-12_1_3_node_106 | 0.4 | n |  | TRUE
47 | bus_LV_5048-12_1_3_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_5048-12_1_3_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_5048-12_1_3_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_5048-12_1_3_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_5048-12_1_3_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_5048-12_1_3_node_86 | 0.4 | n |  | TRUE
53 | bus_LV_5048-12_1_3_node_66 | 0.4 | n |  | TRUE
54 | bus_LV_5048-12_1_3_node_67 | 0.4 | n |  | TRUE
55 | bus_LV_5048-12_1_3_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_5048-12_1_3_node_69 | 0.4 | n |  | TRUE
57 | bus_LV_5048-12_1_3_node_70 | 0.4 | n |  | TRUE
58 | bus_LV_5048-12_1_3_node_71 | 0.4 | n |  | TRUE
59 | bus_LV_5048-12_1_3_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_5048-12_1_3_node_83 | 0.4 | n |  | TRUE
61 | bus_LV_5048-12_1_3_node_100 | 0.4 | n |  | TRUE
62 | bus_LV_5048-12_1_3_node_79 | 0.4 | n |  | TRUE
63 | bus_LV_5048-12_1_3_node_82 | 0.4 | n |  | TRUE
64 | bus_LV_5048-12_1_3_node_81 | 0.4 | n |  | TRUE
65 | bus_LV_5048-12_1_3_node_85 | 0.4 | n |  | TRUE
66 | bus_LV_5048-12_1_3_node_94 | 0.4 | n |  | TRUE
67 | bus_LV_5048-12_1_3_node_95 | 0.4 | n |  | TRUE
68 | bus_LV_5048-12_1_3_node_98 | 0.4 | n |  | TRUE
69 | bus_LV_5048-12_1_3_node_99 | 0.4 | n |  | TRUE
70 | bus_LV_5048-12_1_3_node_101 | 0.4 | n |  | TRUE
71 | bus_MV_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5048-12_1_3_load_129 | 0 | 0.00047633 | 0.00011938 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5048-12_1_3_load_21 | 1 | 0.0011185 | 0.00028031 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5048-12_1_3_load_131 | 3 | 0.00043459 | 0.00010892 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5048-12_1_3_load_10 | 4 | 0.0008087 | 0.00020268 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5048-12_1_3_load_11 | 5 | 0.00095546 | 0.00023946 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5048-12_1_3_load_12 | 6 | 0.00048134 | 0.00012064 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5048-12_1_3_load_13 | 7 | 0.00066311 | 0.00016619 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5048-12_1_3_load_14 | 8 | 0.00079347 | 0.00019886 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5048-12_1_3_load_15 | 9 | 0.00069246 | 0.00017355 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5048-12_1_3_load_42 | 13 | 0.00066123 | 0.00016572 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5048-12_1_3_load_17 | 14 | 0.00035751 | 8.96e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5048-12_1_3_load_20 | 16 | 0.0011244 | 0.0002818 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5048-12_1_3_load_23 | 17 | 0.00053866 | 0.000135 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5048-12_1_3_load_44 | 18 | 0.00067644 | 0.00016953 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5048-12_1_3_load_24 | 19 | 0.00093405 | 0.00023409 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5048-12_1_3_load_30 | 25 | 0.0015615 | 0.00039134 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5048-12_1_3_load_32 | 26 | 0.00013622 | 3.414e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5048-12_1_3_load_87 | 27 | 0.0018206 | 0.0004563 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5048-12_1_3_load_155 | 29 | 0.0018787 | 0.00047085 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5048-12_1_3_load_54 | 31 | 0.00079543 | 0.00019935 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5048-12_1_3_load_153 | 34 | 0.0028648 | 0.00071798 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5048-12_1_3_load_113 | 35 | 0.005303 | 0.001329 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5048-12_1_3_load_154 | 36 | 0.00014481 | 3.6294e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5048-12_1_3_load_53 | 37 | 0.00025062 | 6.2811e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5048-12_1_3_load_96 | 38 | 0.00010312 | 2.5845e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5048-12_1_3_load_156 | 39 | 0.0017487 | 0.00043827 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5048-12_1_3_load_43 | 41 | 0.00073531 | 0.00018429 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5048-12_1_3_load_46 | 42 | 0.0003869 | 9.6965e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5048-12_1_3_load_47 | 43 | 0.0011975 | 0.00030013 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5048-12_1_3_load_78 | 45 | 0.00043683 | 0.00010948 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5048-12_1_3_load_106 | 46 | 0.0020543 | 0.00051484 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5048-12_1_3_load_50 | 48 | 0.00011398 | 2.8566e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5048-12_1_3_load_51 | 49 | 0.00043055 | 0.00010791 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5048-12_1_3_load_52 | 50 | 0.00076253 | 0.00019111 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5048-12_1_3_load_112 | 51 | 0.00021374 | 5.3569e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5048-12_1_3_load_86 | 52 | 0.00010822 | 2.7122e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5048-12_1_3_load_66 | 53 | 0.0022167 | 0.00055556 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5048-12_1_3_load_67 | 54 | 0.0030463 | 0.00076347 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5048-12_1_3_load_68 | 55 | 0.0030542 | 0.00076546 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5048-12_1_3_load_69 | 56 | 0.0069224 | 0.0017349 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5048-12_1_3_load_70 | 57 | 0.0052126 | 0.0013064 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5048-12_1_3_load_71 | 58 | 0.003394 | 0.00085061 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5048-12_1_3_load_83 | 60 | 0.0010129 | 0.00025386 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5048-12_1_3_load_100 | 61 | 0.0041796 | 0.0010475 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5048-12_1_3_load_82 | 63 | 0.0043915 | 0.0011006 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5048-12_1_3_load_81 | 64 | 0.00034466 | 8.638e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5048-12_1_3_load_85 | 65 | 0.00057532 | 0.00014419 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5048-12_1_3_load_94 | 66 | 0.00032423 | 8.126e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5048-12_1_3_load_95 | 67 | 0.00012172 | 3.0505e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5048-12_1_3_load_98 | 68 | 0.00090357 | 0.00022646 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5048-12_1_3_load_101 | 70 | 0.0019074 | 0.00047805 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5048-12_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.29399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5048-12_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.047519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5048-12_1_3_line_2 | NAYY 4x150 SE | 1 | 15 | 0.025446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5048-12_1_3_line_3 | NAYY 4x150 SE | 2 | 3 | 0.026267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5048-12_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.025781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5048-12_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.082604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5048-12_1_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.065411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5048-12_1_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.022244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5048-12_1_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.041485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5048-12_1_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.016582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5048-12_1_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.048344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5048-12_1_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.015841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5048-12_1_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.017785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5048-12_1_3_line_13 | NAYY 4x150 SE | 11 | 66 | 0.03052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5048-12_1_3_line_14 | NAYY 4x150 SE | 11 | 67 | 0.016038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5048-12_1_3_line_15 | NAYY 4x150 SE | 12 | 42 | 0.01727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5048-12_1_3_line_16 | NAYY 4x150 SE | 12 | 43 | 0.018648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5048-12_1_3_line_17 | NAYY 4x150 SE | 13 | 41 | 0.016052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5048-12_1_3_line_18 | NAYY 4x150 SE | 14 | 15 | 0.0062764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5048-12_1_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.015596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5048-12_1_3_line_20 | NAYY 4x150 SE | 16 | 17 | 0.0095629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5048-12_1_3_line_21 | NAYY 4x150 SE | 17 | 18 | 0.013215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5048-12_1_3_line_22 | NAYY 4x150 SE | 18 | 41 | 0.0041654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5048-12_1_3_line_23 | NAYY 4x150 SE | 19 | 20 | 0.021464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5048-12_1_3_line_24 | NAYY 4x150 SE | 19 | 21 | 0.032355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5048-12_1_3_line_25 | NAYY 4x150 SE | 20 | 22 | 0.05875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5048-12_1_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.00197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5048-12_1_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.069978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5048-12_1_3_line_28 | NAYY 4x150 SE | 22 | 25 | 0.02656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5048-12_1_3_line_29 | NAYY 4x150 SE | 23 | 26 | 0.01088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5048-12_1_3_line_30 | NAYY 4x150 SE | 24 | 27 | 0.029816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5048-12_1_3_line_31 | NAYY 4x150 SE | 24 | 28 | 0.10443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5048-12_1_3_line_32 | NAYY 4x150 SE | 25 | 29 | 0.00018943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5048-12_1_3_line_33 | NAYY 4x150 SE | 26 | 33 | 0.072546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5048-12_1_3_line_34 | NAYY 4x150 SE | 27 | 32 | 0.033427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5048-12_1_3_line_35 | NAYY 4x150 SE | 28 | 35 | 0.054886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5048-12_1_3_line_36 | NAYY 4x150 SE | 30 | 31 | 0.021929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5048-12_1_3_line_37 | NAYY 4x150 SE | 30 | 32 | 0.025755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5048-12_1_3_line_38 | NAYY 4x150 SE | 32 | 52 | 0.046255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5048-12_1_3_line_39 | NAYY 4x150 SE | 33 | 47 | 0.099122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5048-12_1_3_line_40 | NAYY 4x150 SE | 33 | 48 | 0.040367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5048-12_1_3_line_41 | NAYY 4x150 SE | 34 | 35 | 0.77155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5048-12_1_3_line_42 | NAYY 4x150 SE | 36 | 37 | 0.027049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5048-12_1_3_line_43 | NAYY 4x150 SE | 36 | 38 | 0.024475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5048-12_1_3_line_44 | NAYY 4x150 SE | 37 | 48 | 0.009009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5048-12_1_3_line_45 | NAYY 4x150 SE | 38 | 67 | 0.016058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5048-12_1_3_line_46 | NAYY 4x150 SE | 39 | 40 | 0.1835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5048-12_1_3_line_47 | NAYY 4x150 SE | 40 | 44 | 0.14946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5048-12_1_3_line_48 | NAYY 4x150 SE | 42 | 44 | 0.080672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5048-12_1_3_line_49 | NAYY 4x150 SE | 42 | 45 | 0.026178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5048-12_1_3_line_50 | NAYY 4x150 SE | 43 | 46 | 0.060779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5048-12_1_3_line_51 | NAYY 4x150 SE | 44 | 60 | 0.018567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5048-12_1_3_line_52 | NAYY 4x150 SE | 45 | 62 | 0.025163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5048-12_1_3_line_53 | NAYY 4x150 SE | 47 | 49 | 0.051609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5048-12_1_3_line_54 | NAYY 4x150 SE | 47 | 50 | 0.024518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5048-12_1_3_line_55 | NAYY 4x150 SE | 50 | 51 | 0.026936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5048-12_1_3_line_56 | NAYY 4x150 SE | 52 | 65 | 0.015829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5048-12_1_3_line_57 | NAYY 4x150 SE | 53 | 54 | 0.018224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5048-12_1_3_line_58 | NAYY 4x150 SE | 53 | 55 | 0.0023562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5048-12_1_3_line_59 | NAYY 4x150 SE | 54 | 56 | 0.0036729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5048-12_1_3_line_60 | NAYY 4x150 SE | 55 | 57 | 0.019624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5048-12_1_3_line_61 | NAYY 4x150 SE | 56 | 58 | 0.0038616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5048-12_1_3_line_62 | NAYY 4x150 SE | 57 | 59 | 0.014614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5048-12_1_3_line_63 | NAYY 4x150 SE | 59 | 60 | 0.046707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5048-12_1_3_line_64 | NAYY 4x150 SE | 59 | 61 | 0.022808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5048-12_1_3_line_65 | NAYY 4x150 SE | 61 | 69 | 0.00034353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5048-12_1_3_line_66 | NAYY 4x150 SE | 62 | 63 | 0.072137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5048-12_1_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.0046688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5048-12_1_3_line_68 | NAYY 4x150 SE | 68 | 69 | 0.035291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5048-12_1_3_line_69 | NAYY 4x150 SE | 69 | 70 | 0.054397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5048-12_1_3_trafo_80 | 0.25 MVA 20/0.4 kV | 71 | 44 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2716628.5625 | 1143838.6521 | 2716422.4984 | 1143628.9641
1 | 2716432.797 | 1143582.5746 | 2716422.4984 | 1143628.9641
2 | 2716614.3824 | 1143859.5124 | 2716616.7684 | 1143853.3989 | 2716628.5625 | 1143838.6521
3 | 2716440.1589 | 1143607.7892 | 2716432.797 | 1143582.5746
4 | 2716737.3457 | 1143816.6103 | 2716737.5978 | 1143816.2776 | 2716753.3662 | 1143796.411
5 | 2716737.3457 | 1143816.6103 | 2716687.4596 | 1143882.4497
6 | 2716753.3662 | 1143796.411 | 2716781.5414 | 1143760.9131 | 2716793.6824 | 1143744.9064
7 | 2716674.1396 | 1143900.2651 | 2716686.6608 | 1143883.504 | 2716687.4596 | 1143882.4497
8 | 2716818.8816 | 1143711.9526 | 2716811.8025 | 1143721.0166 | 2716793.6824 | 1143744.9064
9 | 2716665.8965 | 1143914.5677 | 2716670.2938 | 1143905.4132 | 2716674.1396 | 1143900.2651
10 | 2716854.0612 | 1143678.8845 | 2716821.8453 | 1143708.158 | 2716818.8816 | 1143711.9526
11 | 2716670.9268 | 1143929.5083 | 2716667.6777 | 1143922.2295 | 2716666.7514 | 1143918.8537 | 2716665.8965 | 1143914.5677
12 | 2716665.8965 | 1143914.5677 | 2716663.2716 | 1143911.1813 | 2716654.1944 | 1143901.1879
13 | 2716854.0612 | 1143678.8845 | 2716847.2296 | 1143675.9836 | 2716835.4423 | 1143672.1527 | 2716831.5686 | 1143670.1319 | 2716826.486 | 1143666.2308
14 | 2716854.0612 | 1143678.8845 | 2716865.9298 | 1143668.0971
15 | 2716670.9268 | 1143929.5083 | 2716684.2617 | 1143918.4922
16 | 2716670.9268 | 1143929.5083 | 2716656.4724 | 1143941.2901
17 | 2716644.6039 | 1143888.3165 | 2716654.1944 | 1143901.1879 | 2716654.1944 | 1143901.1879
18 | 2716614.3824 | 1143859.5124 | 2716610.3217 | 1143861.602 | 2716609.2636 | 1143862.9447
19 | 2716614.3824 | 1143859.5124 | 2716622.2566 | 1143862.9558 | 2716627.4026 | 1143867.7037
20 | 2716634.2191 | 1143874.3791 | 2716633.298 | 1143873.1428 | 2716627.4026 | 1143867.7037
21 | 2716634.2191 | 1143874.3791 | 2716642.1151 | 1143884.9763
22 | 2716642.1151 | 1143884.9763 | 2716644.6039 | 1143888.3165
23 | 2717039.4307 | 1143695.6337 | 2717025.909 | 1143678.9644
24 | 2717005.5261 | 1143653.8368 | 2717025.909 | 1143678.9644
25 | 2717039.4307 | 1143695.6337 | 2716997.2541 | 1143736.6432
26 | 2717005.5261 | 1143653.8368 | 2717003.9802 | 1143655.0632
27 | 2716945.8708 | 1143784.29 | 2716997.2541 | 1143736.6432
28 | 2716997.2541 | 1143736.6432 | 2716980.5766 | 1143715.9718
29 | 2717003.9802 | 1143655.0632 | 2716997.2638 | 1143646.5039
30 | 2716945.8708 | 1143784.29 | 2716926.1137 | 1143761.959
31 | 2716912.6837 | 1143860.4758 | 2716893.9876 | 1143832.7837 | 2716945.8708 | 1143784.29
32 | 2716980.4577 | 1143715.8244 | 2716980.5766 | 1143715.9718
33 | 2716952.4798 | 1143589.4315 | 2716997.2638 | 1143646.5039
34 | 2716903.9641 | 1143736.9237 | 2716926.1137 | 1143761.959
35 | 2716912.6837 | 1143860.4758 | 2716919.3408 | 1143867.9988 | 2716924.9444 | 1143876.7355 | 2716926.5966 | 1143887.4636 | 2716921.2652 | 1143896.3996 | 2716912.5743 | 1143906.3363
36 | 2716938.107 | 1143737.1189 | 2716923.8168 | 1143720.4529
37 | 2716923.8168 | 1143720.4529 | 2716903.9641 | 1143736.9237
38 | 2716903.9641 | 1143736.9237 | 2716868.074 | 1143766.1028
39 | 2716888.6482 | 1143513.4544 | 2716952.4798 | 1143589.4315
40 | 2716952.4798 | 1143589.4315 | 2716922.6078 | 1143616.5823
41 | 2716912.5743 | 1143906.3363 | 2717587.925 | 1144279.4162
42 | 2716895.9246 | 1143640.8347 | 2716915.9411 | 1143622.6417
43 | 2716895.9246 | 1143640.8347 | 2716877.8125 | 1143657.2968
44 | 2716915.9411 | 1143622.6417 | 2716922.6078 | 1143616.5823
45 | 2716877.8125 | 1143657.2968 | 2716865.9298 | 1143668.0971
46 | 2716837.4208 | 1143977.8076 | 2716836.1044 | 1143992.581 | 2716839.6088 | 1144003.3339 | 2716845.2602 | 1144009.6031 | 2716853.2179 | 1144013.8712 | 2716860.3815 | 1144016.6785 | 2716863.6023 | 1144020.6436 | 2716863.2713 | 1144027.0081 | 2716859.4046 | 1144034.9497 | 2716844.2965 | 1144059.3179 | 2716838.0953 | 1144070.7165 | 2716833.9296 | 1144083.3777 | 2716829.9714 | 1144096.0429 | 2716814.9757 | 1144122.5592 | 2716804.8624 | 1144131.158
47 | 2716741.0553 | 1143975.9407 | 2716803.7522 | 1143921.8625 | 2716809.1158 | 1143927.5146 | 2716814.9228 | 1143936.4664 | 2716818.0203 | 1143946.8 | 2716828.1056 | 1143958.303 | 2716835.7402 | 1143968.9358 | 2716837.4208 | 1143977.8076
48 | 2716684.2617 | 1143918.4922 | 2716741.0553 | 1143975.9407
49 | 2716684.2617 | 1143918.4922 | 2716704.3181 | 1143901.6687
50 | 2716611.342 | 1143981.9451 | 2716640.6936 | 1143954.1513 | 2716656.4724 | 1143941.2901
51 | 2716741.0553 | 1143975.9407 | 2716727.2038 | 1143988.3052
52 | 2716723.5968 | 1143885.4976 | 2716704.3181 | 1143901.6687
53 | 2716888.6482 | 1143513.4544 | 2716874.1875 | 1143497.6192 | 2716867.548 | 1143494.7108 | 2716862.4095 | 1143493.6883 | 2716858.0811 | 1143493.7045 | 2716854.2475 | 1143494.7643 | 2716846.9303 | 1143500.6181
54 | 2716888.6482 | 1143513.4544 | 2716873.3681 | 1143532.6281
55 | 2716873.3681 | 1143532.6281 | 2716856.5806 | 1143553.6932
56 | 2716868.074 | 1143766.1028 | 2716855.7921 | 1143776.0882
57 | 2716664.2869 | 1144042.8895 | 2716650.3912 | 1144054.6803
58 | 2716664.2869 | 1144042.8895 | 2716666.0835 | 1144041.365
59 | 2716650.3912 | 1144054.6803 | 2716647.5907 | 1144057.0567
60 | 2716681.0468 | 1144028.6683 | 2716666.0835 | 1144041.365
61 | 2716647.5907 | 1144057.0567 | 2716644.6462 | 1144059.5551
62 | 2716692.1897 | 1144019.2132 | 2716681.0468 | 1144028.6683
63 | 2716692.1897 | 1144019.2132 | 2716700.1535 | 1144012.4516 | 2716727.2038 | 1143988.3052
64 | 2716692.1897 | 1144019.2132 | 2716708.4339 | 1144035.2242
65 | 2716708.6786 | 1144035.4653 | 2716708.4339 | 1144035.2242
66 | 2716723.5968 | 1143885.4976 | 2716729.4165 | 1143892.2148 | 2716733.4035 | 1143893.9375 | 2716737.6377 | 1143893.6081 | 2716742.3427 | 1143890.4081 | 2716781.3868 | 1143860.8528
67 | 2716852.1695 | 1143779.0334 | 2716855.7921 | 1143776.0882
68 | 2716708.6786 | 1144035.4653 | 2716715.7613 | 1144042.4515 | 2716727.6558 | 1144057.7809 | 2716729.5932 | 1144063.3954
69 | 2716752.4367 | 1144029.2746 | 2716743.431 | 1144020.3721 | 2716738.4364 | 1144017.4957 | 2716733.2783 | 1144017.507 | 2716725.2888 | 1144020.4322 | 2716708.6786 | 1144035.4653

## bus_geodata
| x | y | coords
0 | 2716422.4984 | 1143628.9641
1 | 2716628.5625 | 1143838.6521
2 | 2716432.797 | 1143582.5746
3 | 2716440.1589 | 1143607.7892
4 | 2716737.3457 | 1143816.6103
5 | 2716753.3662 | 1143796.411
6 | 2716687.4596 | 1143882.4497
7 | 2716793.6824 | 1143744.9064
8 | 2716674.1396 | 1143900.2651
9 | 2716818.8816 | 1143711.9526
10 | 2716665.8965 | 1143914.5677
11 | 2716854.0612 | 1143678.8845
12 | 2716670.9268 | 1143929.5083
13 | 2716654.1944 | 1143901.1879
14 | 2716609.2636 | 1143862.9447
15 | 2716614.3824 | 1143859.5124
16 | 2716627.4026 | 1143867.7037
17 | 2716634.2191 | 1143874.3791
18 | 2716642.1151 | 1143884.9763
19 | 2717025.909 | 1143678.9644
20 | 2717039.4307 | 1143695.6337
21 | 2717005.5261 | 1143653.8368
22 | 2716997.2541 | 1143736.6432
23 | 2717003.9802 | 1143655.0632
24 | 2716945.8708 | 1143784.29
25 | 2716980.5766 | 1143715.9718
26 | 2716997.2638 | 1143646.5039
27 | 2716926.1137 | 1143761.959
28 | 2716912.6837 | 1143860.4758
29 | 2716980.4577 | 1143715.8244
30 | 2716923.8168 | 1143720.4529
31 | 2716938.107 | 1143737.1189
32 | 2716903.9641 | 1143736.9237
33 | 2716952.4798 | 1143589.4315
34 | 2717587.925 | 1144279.4162
35 | 2716912.5743 | 1143906.3363
36 | 2716895.9246 | 1143640.8347
37 | 2716915.9411 | 1143622.6417
38 | 2716877.8125 | 1143657.2968
39 | 2716804.8624 | 1144131.158
40 | 2716837.4208 | 1143977.8076
41 | 2716644.6039 | 1143888.3165
42 | 2716684.2617 | 1143918.4922
43 | 2716656.4724 | 1143941.2901
44 | 2716741.0553 | 1143975.9407
45 | 2716704.3181 | 1143901.6687
46 | 2716611.342 | 1143981.9451
47 | 2716888.6482 | 1143513.4544
48 | 2716922.6078 | 1143616.5823
49 | 2716846.9303 | 1143500.6181
50 | 2716873.3681 | 1143532.6281
51 | 2716856.5806 | 1143553.6932
52 | 2716868.074 | 1143766.1028
53 | 2716664.2869 | 1144042.8895
54 | 2716650.3912 | 1144054.6803
55 | 2716666.0835 | 1144041.365
56 | 2716647.5907 | 1144057.0567
57 | 2716681.0468 | 1144028.6683
58 | 2716644.6462 | 1144059.5551
59 | 2716692.1897 | 1144019.2132
60 | 2716727.2038 | 1143988.3052
61 | 2716708.4339 | 1144035.2242
62 | 2716723.5968 | 1143885.4976
63 | 2716781.3868 | 1143860.8528
64 | 2716852.1695 | 1143779.0334
65 | 2716855.7921 | 1143776.0882
66 | 2716826.486 | 1143666.2308
67 | 2716865.9298 | 1143668.0971
68 | 2716729.5932 | 1144063.3954
69 | 2716708.6786 | 1144035.4653
70 | 2716752.4367 | 1144029.2746
71 | 2716741.0553 | 1143975.9407

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1