## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5049-5_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5049-5_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5049-5_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5049-5_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5049-5_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5049-5_0_2_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_5049-5_0_2_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_5049-5_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5049-5_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5049-5_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_5049-5_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5049-5_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_5049-5_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_5049-5_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5049-5_0_2_node_60 | 0.4 | n |  | TRUE
15 | bus_LV_5049-5_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_5049-5_0_2_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_5049-5_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_5049-5_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_5049-5_0_2_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_5049-5_0_2_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_5049-5_0_2_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_5049-5_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_5049-5_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_5049-5_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_5049-5_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_5049-5_0_2_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_5049-5_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_5049-5_0_2_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_5049-5_0_2_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_5049-5_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_5049-5_0_2_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_5049-5_0_2_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_5049-5_0_2_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_5049-5_0_2_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_5049-5_0_2_node_81 | 0.4 | n |  | TRUE
36 | bus_LV_5049-5_0_2_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_5049-5_0_2_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_5049-5_0_2_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_5049-5_0_2_node_59 | 0.4 | n |  | TRUE
40 | bus_LV_5049-5_0_2_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_5049-5_0_2_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_5049-5_0_2_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_5049-5_0_2_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_5049-5_0_2_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_5049-5_0_2_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_5049-5_0_2_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_5049-5_0_2_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_5049-5_0_2_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_5049-5_0_2_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_5049-5_0_2_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_5049-5_0_2_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_5049-5_0_2_node_71 | 0.4 | n |  | TRUE
53 | bus_LV_5049-5_0_2_node_79 | 0.4 | n |  | TRUE
54 | bus_LV_5049-5_0_2_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_5049-5_0_2_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_5049-5_0_2_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_5049-5_0_2_node_77 | 0.4 | n |  | TRUE
58 | bus_LV_5049-5_0_2_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_5049-5_0_2_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_5049-5_0_2_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_5049-5_0_2_node_169 | 0.4 | n |  | TRUE
62 | bus_LV_5049-5_0_2_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_5049-5_0_2_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_5049-5_0_2_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_5049-5_0_2_node_69 | 0.4 | n |  | TRUE
66 | bus_LV_5049-5_0_2_node_70 | 0.4 | n |  | TRUE
67 | bus_LV_5049-5_0_2_node_72 | 0.4 | n |  | TRUE
68 | bus_LV_5049-5_0_2_node_73 | 0.4 | n |  | TRUE
69 | bus_LV_5049-5_0_2_node_82 | 0.4 | n |  | TRUE
70 | bus_LV_5049-5_0_2_node_74 | 0.4 | n |  | TRUE
71 | bus_LV_5049-5_0_2_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_5049-5_0_2_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_5049-5_0_2_node_80 | 0.4 | n |  | TRUE
74 | bus_LV_5049-5_0_2_node_78 | 0.4 | n |  | TRUE
75 | bus_LV_5049-5_0_2_node_170 | 0.4 | n |  | TRUE
76 | bus_MV_0_node_28 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5049-5_0_2_load_0 | 0 | 0.0022137 | 0.0005548 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5049-5_0_2_load_1 | 1 | 0.0017564 | 0.00044019 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5049-5_0_2_load_2 | 2 | 0.0015913 | 0.00039882 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5049-5_0_2_load_3 | 3 | 0.0015603 | 0.00039105 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5049-5_0_2_load_4 | 4 | 0.001495 | 0.00037468 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5049-5_0_2_load_32 | 6 | 0.00087957 | 0.00022044 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5049-5_0_2_load_5 | 7 | 0.0010637 | 0.00026659 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5049-5_0_2_load_8 | 10 | 0.0011304 | 0.0002833 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5049-5_0_2_load_9 | 11 | 0.0010957 | 0.00027461 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5049-5_0_2_load_10 | 12 | 0.00061631 | 0.00015446 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5049-5_0_2_load_11 | 13 | 0.0007363 | 0.00018453 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5049-5_0_2_load_13 | 17 | 0.0004765 | 0.00011942 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5049-5_0_2_load_14 | 18 | 0.00061262 | 0.00015354 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5049-5_0_2_load_21 | 19 | 0.00067143 | 0.00016828 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5049-5_0_2_load_23 | 20 | 0.00083855 | 0.00021016 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5049-5_0_2_load_15 | 21 | 0.00092606 | 0.00023209 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5049-5_0_2_load_17 | 22 | 0.00074418 | 0.00018651 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5049-5_0_2_load_18 | 23 | 0.00059715 | 0.00014966 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5049-5_0_2_load_19 | 24 | 0.0005587 | 0.00014002 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5049-5_0_2_load_20 | 25 | 0.00056164 | 0.00014076 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5049-5_0_2_load_22 | 26 | 0.00024127 | 6.0468e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5049-5_0_2_load_25 | 28 | 0.00027274 | 6.8355e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5049-5_0_2_load_26 | 29 | 0.00030979 | 7.764e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5049-5_0_2_load_27 | 30 | 0.00035108 | 8.7989e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5049-5_0_2_load_29 | 31 | 0.0032019 | 0.00080248 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5049-5_0_2_load_28 | 32 | 0.00035948 | 9.0093e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5049-5_0_2_load_30 | 33 | 0.00070145 | 0.0001758 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5049-5_0_2_load_31 | 34 | 0.0018187 | 0.00045582 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5049-5_0_2_load_81 | 35 | 0.0022032 | 0.00055218 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5049-5_0_2_load_34 | 36 | 0.0021348 | 0.00053503 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5049-5_0_2_load_36 | 38 | 0.0014991 | 0.00037572 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5049-5_0_2_load_59 | 39 | 0.00092076 | 0.00023076 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5049-5_0_2_load_37 | 40 | 0.00077706 | 0.00019475 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5049-5_0_2_load_38 | 41 | 0.00084268 | 0.00021119 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5049-5_0_2_load_39 | 42 | 0.0010069 | 0.00025234 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5049-5_0_2_load_40 | 43 | 0.0014252 | 0.00035718 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5049-5_0_2_load_66 | 44 | 0.00068328 | 0.00017125 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5049-5_0_2_load_41 | 45 | 0.0011547 | 0.00028941 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5049-5_0_2_load_47 | 46 | 0.0013725 | 0.00034399 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5049-5_0_2_load_42 | 47 | 0.0013926 | 0.00034903 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5049-5_0_2_load_43 | 48 | 0.0011065 | 0.00027731 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5049-5_0_2_load_46 | 51 | 0.00068728 | 0.00017225 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5049-5_0_2_load_71 | 52 | 0.0011017 | 0.0002761 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5049-5_0_2_load_79 | 53 | 0.00094968 | 0.00023801 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5049-5_0_2_load_48 | 54 | 0.00077133 | 0.00019331 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5049-5_0_2_load_49 | 55 | 0.00077373 | 0.00019391 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5049-5_0_2_load_50 | 56 | 0.00092175 | 0.00023101 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5049-5_0_2_load_77 | 57 | 0.0010277 | 0.00025757 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5049-5_0_2_load_51 | 58 | 0.0028298 | 0.00070921 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5049-5_0_2_load_52 | 59 | 0.00056769 | 0.00014228 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5049-5_0_2_load_61 | 60 | 0.00038215 | 9.5775e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5049-5_0_2_load_169 | 61 | 0.00081821 | 0.00020506 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5049-5_0_2_load_53 | 62 | 0.00067577 | 0.00016937 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5049-5_0_2_load_67 | 63 | 0.00096344 | 0.00024146 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5049-5_0_2_load_68 | 64 | 0.00083709 | 0.00020979 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5049-5_0_2_load_69 | 65 | 0.00081336 | 0.00020385 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5049-5_0_2_load_72 | 67 | 0.0012091 | 0.00030304 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5049-5_0_2_load_73 | 68 | 0.00077793 | 0.00019497 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5049-5_0_2_load_74 | 70 | 0.00081221 | 0.00020356 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5049-5_0_2_load_75 | 71 | 0.0010779 | 0.00027015 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5049-5_0_2_load_76 | 72 | 0.00086221 | 0.00021609 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5049-5_0_2_load_80 | 73 | 0.00075524 | 0.00018928 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5049-5_0_2_load_78 | 74 | 0.0012432 | 0.00031156 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5049-5_0_2_load_170 | 75 | 0.00040755 | 0.00010214 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5049-5_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_5049-5_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_5049-5_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0021345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_5049-5_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.010943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_5049-5_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.10841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_5049-5_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.00903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_5049-5_0_2_line_6 | NAYY 4x150 SE | 5 | 35 | 0.085817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_5049-5_0_2_line_7 | NAYY 4x150 SE | 6 | 34 | 0.013192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_5049-5_0_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.0054311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5049-5_0_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.031237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5049-5_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.12179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5049-5_0_2_line_11 | NAYY 4x150 SE | 8 | 11 | 0.10178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5049-5_0_2_line_12 | NAYY 4x150 SE | 9 | 12 | 0.0048777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5049-5_0_2_line_13 | NAYY 4x150 SE | 9 | 13 | 0.0085671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5049-5_0_2_line_14 | NAYY 4x150 SE | 10 | 14 | 0.14478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5049-5_0_2_line_15 | NAYY 4x150 SE | 12 | 15 | 0.033634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5049-5_0_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.0078248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5049-5_0_2_line_17 | NAYY 4x150 SE | 14 | 36 | 0.14065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5049-5_0_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.020858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5049-5_0_2_line_19 | NAYY 4x150 SE | 15 | 18 | 0.013794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5049-5_0_2_line_20 | NAYY 4x150 SE | 16 | 22 | 0.006012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5049-5_0_2_line_21 | NAYY 4x150 SE | 16 | 21 | 0.0076447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5049-5_0_2_line_22 | NAYY 4x150 SE | 17 | 19 | 0.0037259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5049-5_0_2_line_23 | NAYY 4x150 SE | 18 | 20 | 0.0080869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5049-5_0_2_line_24 | NAYY 4x150 SE | 20 | 26 | 0.015037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5049-5_0_2_line_25 | NAYY 4x150 SE | 22 | 23 | 0.002969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5049-5_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.014727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5049-5_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.0012078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5049-5_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.023708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5049-5_0_2_line_29 | NAYY 4x150 SE | 27 | 28 | 0.0063441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_5049-5_0_2_line_30 | NAYY 4x150 SE | 27 | 29 | 0.036812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_5049-5_0_2_line_31 | NAYY 4x150 SE | 28 | 30 | 0.027688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_5049-5_0_2_line_32 | NAYY 4x150 SE | 29 | 31 | 0.040672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_5049-5_0_2_line_33 | NAYY 4x150 SE | 30 | 32 | 0.00092658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_5049-5_0_2_line_34 | NAYY 4x150 SE | 31 | 33 | 0.0022416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_5049-5_0_2_line_35 | NAYY 4x150 SE | 33 | 34 | 0.012492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_5049-5_0_2_line_36 | NAYY 4x150 SE | 35 | 69 | 0.10248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5049-5_0_2_line_37 | NAYY 4x150 SE | 36 | 37 | 0.11775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5049-5_0_2_line_38 | NAYY 4x150 SE | 37 | 38 | 0.092651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5049-5_0_2_line_39 | NAYY 4x150 SE | 38 | 39 | 0.024871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5049-5_0_2_line_40 | NAYY 4x150 SE | 39 | 62 | 0.087842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5049-5_0_2_line_41 | NAYY 4x150 SE | 40 | 41 | 0.02881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5049-5_0_2_line_42 | NAYY 4x150 SE | 40 | 42 | 0.039827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5049-5_0_2_line_43 | NAYY 4x150 SE | 41 | 43 | 0.29798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5049-5_0_2_line_44 | NAYY 4x150 SE | 42 | 44 | 0.04743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5049-5_0_2_line_45 | NAYY 4x150 SE | 43 | 45 | 0.0063068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5049-5_0_2_line_46 | NAYY 4x150 SE | 44 | 63 | 0.0055408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5049-5_0_2_line_47 | NAYY 4x150 SE | 45 | 46 | 0.0096328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5049-5_0_2_line_48 | NAYY 4x150 SE | 46 | 54 | 0.0028274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5049-5_0_2_line_49 | NAYY 4x150 SE | 47 | 48 | 0.0015185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5049-5_0_2_line_50 | NAYY 4x150 SE | 48 | 49 | 0.054497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5049-5_0_2_line_51 | NAYY 4x150 SE | 49 | 50 | 0.018349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5049-5_0_2_line_52 | NAYY 4x150 SE | 49 | 51 | 0.011886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5049-5_0_2_line_53 | NAYY 4x150 SE | 50 | 52 | 0.023744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5049-5_0_2_line_54 | NAYY 4x150 SE | 51 | 53 | 0.002786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5049-5_0_2_line_55 | NAYY 4x150 SE | 52 | 69 | 0.26217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5049-5_0_2_line_56 | NAYY 4x150 SE | 53 | 74 | 0.00012025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5049-5_0_2_line_57 | NAYY 4x150 SE | 54 | 55 | 0.0033685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5049-5_0_2_line_58 | NAYY 4x150 SE | 55 | 56 | 0.010212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5049-5_0_2_line_59 | NAYY 4x150 SE | 56 | 57 | 0.00064257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5049-5_0_2_line_60 | NAYY 4x150 SE | 57 | 68 | 0.0048016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5049-5_0_2_line_61 | NAYY 4x150 SE | 58 | 59 | 0.11448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5049-5_0_2_line_62 | NAYY 4x150 SE | 58 | 60 | 0.074061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5049-5_0_2_line_63 | NAYY 4x150 SE | 58 | 61 | 0.64326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5049-5_0_2_line_64 | NAYY 4x150 SE | 59 | 62 | 0.046017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5049-5_0_2_line_65 | NAYY 4x150 SE | 61 | 75 | 0.0061766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5049-5_0_2_line_66 | NAYY 4x150 SE | 64 | 65 | 0.0043177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5049-5_0_2_line_67 | NAYY 4x150 SE | 65 | 66 | 0.019046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5049-5_0_2_line_68 | NAYY 4x150 SE | 66 | 67 | 0.0093167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5049-5_0_2_line_69 | NAYY 4x150 SE | 66 | 68 | 0.015495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5049-5_0_2_line_70 | NAYY 4x150 SE | 67 | 70 | 0.0029784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_5049-5_0_2_line_71 | NAYY 4x150 SE | 70 | 71 | 0.001251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_5049-5_0_2_line_72 | NAYY 4x150 SE | 71 | 72 | 0.0088335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5049-5_0_2_line_73 | NAYY 4x150 SE | 72 | 73 | 0.0024624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5049-5_0_2_line_74 | NAYY 4x150 SE | 73 | 74 | 0.0011276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5049-5_0_2_trafo_28 | 0.25 MVA 20/0.4 kV | 76 | 32 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2715810.9211 | 1152230.2829 | 2715825.0159 | 1152227.3664
1 | 2715810.9211 | 1152230.2829 | 2715808.0312 | 1152230.8809 | 2715809.4545 | 1152239.4918 | 2715808.5085 | 1152244.7772 | 2715808.5085 | 1152244.7772
2 | 2715827.1061 | 1152226.9338 | 2715825.0159 | 1152227.3664
3 | 2715808.5085 | 1152244.7772 | 2715798.0953 | 1152248.1424
4 | 2715904.8892 | 1152196.3093 | 2715882.5979 | 1152184.2946 | 2715868.1891 | 1152183.9061 | 2715849.9768 | 1152188.8925 | 2715834.1102 | 1152194.8469 | 2715827.1061 | 1152226.9338 | 2715827.1061 | 1152226.9338
5 | 2715791.4257 | 1152253.7104 | 2715795.1299 | 1152249.1007 | 2715798.0953 | 1152248.1424
6 | 2715904.8892 | 1152196.3093 | 2715958.5001 | 1152263.3194
7 | 2715791.4257 | 1152253.7104 | 2715792.0397 | 1152258.1029 | 2715792.1146 | 1152261.7957 | 2715793.1476 | 1152266.7522
8 | 2715705.8993 | 1152212.8062 | 2715710.9181 | 1152214.8818
9 | 2715721.5142 | 1152243.8937 | 2715719.8981 | 1152234.5231 | 2715712.639 | 1152216.8051 | 2715710.9181 | 1152214.8818
10 | 2715705.8993 | 1152212.8062 | 2715708.3361 | 1152225.8062 | 2715708.2147 | 1152229.3285 | 2715706.8197 | 1152232.0146 | 2715703.8709 | 1152234.4707 | 2715700.769 | 1152235.3006 | 2715697.7493 | 1152234.6533 | 2715695.4963 | 1152233.6538 | 2715693.4804 | 1152231.5025 | 2715692.0712 | 1152228.1399 | 2715689.6062 | 1152195.8264 | 2715686.5201 | 1152163.4787 | 2715685.9419 | 1152152.0266 | 2715685.856 | 1152145.5841
11 | 2715705.8993 | 1152212.8062 | 2715706.5915 | 1152205.9483 | 2715710.7785 | 1152195.7885 | 2715716.9931 | 1152187.569 | 2715731.8993 | 1152172.4675 | 2715739.9548 | 1152164.7281 | 2715757.4856 | 1152142.8836 | 2715765.4594 | 1152132.374
12 | 2715721.5142 | 1152243.8937 | 2715721.2578 | 1152248.7647
13 | 2715721.5142 | 1152243.8937 | 2715726.0492 | 1152245.582 | 2715729.7403 | 1152246.1054
14 | 2715696.8925 | 1152001.2245 | 2715685.856 | 1152145.5841
15 | 2715730.2814 | 1152280.5868 | 2715728.8644 | 1152276.0343 | 2715724.148 | 1152265.8146 | 2715721.4639 | 1152258.8917 | 2715720.8975 | 1152255.612 | 2715721.2578 | 1152248.7647
16 | 2715737.4066 | 1152245.767 | 2715733.8501 | 1152246.6881 | 2715729.7403 | 1152246.1054
17 | 2715561.4474 | 1151963.3183 | 2715696.8925 | 1152001.2245
18 | 2715730.2814 | 1152280.5868 | 2715725.0007 | 1152295.7289 | 2715724.5894 | 1152300.533
19 | 2715730.2814 | 1152280.5868 | 2715735.4932 | 1152288.192 | 2715737.2032 | 1152292.4347
20 | 2715737.4066 | 1152245.767 | 2715740.4339 | 1152247.6153 | 2715742.8958 | 1152247.7413
21 | 2715737.4066 | 1152245.767 | 2715740.1543 | 1152242.5954 | 2715741.3205 | 1152240.2273 | 2715741.7349 | 1152239.5328
22 | 2715724.0168 | 1152304.2051 | 2715724.4266 | 1152302.4335 | 2715724.5894 | 1152300.533
23 | 2715740.2263 | 1152299.9353 | 2715737.2032 | 1152292.4347
24 | 2715740.2263 | 1152299.9353 | 2715740.2263 | 1152299.9353 | 2715741.5695 | 1152306.7324 | 2715741.8564 | 1152310.5738 | 2715741.5655 | 1152314.8206
25 | 2715745.8608 | 1152247.8931 | 2715742.8958 | 1152247.7413
26 | 2715760.3971 | 1152249.6316 | 2715756.431 | 1152248.4343 | 2715745.8608 | 1152247.8931
27 | 2715760.3971 | 1152249.6316 | 2715761.5533 | 1152249.9806
28 | 2715741.5801 | 1152338.1203 | 2715740.5334 | 1152336.6659 | 2715740.2132 | 1152334.5583 | 2715741.5655 | 1152314.8206
29 | 2715741.5801 | 1152338.1203 | 2715737.3555 | 1152342.6533 | 2715737.2514 | 1152342.7581
30 | 2715741.5801 | 1152338.1203 | 2715742.139 | 1152338.598 | 2715743.6214 | 1152339.3493 | 2715745.909 | 1152338.9485 | 2715747.6643 | 1152337.8815 | 2715754.3902 | 1152330.617 | 2715766.187 | 1152314.2952
31 | 2715718.4108 | 1152363.0298 | 2715728.6435 | 1152351.4141 | 2715737.2514 | 1152342.7581
32 | 2715766.187 | 1152314.2952 | 2715770.044 | 1152308.9588 | 2715781.5576 | 1152288.2439 | 2715787.8538 | 1152279.9811
33 | 2715718.4108 | 1152363.0298 | 2715717.7983 | 1152363.7251
34 | 2715789.2125 | 1152278.1982 | 2715787.8538 | 1152279.9811
35 | 2715789.2125 | 1152278.1982 | 2715791.803 | 1152274.7985 | 2715793.0217 | 1152270.5079 | 2715793.1476 | 1152266.7522
36 | 2715897.8591 | 1152341.7719 | 2715928.4055 | 1152312.5288 | 2715939.3233 | 1152301.6539 | 2715943.8491 | 1152294.2471 | 2715947.8208 | 1152282.927 | 2715950.1646 | 1152273.6326 | 2715951.6104 | 1152267.9121 | 2715953.198 | 1152265.5966 | 2715955.6129 | 1152264.1644 | 2715958.5001 | 1152263.3194
37 | 2715503.6299 | 1152065.0144 | 2715506.715 | 1152061.0598 | 2715518.2195 | 1152047.1933 | 2715526.5715 | 1152030.3977 | 2715539.2136 | 1151999.2637 | 2715544.8939 | 1151987.6871 | 2715561.4474 | 1151963.3183
38 | 2715503.6299 | 1152065.0144 | 2715499.5716 | 1152062.0791 | 2715495.8488 | 1152061.663 | 2715491.4148 | 1152063.1011 | 2715486.7558 | 1152067.07 | 2715472.8529 | 1152084.7154 | 2715466.4897 | 1152098.2914 | 2715461.9545 | 1152113.4146 | 2715457.7513 | 1152120.4388 | 2715450.102 | 1152129.2694
39 | 2715433.9414 | 1152148.1731 | 2715441.6268 | 1152139.0534 | 2715450.102 | 1152129.2694
40 | 2715433.9414 | 1152148.1731 | 2715431.3916 | 1152151.1987 | 2715427.4241 | 1152154.3359 | 2715422.2988 | 1152156.6059 | 2715412.0524 | 1152160.1231 | 2715402.1413 | 1152164.1693 | 2715395.6352 | 1152167.5914 | 2715390.5773 | 1152174.7549 | 2715378.4683 | 1152196.1595 | 2715372.4274 | 1152205.3175
41 | 2716090.7918 | 1152956.1103 | 2716090.4872 | 1152954.6714 | 2716082.8958 | 1152934.7894 | 2716081.5718 | 1152928.8789
42 | 2716090.7918 | 1152956.1103 | 2716126.0297 | 1152937.5508
43 | 2715895.7235 | 1152695.9603 | 2716081.5718 | 1152928.8789
44 | 2716126.0297 | 1152937.5508 | 2716172.5843 | 1152946.6236
45 | 2715895.7235 | 1152695.9603 | 2715892.7128 | 1152690.4185 | 2715892.7128 | 1152690.4185
46 | 2716174.544 | 1152951.8063 | 2716172.5843 | 1152946.6236
47 | 2715892.7128 | 1152690.4185 | 2715892.0807 | 1152686.1701 | 2715892.3215 | 1152680.8378 | 2715892.3215 | 1152680.8378
48 | 2715893.316 | 1152678.1911 | 2715892.3215 | 1152680.8378
49 | 2715855.4966 | 1152681.8386 | 2715854.4042 | 1152680.784
50 | 2715863.9666 | 1152632.6155 | 2715860.1639 | 1152636.3671 | 2715850.5978 | 1152655.218 | 2715847.5294 | 1152667.8786 | 2715850.787 | 1152677.292 | 2715854.4042 | 1152680.784
51 | 2715865.2871 | 1152615.0513 | 2715862.2834 | 1152629.9369 | 2715863.9666 | 1152632.6155
52 | 2715863.9666 | 1152632.6155 | 2715866.4102 | 1152635.6645 | 2715870.7981 | 1152637.7948 | 2715873.7919 | 1152638.6026
53 | 2715865.2871 | 1152615.0513 | 2715871.8075 | 1152615.2657 | 2715876.8309 | 1152613.8948 | 2715878.0904 | 1152612.2624 | 2715882.8348 | 1152603.5147
54 | 2715873.7919 | 1152638.6026 | 2715876.4817 | 1152639.3284
55 | 2715897.8591 | 1152341.7719 | 2715882.8348 | 1152603.5147
56 | 2715876.5978 | 1152639.3597 | 2715876.4817 | 1152639.3284
57 | 2715893.316 | 1152678.1911 | 2715894.5007 | 1152675.0379
58 | 2715894.5007 | 1152675.0379 | 2715898.0924 | 1152665.4785
59 | 2715898.3184 | 1152664.877 | 2715898.0924 | 1152665.4785
60 | 2715898.3184 | 1152664.877 | 2715900.0072 | 1152660.3822
61 | 2715349.935 | 1152340.0819 | 2715346.7417 | 1152338.3918 | 2715328.1921 | 1152324.1716 | 2715323.7092 | 1152319.3603 | 2715321.6139 | 1152313.7386 | 2715321.4046 | 1152306.6299 | 2715322.8824 | 1152300.4095 | 2715332.8412 | 1152285.0454 | 2715352.8396 | 1152246.8605
62 | 2715349.935 | 1152340.0819 | 2715417.4012 | 1152309.5307
63 | 2715349.935 | 1152340.0819 | 2715025.3118 | 1152895.4189
64 | 2715352.8396 | 1152246.8605 | 2715354.4896 | 1152243.71 | 2715363.7467 | 1152220.9053 | 2715371.3054 | 1152207.0185 | 2715372.4274 | 1152205.3175
65 | 2715023.2434 | 1152901.2389 | 2715025.3118 | 1152895.4189
66 | 2715914.7278 | 1152626.263 | 2715912.2546 | 1152629.8021
67 | 2715901.7259 | 1152645.6729 | 2715910.7087 | 1152632.0143 | 2715912.2546 | 1152629.8021
68 | 2715901.7259 | 1152645.6729 | 2715898.8638 | 1152644.4281 | 2715892.7861 | 1152643.2252
69 | 2715901.7259 | 1152645.6729 | 2715902.9078 | 1152648.075 | 2715902.8612 | 1152650.498 | 2715902.8147 | 1152652.9098 | 2715900.0072 | 1152660.3822
70 | 2715889.8644 | 1152642.6469 | 2715892.7861 | 1152643.2252
71 | 2715888.6372 | 1152642.404 | 2715889.8644 | 1152642.6469
72 | 2715888.6372 | 1152642.404 | 2715885.7956 | 1152641.8416 | 2715880.0638 | 1152640.295
73 | 2715880.0638 | 1152640.295 | 2715877.6864 | 1152639.6535
74 | 2715876.5978 | 1152639.3597 | 2715877.6864 | 1152639.6535

## bus_geodata
| x | y | coords
0 | 2715810.9211 | 1152230.2829
1 | 2715825.0159 | 1152227.3664
2 | 2715808.5085 | 1152244.7772
3 | 2715827.1061 | 1152226.9338
4 | 2715798.0953 | 1152248.1424
5 | 2715904.8892 | 1152196.3093
6 | 2715791.4257 | 1152253.7104
7 | 2715710.9181 | 1152214.8818
8 | 2715705.8993 | 1152212.8062
9 | 2715721.5142 | 1152243.8937
10 | 2715685.856 | 1152145.5841
11 | 2715765.4594 | 1152132.374
12 | 2715721.2578 | 1152248.7647
13 | 2715729.7403 | 1152246.1054
14 | 2715696.8925 | 1152001.2245
15 | 2715730.2814 | 1152280.5868
16 | 2715737.4066 | 1152245.767
17 | 2715724.5894 | 1152300.533
18 | 2715737.2032 | 1152292.4347
19 | 2715724.0168 | 1152304.2051
20 | 2715740.2263 | 1152299.9353
21 | 2715741.7349 | 1152239.5328
22 | 2715742.8958 | 1152247.7413
23 | 2715745.8609 | 1152247.8931
24 | 2715760.3971 | 1152249.6316
25 | 2715761.5533 | 1152249.9806
26 | 2715741.5655 | 1152314.8206
27 | 2715741.5801 | 1152338.1203
28 | 2715737.2514 | 1152342.7581
29 | 2715766.187 | 1152314.2952
30 | 2715718.4108 | 1152363.0298
31 | 2715787.8538 | 1152279.9811
32 | 2715717.7983 | 1152363.7251
33 | 2715789.2125 | 1152278.1982
34 | 2715793.1476 | 1152266.7522
35 | 2715958.5001 | 1152263.3194
36 | 2715561.4474 | 1151963.3183
37 | 2715503.6299 | 1152065.0144
38 | 2715450.102 | 1152129.2694
39 | 2715433.9414 | 1152148.1731
40 | 2716090.7918 | 1152956.1103
41 | 2716081.5718 | 1152928.8789
42 | 2716126.0297 | 1152937.5508
43 | 2715895.7235 | 1152695.9602
44 | 2716172.5843 | 1152946.6236
45 | 2715892.7128 | 1152690.4185
46 | 2715892.3215 | 1152680.8378
47 | 2715855.4966 | 1152681.8386
48 | 2715854.4042 | 1152680.784
49 | 2715863.9666 | 1152632.6155
50 | 2715865.2871 | 1152615.0513
51 | 2715873.7919 | 1152638.6026
52 | 2715882.8348 | 1152603.5147
53 | 2715876.4817 | 1152639.3284
54 | 2715893.316 | 1152678.1911
55 | 2715894.5007 | 1152675.0379
56 | 2715898.0924 | 1152665.4785
57 | 2715898.3184 | 1152664.877
58 | 2715349.935 | 1152340.0819
59 | 2715352.8396 | 1152246.8605
60 | 2715417.4012 | 1152309.5307
61 | 2715025.3118 | 1152895.4189
62 | 2715372.4274 | 1152205.3175
63 | 2716174.544 | 1152951.8063
64 | 2715914.7278 | 1152626.263
65 | 2715912.2546 | 1152629.8021
66 | 2715901.7259 | 1152645.6729
67 | 2715892.7861 | 1152643.2252
68 | 2715900.0072 | 1152660.3822
69 | 2715897.859 | 1152341.7719
70 | 2715889.8644 | 1152642.6469
71 | 2715888.6372 | 1152642.404
72 | 2715880.0638 | 1152640.295
73 | 2715877.6864 | 1152639.6535
74 | 2715876.5978 | 1152639.3597
75 | 2715023.2434 | 1152901.2389
76 | 2715717.7983 | 1152363.7251

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1