## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5049-6_1_3_node_41 | 0.4 | n |  | TRUE
1 | bus_LV_5049-6_1_3_node_42 | 0.4 | n |  | TRUE
2 | bus_LV_5049-6_1_3_node_43 | 0.4 | n |  | TRUE
3 | bus_LV_5049-6_1_3_node_44 | 0.4 | n |  | TRUE
4 | bus_LV_5049-6_1_3_node_46 | 0.4 | n |  | TRUE
5 | bus_LV_5049-6_1_3_node_76 | 0.4 | n |  | TRUE
6 | bus_LV_5049-6_1_3_node_45 | 0.4 | n |  | TRUE
7 | bus_LV_5049-6_1_3_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_5049-6_1_3_node_104 | 0.4 | n |  | TRUE
9 | bus_LV_5049-6_1_3_node_91 | 0.4 | n |  | TRUE
10 | bus_LV_5049-6_1_3_node_93 | 0.4 | n |  | TRUE
11 | bus_LV_5049-6_1_3_node_89 | 0.4 | n |  | TRUE
12 | bus_LV_5049-6_1_3_node_47 | 0.4 | n |  | TRUE
13 | bus_LV_5049-6_1_3_node_73 | 0.4 | n |  | TRUE
14 | bus_LV_5049-6_1_3_node_105 | 0.4 | n |  | TRUE
15 | bus_LV_5049-6_1_3_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_5049-6_1_3_node_75 | 0.4 | n |  | TRUE
17 | bus_LV_5049-6_1_3_node_110 | 0.4 | n |  | TRUE
18 | bus_LV_5049-6_1_3_node_111 | 0.4 | n |  | TRUE
19 | bus_LV_5049-6_1_3_node_112 | 0.4 | n |  | TRUE
20 | bus_LV_5049-6_1_3_node_103 | 0.4 | n |  | TRUE
21 | bus_LV_5049-6_1_3_node_94 | 0.4 | n |  | TRUE
22 | bus_LV_5049-6_1_3_node_100 | 0.4 | n |  | TRUE
23 | bus_LV_5049-6_1_3_node_92 | 0.4 | n |  | TRUE
24 | bus_LV_5049-6_1_3_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_5049-6_1_3_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_5049-6_1_3_node_133 | 0.4 | n |  | TRUE
27 | bus_LV_5049-6_1_3_node_134 | 0.4 | n |  | TRUE
28 | bus_LV_5049-6_1_3_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_5049-6_1_3_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_5049-6_1_3_node_55 | 0.4 | n |  | TRUE
31 | bus_LV_5049-6_1_3_node_56 | 0.4 | n |  | TRUE
32 | bus_LV_5049-6_1_3_node_57 | 0.4 | n |  | TRUE
33 | bus_LV_5049-6_1_3_node_149 | 0.4 | n |  | TRUE
34 | bus_LV_5049-6_1_3_node_148 | 0.4 | n |  | TRUE
35 | bus_LV_5049-6_1_3_node_150 | 0.4 | n |  | TRUE
36 | bus_LV_5049-6_1_3_node_145 | 0.4 | n |  | TRUE
37 | bus_LV_5049-6_1_3_node_147 | 0.4 | n |  | TRUE
38 | bus_LV_5049-6_1_3_node_146 | 0.4 | n |  | TRUE
39 | bus_LV_5049-6_1_3_node_140 | 0.4 | n |  | TRUE
40 | bus_LV_5049-6_1_3_node_106 | 0.4 | n |  | TRUE
41 | bus_LV_5049-6_1_3_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_5049-6_1_3_node_79 | 0.4 | n |  | TRUE
43 | bus_LV_5049-6_1_3_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_5049-6_1_3_node_86 | 0.4 | n |  | TRUE
45 | bus_LV_5049-6_1_3_node_80 | 0.4 | n |  | TRUE
46 | bus_LV_5049-6_1_3_node_81 | 0.4 | n |  | TRUE
47 | bus_LV_5049-6_1_3_node_85 | 0.4 | n |  | TRUE
48 | bus_LV_5049-6_1_3_node_88 | 0.4 | n |  | TRUE
49 | bus_LV_5049-6_1_3_node_95 | 0.4 | n |  | TRUE
50 | bus_LV_5049-6_1_3_node_82 | 0.4 | n |  | TRUE
51 | bus_LV_5049-6_1_3_node_83 | 0.4 | n |  | TRUE
52 | bus_LV_5049-6_1_3_node_84 | 0.4 | n |  | TRUE
53 | bus_LV_5049-6_1_3_node_96 | 0.4 | n |  | TRUE
54 | bus_LV_5049-6_1_3_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_5049-6_1_3_node_101 | 0.4 | n |  | TRUE
56 | bus_LV_5049-6_1_3_node_102 | 0.4 | n |  | TRUE
57 | bus_LV_5049-6_1_3_node_97 | 0.4 | n |  | TRUE
58 | bus_LV_5049-6_1_3_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_5049-6_1_3_node_99 | 0.4 | n |  | TRUE
60 | bus_LV_5049-6_1_3_node_113 | 0.4 | n |  | TRUE
61 | bus_LV_5049-6_1_3_node_114 | 0.4 | n |  | TRUE
62 | bus_LV_5049-6_1_3_node_108 | 0.4 | n |  | TRUE
63 | bus_LV_5049-6_1_3_node_107 | 0.4 | n |  | TRUE
64 | bus_LV_5049-6_1_3_node_109 | 0.4 | n |  | TRUE
65 | bus_LV_5049-6_1_3_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_5049-6_1_3_node_117 | 0.4 | n |  | TRUE
67 | bus_LV_5049-6_1_3_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_5049-6_1_3_node_138 | 0.4 | n |  | TRUE
69 | bus_LV_5049-6_1_3_node_141 | 0.4 | n |  | TRUE
70 | bus_LV_5049-6_1_3_node_118 | 0.4 | n |  | TRUE
71 | bus_LV_5049-6_1_3_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_5049-6_1_3_node_120 | 0.4 | n |  | TRUE
73 | bus_LV_5049-6_1_3_node_121 | 0.4 | n |  | TRUE
74 | bus_LV_5049-6_1_3_node_122 | 0.4 | n |  | TRUE
75 | bus_LV_5049-6_1_3_node_123 | 0.4 | n |  | TRUE
76 | bus_LV_5049-6_1_3_node_124 | 0.4 | n |  | TRUE
77 | bus_LV_5049-6_1_3_node_125 | 0.4 | n |  | TRUE
78 | bus_LV_5049-6_1_3_node_126 | 0.4 | n |  | TRUE
79 | bus_LV_5049-6_1_3_node_127 | 0.4 | n |  | TRUE
80 | bus_LV_5049-6_1_3_node_128 | 0.4 | n |  | TRUE
81 | bus_LV_5049-6_1_3_node_132 | 0.4 | n |  | TRUE
82 | bus_LV_5049-6_1_3_node_131 | 0.4 | n |  | TRUE
83 | bus_LV_5049-6_1_3_node_136 | 0.4 | n |  | TRUE
84 | bus_LV_5049-6_1_3_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_5049-6_1_3_node_137 | 0.4 | n |  | TRUE
86 | bus_LV_5049-6_1_3_node_142 | 0.4 | n |  | TRUE
87 | bus_LV_5049-6_1_3_node_144 | 0.4 | n |  | TRUE
88 | bus_LV_5049-6_1_3_node_143 | 0.4 | n |  | TRUE
89 | bus_LV_5049-6_1_3_node_151 | 0.4 | n |  | TRUE
90 | bus_LV_5049-6_1_3_node_152 | 0.4 | n |  | TRUE
91 | bus_LV_5049-6_1_3_node_153 | 0.4 | n |  | TRUE
92 | bus_LV_5049-6_1_3_node_154 | 0.4 | n |  | TRUE
93 | bus_LV_5049-6_1_3_node_155 | 0.4 | n |  | TRUE
94 | bus_LV_5049-6_1_3_node_172 | 0.4 | n |  | TRUE
95 | bus_LV_5049-6_1_3_node_156 | 0.4 | n |  | TRUE
96 | bus_LV_5049-6_1_3_node_157 | 0.4 | n |  | TRUE
97 | bus_LV_5049-6_1_3_node_170 | 0.4 | n |  | TRUE
98 | bus_LV_5049-6_1_3_node_171 | 0.4 | n |  | TRUE
99 | bus_LV_5049-6_1_3_node_192 | 0.4 | n |  | TRUE
100 | bus_LV_5049-6_1_3_node_158 | 0.4 | n |  | TRUE
101 | bus_LV_5049-6_1_3_node_191 | 0.4 | n |  | TRUE
102 | bus_LV_5049-6_1_3_node_159 | 0.4 | n |  | TRUE
103 | bus_LV_5049-6_1_3_node_160 | 0.4 | n |  | TRUE
104 | bus_LV_5049-6_1_3_node_161 | 0.4 | n |  | TRUE
105 | bus_LV_5049-6_1_3_node_162 | 0.4 | n |  | TRUE
106 | bus_LV_5049-6_1_3_node_163 | 0.4 | n |  | TRUE
107 | bus_LV_5049-6_1_3_node_164 | 0.4 | n |  | TRUE
108 | bus_LV_5049-6_1_3_node_167 | 0.4 | n |  | TRUE
109 | bus_LV_5049-6_1_3_node_165 | 0.4 | n |  | TRUE
110 | bus_LV_5049-6_1_3_node_166 | 0.4 | n |  | TRUE
111 | bus_LV_5049-6_1_3_node_173 | 0.4 | n |  | TRUE
112 | bus_LV_5049-6_1_3_node_174 | 0.4 | n |  | TRUE
113 | bus_LV_5049-6_1_3_node_175 | 0.4 | n |  | TRUE
114 | bus_LV_5049-6_1_3_node_176 | 0.4 | n |  | TRUE
115 | bus_LV_5049-6_1_3_node_177 | 0.4 | n |  | TRUE
116 | bus_LV_5049-6_1_3_node_178 | 0.4 | n |  | TRUE
117 | bus_LV_5049-6_1_3_node_179 | 0.4 | n |  | TRUE
118 | bus_LV_5049-6_1_3_node_183 | 0.4 | n |  | TRUE
119 | bus_LV_5049-6_1_3_node_182 | 0.4 | n |  | TRUE
120 | bus_LV_5049-6_1_3_node_184 | 0.4 | n |  | TRUE
121 | bus_LV_5049-6_1_3_node_186 | 0.4 | n |  | TRUE
122 | bus_LV_5049-6_1_3_node_181 | 0.4 | n |  | TRUE
123 | bus_LV_5049-6_1_3_node_180 | 0.4 | n |  | TRUE
124 | bus_LV_5049-6_1_3_node_185 | 0.4 | n |  | TRUE
125 | bus_LV_5049-6_1_3_node_187 | 0.4 | n |  | TRUE
126 | bus_LV_5049-6_1_3_node_188 | 0.4 | n |  | TRUE
127 | bus_LV_5049-6_1_3_node_189 | 0.4 | n |  | TRUE
128 | bus_LV_5049-6_1_3_node_190 | 0.4 | n |  | TRUE
129 | bus_MV_0_node_55 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5049-6_1_3_load_41 | 0 | 8.6901e-05 | 2.1779e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5049-6_1_3_load_42 | 1 | 9.7413e-05 | 2.4414e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5049-6_1_3_load_44 | 3 | 0.00010152 | 2.5444e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5049-6_1_3_load_46 | 4 | 0.00011756 | 2.9463e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5049-6_1_3_load_76 | 5 | 0.00014218 | 3.5634e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5049-6_1_3_load_48 | 7 | 0.00015617 | 3.9141e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5049-6_1_3_load_104 | 8 | 0.00019656 | 4.9264e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5049-6_1_3_load_91 | 9 | 9.4923e-05 | 2.379e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5049-6_1_3_load_93 | 10 | 0.0001076 | 2.6968e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5049-6_1_3_load_89 | 11 | 9.9653e-05 | 2.4975e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5049-6_1_3_load_47 | 12 | 9.9189e-05 | 2.4859e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5049-6_1_3_load_73 | 13 | 0.00011544 | 2.8932e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5049-6_1_3_load_105 | 14 | 0.00018415 | 4.6151e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5049-6_1_3_load_74 | 15 | 0.00010546 | 2.6432e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5049-6_1_3_load_110 | 17 | 0.00014677 | 3.6783e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5049-6_1_3_load_111 | 18 | 0.00014578 | 3.6537e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5049-6_1_3_load_112 | 19 | 0.00011113 | 2.7852e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5049-6_1_3_load_103 | 20 | 0.00010539 | 2.6414e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5049-6_1_3_load_94 | 21 | 0.00011795 | 2.9561e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5049-6_1_3_load_100 | 22 | 8.2198e-05 | 2.0601e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5049-6_1_3_load_92 | 23 | 0.00015584 | 3.9057e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5049-6_1_3_load_51 | 24 | 0.00042338 | 0.00010611 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5049-6_1_3_load_52 | 25 | 0.0010957 | 0.0002746 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5049-6_1_3_load_133 | 26 | 0.0002597 | 6.5086e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5049-6_1_3_load_134 | 27 | 0.00041676 | 0.00010445 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5049-6_1_3_load_54 | 29 | 0.0009227 | 0.00023125 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5049-6_1_3_load_55 | 30 | 9.9209e-05 | 2.4864e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5049-6_1_3_load_56 | 31 | 0.00026443 | 6.6273e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5049-6_1_3_load_149 | 33 | 0.00029235 | 7.327e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5049-6_1_3_load_150 | 35 | 0.00026803 | 6.7175e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5049-6_1_3_load_145 | 36 | 0.00089441 | 0.00022416 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5049-6_1_3_load_147 | 37 | 0.00073658 | 0.0001846 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5049-6_1_3_load_140 | 39 | 0.0012927 | 0.00032398 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5049-6_1_3_load_77 | 41 | 0.00010313 | 2.5848e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5049-6_1_3_load_79 | 42 | 0.00011949 | 2.9946e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5049-6_1_3_load_87 | 43 | 9.419e-05 | 2.3606e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5049-6_1_3_load_86 | 44 | 9.6298e-05 | 2.4135e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5049-6_1_3_load_80 | 45 | 0.0001116 | 2.797e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5049-6_1_3_load_81 | 46 | 0.00014284 | 3.58e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5049-6_1_3_load_85 | 47 | 0.00010705 | 2.6829e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5049-6_1_3_load_88 | 48 | 0.00012036 | 3.0166e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5049-6_1_3_load_82 | 50 | 0.00011201 | 2.8073e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5049-6_1_3_load_83 | 51 | 0.00011301 | 2.8322e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5049-6_1_3_load_96 | 53 | 0.00029978 | 7.5133e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5049-6_1_3_load_90 | 54 | 8.1612e-05 | 2.0454e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5049-6_1_3_load_101 | 55 | 0.00013439 | 3.3681e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5049-6_1_3_load_102 | 56 | 0.00018594 | 4.66e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5049-6_1_3_load_98 | 58 | 0.0003551 | 8.8996e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5049-6_1_3_load_99 | 59 | 0.00010652 | 2.6696e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5049-6_1_3_load_113 | 60 | 0.00032006 | 8.0214e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5049-6_1_3_load_114 | 61 | 0.00023977 | 6.0092e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5049-6_1_3_load_107 | 63 | 9.6308e-05 | 2.4137e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5049-6_1_3_load_109 | 64 | 0.00013911 | 3.4864e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5049-6_1_3_load_116 | 65 | 0.00014251 | 3.5716e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5049-6_1_3_load_117 | 66 | 0.00010675 | 2.6754e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5049-6_1_3_load_138 | 68 | 0.00033488 | 8.3929e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5049-6_1_3_load_119 | 71 | 0.00074222 | 0.00018602 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5049-6_1_3_load_121 | 73 | 0.00010665 | 2.6729e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5049-6_1_3_load_122 | 74 | 0.00014217 | 3.5631e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5049-6_1_3_load_123 | 75 | 0.00012754 | 3.1964e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5049-6_1_3_load_125 | 77 | 0.00011458 | 2.8717e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5049-6_1_3_load_126 | 78 | 0.00021789 | 5.4607e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5049-6_1_3_load_127 | 79 | 8.3795e-05 | 2.1001e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5049-6_1_3_load_128 | 80 | 0.00010221 | 2.5615e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5049-6_1_3_load_132 | 81 | 9.69e-05 | 2.4285e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5049-6_1_3_load_131 | 82 | 0.00011342 | 2.8426e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5049-6_1_3_load_136 | 83 | 0.00031179 | 7.8142e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5049-6_1_3_load_139 | 84 | 0.00025377 | 6.36e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5049-6_1_3_load_137 | 85 | 0.00077385 | 0.00019395 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5049-6_1_3_load_142 | 86 | 0.00038274 | 9.5925e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5049-6_1_3_load_144 | 87 | 0.00074632 | 0.00018705 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5049-6_1_3_load_143 | 88 | 0.00022627 | 5.6708e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5049-6_1_3_load_151 | 89 | 0.00025311 | 6.3436e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5049-6_1_3_load_153 | 91 | 0.00033688 | 8.4431e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5049-6_1_3_load_154 | 92 | 0.0021422 | 0.00053688 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5049-6_1_3_load_155 | 93 | 0.00025856 | 6.4802e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5049-6_1_3_load_172 | 94 | 0.00073302 | 0.00018371 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5049-6_1_3_load_156 | 95 | 0.00082489 | 0.00020674 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5049-6_1_3_load_157 | 96 | 0.0003356 | 8.411e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5049-6_1_3_load_170 | 97 | 0.00028656 | 7.1818e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5049-6_1_3_load_171 | 98 | 0.00031786 | 7.9662e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5049-6_1_3_load_192 | 99 | 0.00061271 | 0.00015356 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5049-6_1_3_load_158 | 100 | 0.00024372 | 6.1082e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5049-6_1_3_load_191 | 101 | 0.00070943 | 0.0001778 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5049-6_1_3_load_160 | 103 | 0.00015752 | 3.9479e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5049-6_1_3_load_161 | 104 | 0.00018024 | 4.5172e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5049-6_1_3_load_162 | 105 | 0.00017114 | 4.2892e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5049-6_1_3_load_163 | 106 | 0.00017526 | 4.3923e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5049-6_1_3_load_164 | 107 | 0.0001914 | 4.7968e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5049-6_1_3_load_167 | 108 | 0.00017708 | 4.438e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5049-6_1_3_load_165 | 109 | 0.00018465 | 4.6277e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5049-6_1_3_load_166 | 110 | 0.00023974 | 6.0085e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5049-6_1_3_load_173 | 111 | 0.00076248 | 0.00019109 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5049-6_1_3_load_175 | 113 | 0.00065533 | 0.00016424 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5049-6_1_3_load_176 | 114 | 0.00087751 | 0.00021993 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5049-6_1_3_load_178 | 116 | 0.00040681 | 0.00010196 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5049-6_1_3_load_179 | 117 | 0.00066165 | 0.00016583 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5049-6_1_3_load_182 | 119 | 0.00083644 | 0.00020963 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5049-6_1_3_load_184 | 120 | 8.4008e-05 | 2.1054e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5049-6_1_3_load_186 | 121 | 0.00014221 | 3.5642e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5049-6_1_3_load_181 | 122 | 0.00106 | 0.00026567 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5049-6_1_3_load_180 | 123 | 0.00095647 | 0.00023971 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5049-6_1_3_load_185 | 124 | 0.0001272 | 3.1879e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5049-6_1_3_load_187 | 125 | 0.00015129 | 3.7916e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5049-6_1_3_load_188 | 126 | 8.2139e-05 | 2.0586e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5049-6_1_3_load_189 | 127 | 0.0011457 | 0.00028714 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5049-6_1_3_load_190 | 128 | 0.00069167 | 0.00017335 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5049-6_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5049-6_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.19784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5049-6_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.15499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5049-6_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.22954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5049-6_1_3_line_4 | NAYY 4x150 SE | 3 | 7 | 0.082193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5049-6_1_3_line_5 | NAYY 4x150 SE | 4 | 5 | 0.050306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5049-6_1_3_line_6 | NAYY 4x150 SE | 4 | 6 | 0.17916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5049-6_1_3_line_7 | NAYY 4x150 SE | 5 | 14 | 0.11945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5049-6_1_3_line_8 | NAYY 4x150 SE | 6 | 12 | 0.14123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5049-6_1_3_line_9 | NAYY 4x150 SE | 7 | 8 | 0.058683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5049-6_1_3_line_10 | NAYY 4x150 SE | 8 | 20 | 0.005145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5049-6_1_3_line_11 | NAYY 4x150 SE | 9 | 10 | 0.12976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5049-6_1_3_line_12 | NAYY 4x150 SE | 9 | 11 | 0.06329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5049-6_1_3_line_13 | NAYY 4x150 SE | 10 | 49 | 0.064545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5049-6_1_3_line_14 | NAYY 4x150 SE | 11 | 54 | 0.081868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5049-6_1_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.30177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5049-6_1_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.072096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5049-6_1_3_line_17 | NAYY 4x150 SE | 14 | 40 | 0.033022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5049-6_1_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.17221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5049-6_1_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.22227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5049-6_1_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.19529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5049-6_1_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.083652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5049-6_1_3_line_22 | NAYY 4x150 SE | 19 | 59 | 0.051864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5049-6_1_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.19901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5049-6_1_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.078425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5049-6_1_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.011647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5049-6_1_3_line_26 | NAYY 4x150 SE | 22 | 55 | 0.057848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5049-6_1_3_line_27 | NAYY 4x150 SE | 23 | 54 | 0.0048057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5049-6_1_3_line_28 | NAYY 4x150 SE | 24 | 25 | 0.029719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5049-6_1_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.10238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5049-6_1_3_line_30 | NAYY 4x150 SE | 26 | 27 | 0.16685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5049-6_1_3_line_31 | NAYY 4x150 SE | 27 | 67 | 0.076715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5049-6_1_3_line_32 | NAYY 4x150 SE | 28 | 29 | 0.038524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_5049-6_1_3_line_33 | NAYY 4x150 SE | 28 | 30 | 0.15028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_5049-6_1_3_line_34 | NAYY 4x150 SE | 29 | 31 | 0.15725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_5049-6_1_3_line_35 | NAYY 4x150 SE | 30 | 32 | 0.011217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5049-6_1_3_line_36 | NAYY 4x150 SE | 31 | 33 | 0.034498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_5049-6_1_3_line_37 | NAYY 4x150 SE | 32 | 34 | 0.057507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5049-6_1_3_line_38 | NAYY 4x150 SE | 33 | 35 | 0.14225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_5049-6_1_3_line_39 | NAYY 4x150 SE | 34 | 36 | 0.020291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5049-6_1_3_line_40 | NAYY 4x150 SE | 34 | 37 | 0.013332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5049-6_1_3_line_41 | NAYY 4x150 SE | 35 | 89 | 0.22162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_5049-6_1_3_line_42 | NAYY 4x150 SE | 36 | 87 | 0.12285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5049-6_1_3_line_43 | NAYY 4x150 SE | 37 | 38 | 0.04077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5049-6_1_3_line_44 | NAYY 4x150 SE | 38 | 39 | 0.12563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5049-6_1_3_line_45 | NAYY 4x150 SE | 39 | 85 | 8.4985e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5049-6_1_3_line_46 | NAYY 4x150 SE | 40 | 62 | 0.051122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5049-6_1_3_line_47 | NAYY 4x150 SE | 41 | 42 | 0.24062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5049-6_1_3_line_48 | NAYY 4x150 SE | 42 | 43 | 0.20672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5049-6_1_3_line_49 | NAYY 4x150 SE | 43 | 44 | 0.055607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5049-6_1_3_line_50 | NAYY 4x150 SE | 44 | 52 | 0.027693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5049-6_1_3_line_51 | NAYY 4x150 SE | 45 | 46 | 0.01843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5049-6_1_3_line_52 | NAYY 4x150 SE | 45 | 47 | 0.23464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5049-6_1_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.02845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5049-6_1_3_line_54 | NAYY 4x150 SE | 47 | 51 | 0.12124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5049-6_1_3_line_55 | NAYY 4x150 SE | 48 | 49 | 0.069751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5049-6_1_3_line_56 | NAYY 4x150 SE | 49 | 53 | 0.053486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5049-6_1_3_line_57 | NAYY 4x150 SE | 50 | 51 | 0.054436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5049-6_1_3_line_58 | NAYY 4x150 SE | 50 | 52 | 0.019606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5049-6_1_3_line_59 | NAYY 4x150 SE | 55 | 56 | 0.075772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5049-6_1_3_line_60 | NAYY 4x150 SE | 57 | 58 | 0.065013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5049-6_1_3_line_61 | NAYY 4x150 SE | 57 | 59 | 0.035067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5049-6_1_3_line_62 | NAYY 4x150 SE | 58 | 60 | 0.2911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5049-6_1_3_line_63 | NAYY 4x150 SE | 60 | 61 | 0.017987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5049-6_1_3_line_64 | NAYY 4x150 SE | 61 | 67 | 0.0084814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5049-6_1_3_line_65 | NAYY 4x150 SE | 62 | 64 | 0.035753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5049-6_1_3_line_66 | NAYY 4x150 SE | 62 | 63 | 0.0004059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5049-6_1_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.012464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5049-6_1_3_line_68 | NAYY 4x150 SE | 65 | 66 | 0.03172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5049-6_1_3_line_69 | NAYY 4x150 SE | 66 | 70 | 0.29222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5049-6_1_3_line_70 | NAYY 4x150 SE | 67 | 68 | 0.021253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_5049-6_1_3_line_71 | NAYY 4x150 SE | 68 | 69 | 0.137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_5049-6_1_3_line_72 | NAYY 4x150 SE | 69 | 87 | 0.090588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5049-6_1_3_line_73 | NAYY 4x150 SE | 69 | 88 | 0.022441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5049-6_1_3_line_74 | NAYY 4x150 SE | 70 | 71 | 0.13484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_5049-6_1_3_line_75 | NAYY 4x150 SE | 70 | 72 | 0.21306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_5049-6_1_3_line_76 | NAYY 4x150 SE | 72 | 73 | 0.036425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_5049-6_1_3_line_77 | NAYY 4x150 SE | 73 | 74 | 0.020722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_5049-6_1_3_line_78 | NAYY 4x150 SE | 74 | 75 | 0.003627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_5049-6_1_3_line_79 | NAYY 4x150 SE | 75 | 76 | 0.005692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_5049-6_1_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.029243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_5049-6_1_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.02097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_5049-6_1_3_line_82 | NAYY 4x150 SE | 77 | 79 | 0.009531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_5049-6_1_3_line_83 | NAYY 4x150 SE | 78 | 80 | 0.013542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_5049-6_1_3_line_84 | NAYY 4x150 SE | 80 | 81 | 0.012984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_5049-6_1_3_line_85 | NAYY 4x150 SE | 81 | 82 | 0.013344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_5049-6_1_3_line_86 | NAYY 4x150 SE | 83 | 84 | 0.011592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_5049-6_1_3_line_87 | NAYY 4x150 SE | 84 | 86 | 0.0018819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_5049-6_1_3_line_88 | NAYY 4x150 SE | 86 | 88 | 0.019163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_5049-6_1_3_line_89 | NAYY 4x150 SE | 89 | 90 | 0.19924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_5049-6_1_3_line_90 | NAYY 4x150 SE | 90 | 91 | 0.17847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_5049-6_1_3_line_91 | NAYY 4x150 SE | 90 | 92 | 0.20202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_5049-6_1_3_line_92 | NAYY 4x150 SE | 91 | 93 | 0.01457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_5049-6_1_3_line_93 | NAYY 4x150 SE | 91 | 94 | 0.17156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_5049-6_1_3_line_94 | NAYY 4x150 SE | 92 | 95 | 0.002712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_5049-6_1_3_line_95 | NAYY 4x150 SE | 93 | 96 | 0.034356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_5049-6_1_3_line_96 | NAYY 4x150 SE | 94 | 98 | 0.015753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_5049-6_1_3_line_97 | NAYY 4x150 SE | 95 | 99 | 0.25624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_5049-6_1_3_line_98 | NAYY 4x150 SE | 96 | 100 | 0.051809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_5049-6_1_3_line_99 | NAYY 4x150 SE | 97 | 98 | 0.023561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_5049-6_1_3_line_100 | NAYY 4x150 SE | 99 | 101 | 0.15205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_5049-6_1_3_line_101 | NAYY 4x150 SE | 100 | 102 | 0.13503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_5049-6_1_3_line_102 | NAYY 4x150 SE | 101 | 111 | 0.16483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_5049-6_1_3_line_103 | NAYY 4x150 SE | 102 | 103 | 0.1126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_5049-6_1_3_line_104 | NAYY 4x150 SE | 102 | 104 | 0.176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_5049-6_1_3_line_105 | NAYY 4x150 SE | 103 | 105 | 0.0093078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_5049-6_1_3_line_106 | NAYY 4x150 SE | 104 | 106 | 0.046626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_5049-6_1_3_line_107 | NAYY 4x150 SE | 105 | 107 | 0.12599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_5049-6_1_3_line_108 | NAYY 4x150 SE | 106 | 108 | 0.22253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_5049-6_1_3_line_109 | NAYY 4x150 SE | 107 | 109 | 0.007938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_5049-6_1_3_line_110 | NAYY 4x150 SE | 109 | 110 | 0.015251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_5049-6_1_3_line_111 | NAYY 4x150 SE | 111 | 112 | 0.003758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_5049-6_1_3_line_112 | NAYY 4x150 SE | 112 | 113 | 0.2548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_5049-6_1_3_line_113 | NAYY 4x150 SE | 113 | 114 | 0.044127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_5049-6_1_3_line_114 | NAYY 4x150 SE | 114 | 115 | 0.15218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_5049-6_1_3_line_115 | NAYY 4x150 SE | 115 | 116 | 0.15477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_5049-6_1_3_line_116 | NAYY 4x150 SE | 115 | 117 | 0.081485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_5049-6_1_3_line_117 | NAYY 4x150 SE | 116 | 118 | 0.024668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_5049-6_1_3_line_118 | NAYY 4x150 SE | 117 | 119 | 0.011468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_5049-6_1_3_line_119 | NAYY 4x150 SE | 118 | 120 | 0.018879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_5049-6_1_3_line_120 | NAYY 4x150 SE | 118 | 121 | 0.32424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_5049-6_1_3_line_121 | NAYY 4x150 SE | 119 | 122 | 0.019103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_5049-6_1_3_line_122 | NAYY 4x150 SE | 120 | 124 | 0.030469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_5049-6_1_3_line_123 | NAYY 4x150 SE | 121 | 125 | 0.010166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_5049-6_1_3_line_124 | NAYY 4x150 SE | 122 | 123 | 0.0094673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_5049-6_1_3_line_125 | NAYY 4x150 SE | 124 | 126 | 0.011511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_5049-6_1_3_line_126 | NAYY 4x150 SE | 126 | 127 | 0.15478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_5049-6_1_3_line_127 | NAYY 4x150 SE | 127 | 128 | 0.045901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5049-6_1_3_trafo_55 | 0.25 MVA 20/0.4 kV | 129 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35
0 | 2713841.903 | 1151138.7127 | 2713840.5997 | 1151144.0793 | 2713835.4478 | 1151160.7072
1 | 2713735.7362 | 1151110.4655 | 2713752.1585 | 1151112.5102 | 2713760.5093 | 1151114.269 | 2713770.5097 | 1151114.458 | 2713780.5937 | 1151109.8231 | 2713787.5103 | 1151102.56 | 2713794.7963 | 1151092.4131 | 2713800.7202 | 1151086.0874 | 2713807.9531 | 1151079.1527 | 2713813.8831 | 1151072.5048 | 2713819.1378 | 1151067.4673 | 2713827.5995 | 1151063.7692 | 2713833.7424 | 1151062.918 | 2713840.3797 | 1151070.4373 | 2713839.8811 | 1151079.7563 | 2713842.6183 | 1151105.5363 | 2713844.0417 | 1151115.5254 | 2713844.0966 | 1151129.6803 | 2713841.903 | 1151138.7127
2 | 2713735.7362 | 1151110.4655 | 2713740.505 | 1151087.6514 | 2713741.6236 | 1151072.329 | 2713738.8696 | 1151060.0133 | 2713739.5447 | 1151051.5093 | 2713744.9924 | 1151030.1535 | 2713745.8339 | 1151023.8096 | 2713745.8061 | 1151008.6212 | 2713745.9966 | 1150999.7522 | 2713748.7691 | 1150979.391 | 2713752.1797 | 1150971.1721 | 2713750.3274 | 1150965.589 | 2713745.3856 | 1150960.1588
3 | 2713633.6433 | 1151316.0537 | 2713735.7362 | 1151110.4655
4 | 2713745.3856 | 1150960.1588 | 2713734.4135 | 1150952.4576 | 2713732.2112 | 1150949.1361 | 2713729.3256 | 1150938.0965 | 2713726.4165 | 1150928.702 | 2713714.0411 | 1150902.6067 | 2713711.3044 | 1150894.6497 | 2713711.2154 | 1150888.3883
5 | 2713587.5229 | 1151296.5728 | 2713589.9314 | 1151297.1613 | 2713616.0308 | 1151310.7958 | 2713633.6433 | 1151316.0537
6 | 2713709.678 | 1151444.2401 | 2713707.4693 | 1151446.5555 | 2713703.256 | 1151446.476 | 2713690.8109 | 1151439.9813 | 2713652.8229 | 1151423.7649 | 2713646.366 | 1151416.4604 | 2713642.8024 | 1151408.7992 | 2713643.0775 | 1151394.2281 | 2713637.4086 | 1151378.5218 | 2713636.4595 | 1151363.316 | 2713632.9192 | 1151354.4211 | 2713629.3712 | 1151345.9374 | 2713631.5595 | 1151339.0074 | 2713637.4937 | 1151330.0801 | 2713637.6022 | 1151324.3339 | 2713635.4348 | 1151319.1673 | 2713633.6433 | 1151316.0537
7 | 2713510.6097 | 1151217.2578 | 2713510.6097 | 1151217.2578 | 2713513.3299 | 1151220.3889 | 2713517.6174 | 1151238.9375 | 2713524.6579 | 1151258.4721 | 2713532.0933 | 1151268.4633 | 2713565.9196 | 1151291.2937 | 2713587.5229 | 1151296.5728
8 | 2713709.678 | 1151444.2401 | 2713736.7559 | 1151514.9427 | 2713751.3414 | 1151527.1929 | 2713761.3559 | 1151548.5406 | 2713778.4289 | 1151563.7865
9 | 2713711.2154 | 1150888.3883 | 2713715.3381 | 1150872.1442 | 2713716.1934 | 1150864.6665 | 2713714.3515 | 1150853.2352 | 2713705.899 | 1150832.0394 | 2713705.899 | 1150832.0394
10 | 2713705.899 | 1150832.0394 | 2713706.303 | 1150826.9103 | 2713706.303 | 1150826.9103
11 | 2713960.4991 | 1150798.4976 | 2713965.2874 | 1150804.7994 | 2713996.347 | 1150823.366 | 2714014.8867 | 1150828.787 | 2714031.3615 | 1150842.2855 | 2714037.7015 | 1150850.0996 | 2714044.406 | 1150865.8259 | 2714051.2698 | 1150873.1384 | 2714058.5221 | 1150876.1555
12 | 2713925.0786 | 1150746.1611 | 2713932.148 | 1150758.9867 | 2713947.2703 | 1150781.0873 | 2713960.4991 | 1150798.4976
13 | 2714087.7901 | 1150873.7524 | 2714099.0891 | 1150887.2865 | 2714097.2121 | 1150891.9318 | 2714091.5297 | 1150889.5338 | 2714084.4692 | 1150886.9317 | 2714069.1748 | 1150879.2259 | 2714058.5221 | 1150876.1555 | 2714058.5221 | 1150876.1555
14 | 2713925.0786 | 1150746.1611 | 2713920.0034 | 1150736.9535 | 2713898.2419 | 1150712.6815 | 2713880.5021 | 1150696.2019 | 2713867.4794 | 1150689.7293 | 2713867.4794 | 1150689.7293
15 | 2713778.4289 | 1151563.7865 | 2713702.8308 | 1151855.9305
16 | 2713702.8308 | 1151855.9305 | 2713696.5536 | 1151861.9593 | 2713689.9498 | 1151872.2192 | 2713681.0644 | 1151897.2015 | 2713678.474 | 1151907.137 | 2713670.1495 | 1151918.8971
17 | 2713503.5103 | 1151244.4199 | 2713503.0189 | 1151232.2025 | 2713502.462 | 1151223.464 | 2713504.6175 | 1151218.2678 | 2713507.841 | 1151216.6941 | 2713510.6097 | 1151217.2578
18 | 2713631.8715 | 1152084.3313 | 2713631.7135 | 1152071.5531 | 2713633.2723 | 1152052.4143 | 2713637.6019 | 1152035.329 | 2713646.2459 | 1152023.1173 | 2713647.5865 | 1151994.3901 | 2713654.5292 | 1151966.169 | 2713665.5604 | 1151933.6443 | 2713669.8298 | 1151919.3487 | 2713670.1495 | 1151918.8971
19 | 2713631.8715 | 1152084.3313 | 2713619.3551 | 1152082.9054 | 2713609.0003 | 1152089.3811 | 2713605.6916 | 1152098.3358 | 2713611.452 | 1152105.4936 | 2713620.9202 | 1152104.1046 | 2713629.6203 | 1152101.5225 | 2713634.332 | 1152102.0117 | 2713642.5666 | 1152102.9454 | 2713649.5753 | 1152107.0026 | 2713650.5645 | 1152116.8166 | 2713653.3481 | 1152136.082 | 2713648.6729 | 1152154.8062 | 2713641.7523 | 1152167.2284 | 2713604.7061 | 1152233.9518
20 | 2713631.8715 | 1152084.3313 | 2713657.291 | 1152074.4264 | 2713677.1311 | 1152063.2267 | 2713702.5281 | 1152054.5224 | 2713713.4308 | 1152049.9362 | 2713740.9664 | 1152034.0899 | 2713751.1013 | 1152027.488 | 2713776.3928 | 1152024.3746 | 2713792.4004 | 1152025.0774 | 2713812.7147 | 1152031.0541
21 | 2713812.7147 | 1152031.0541 | 2713812.7147 | 1152031.0541 | 2713826.1763 | 1152060.8504 | 2713831.1149 | 1152074.9198 | 2713847.1366 | 1152095.981 | 2713852.122 | 1152104.1643
22 | 2713852.122 | 1152104.1643 | 2713876.6645 | 1152144.4492 | 2713878.39 | 1152148.8118
23 | 2713851.0368 | 1150690.319 | 2713706.303 | 1150826.9103
24 | 2713851.0368 | 1150690.319 | 2713825.3053 | 1150764.4026
25 | 2713862.6768 | 1150689.9015 | 2713851.0368 | 1150690.319 | 2713851.0368 | 1150690.319
26 | 2713825.3053 | 1150764.4026 | 2713830.1378 | 1150771.089 | 2713833.0777 | 1150801.5982 | 2713832.8219 | 1150820.5439
27 | 2713867.4794 | 1150689.7293 | 2713862.6768 | 1150689.9015
28 | 2714148.4967 | 1152755.5125 | 2714170.5104 | 1152735.547
29 | 2714157.7405 | 1152633.9621 | 2714170.5104 | 1152735.547
30 | 2714157.7405 | 1152633.9621 | 2714159.3181 | 1152628.8886 | 2714165.2349 | 1152618.0268 | 2714172.859 | 1152601.3268 | 2714178.4499 | 1152590.2476 | 2714180.2343 | 1152577.106 | 2714178.5418 | 1152557.8833 | 2714176.7906 | 1152540.9389 | 2714173.0555 | 1152519.3314 | 2714168.2629 | 1152497.6261 | 2714164.2303 | 1152486.0308 | 2714154.1445 | 1152478.8542
31 | 2714145.6523 | 1152409.2275 | 2714140.8893 | 1152438.5791 | 2714139.1011 | 1152464.4736 | 2714145.7049 | 1152472.8488 | 2714154.1445 | 1152478.8542
32 | 2714392.9607 | 1152199.9012 | 2714402.7275 | 1152215.119 | 2714411.4799 | 1152224.7361 | 2714417.268 | 1152229.4069
33 | 2714392.9607 | 1152199.9012 | 2714389.7653 | 1152136.1757 | 2714392.9177 | 1152125.8064 | 2714396.8896 | 1152115.5417 | 2714399.6301 | 1152093.3233 | 2714400.6983 | 1152088.0067 | 2714397.9411 | 1152081.6167 | 2714393.7665 | 1152075.0776 | 2714388.1812 | 1152069.6568 | 2714382.67 | 1152059.9345 | 2714380.2925 | 1152057.8753
34 | 2714510.7929 | 1152331.1463 | 2714510.1174 | 1152324.1655 | 2714510.0023 | 1152315.691 | 2714512.7266 | 1152302.4117 | 2714513.5263 | 1152295.4778 | 2714512.6815 | 1152290.6586 | 2714508.4721 | 1152283.1402 | 2714499.7898 | 1152275.092 | 2714493.5966 | 1152271.3829 | 2714482.0216 | 1152268.5166 | 2714474.9789 | 1152263.8574 | 2714463.7997 | 1152253.0934 | 2714453.4882 | 1152247.5604 | 2714438.5281 | 1152243.0732 | 2714428.0597 | 1152238.1155 | 2714417.268 | 1152229.4069
35 | 2714374.2412 | 1152064.3775 | 2714374.9069 | 1152060.4541 | 2714376.8188 | 1152057.5996 | 2714379.415 | 1152057.1153 | 2714380.2925 | 1152057.8753
36 | 2714510.7929 | 1152331.1463 | 2714513.0555 | 1152354.5306 | 2714513.087 | 1152365.5352
37 | 2714374.2412 | 1152064.3775 | 2714363.6278 | 1152064.2092 | 2714356.0777 | 1152060.3855 | 2714349.8249 | 1152061.412 | 2714345.9022 | 1152073.5345 | 2714342.6441 | 1152087.0484 | 2714340.9477 | 1152092.2974
38 | 2714513.087 | 1152365.5352 | 2714513.1137 | 1152374.8786 | 2714515.8608 | 1152393.4877 | 2714515.0507 | 1152409.0382 | 2714510.6024 | 1152431.4353 | 2714508.9003 | 1152449.8931 | 2714505.9937 | 1152477.2005 | 2714503.4477 | 1152501.6907 | 2714502.8394 | 1152506.7269
39 | 2714340.9477 | 1152092.2974 | 2714337.9871 | 1152101.4585 | 2714337.0053 | 1152112.0763
40 | 2714340.9477 | 1152092.2974 | 2714350.5583 | 1152095.949 | 2714353.0159 | 1152097.7577
41 | 2714502.8394 | 1152506.7269 | 2714502.3544 | 1152510.7426 | 2714503.3945 | 1152516.1883 | 2714506.0359 | 1152519.3739 | 2714510.0081 | 1152521.5954 | 2714518.992 | 1152524.2568 | 2714522.6149 | 1152526.2826 | 2714524.8267 | 1152530.6609 | 2714525.5059 | 1152538.1344 | 2714524.4503 | 1152552.8686 | 2714524.864 | 1152562.5941 | 2714524.4056 | 1152570.146 | 2714523.0959 | 1152577.2592 | 2714520.4518 | 1152582.29 | 2714514.8375 | 1152586.4972 | 2714512.7867 | 1152589.3935 | 2714512.7246 | 1152592.2498 | 2714514.7268 | 1152594.734 | 2714517.2086 | 1152595.8152 | 2714520.2148 | 1152594.7494 | 2714523.4823 | 1152590.0306 | 2714534.0751 | 1152568.6399 | 2714546.3549 | 1152540.4879 | 2714550.5909 | 1152529.2499 | 2714551.9069 | 1152522.2146 | 2714551.5303 | 1152505.6964 | 2714551.7404 | 1152499.096 | 2714553.9233 | 1152492.1306
42 | 2714279.0248 | 1152211.6015 | 2714295.5445 | 1152184.7309 | 2714308.0763 | 1152163.0875 | 2714310.4183 | 1152161.8423 | 2714321.8793 | 1152150.1075 | 2714340.6597 | 1152134.5424 | 2714338.9576 | 1152123.1136 | 2714336.8182 | 1152114.1003 | 2714337.0053 | 1152112.0763
43 | 2714365.7882 | 1152134.7529 | 2714365.4702 | 1152125.2293 | 2714364.0653 | 1152113.9173 | 2714359.8321 | 1152106.0206 | 2714356.0167 | 1152099.9664 | 2714353.0159 | 1152097.7577
44 | 2714365.7882 | 1152134.7529 | 2714359.2266 | 1152148.4041 | 2714336.3345 | 1152194.1334 | 2714327.1184 | 1152212.5597 | 2714321.8847 | 1152226.225 | 2714311.8006 | 1152248.1256
45 | 2714311.765 | 1152248.2028 | 2714311.8006 | 1152248.1256
46 | 2713459.2511 | 1151221.9269 | 2713483.1445 | 1151241.0229 | 2713503.5103 | 1151244.4199
47 | 2713878.8681 | 1150448.4936 | 2713879.833 | 1150207.874
48 | 2714085.4373 | 1150440.6861 | 2713878.8681 | 1150448.4936
49 | 2714085.4373 | 1150440.6861 | 2714089.2798 | 1150442.5378 | 2714094.6227 | 1150443.8288 | 2714098.3046 | 1150437.9501 | 2714103.7374 | 1150434.4951 | 2714112.5898 | 1150439.4105 | 2714121.0843 | 1150446.9986 | 2714128.3854 | 1150455.1645
50 | 2714155.4512 | 1150458.0569 | 2714148.2751 | 1150459.0995 | 2714137.5632 | 1150458.3071 | 2714128.3854 | 1150455.1645
51 | 2714034.4726 | 1150773.0444 | 2714035.2871 | 1150775.6821 | 2714041.738 | 1150789.9623
52 | 2714034.4726 | 1150773.0444 | 2714198.2668 | 1150605.0328
53 | 2714041.738 | 1150789.9623 | 2714042.5163 | 1150791.6852 | 2714056.8978 | 1150814.0142
54 | 2714198.2668 | 1150605.0328 | 2714200.5074 | 1150612.8026 | 2714204.3082 | 1150616.4438 | 2714207.9133 | 1150615.0223 | 2714209.8537 | 1150607.0426 | 2714210.0339 | 1150597.5397 | 2714210.8242 | 1150587.4479 | 2714211.9454 | 1150575.2944 | 2714213.6204 | 1150565.5197 | 2714211.2121 | 1150551.2089 | 2714208.493 | 1150537.4927 | 2714203.6749 | 1150524.3259 | 2714201.5017 | 1150512.9994
55 | 2714087.7901 | 1150873.7524 | 2714073.1242 | 1150860.8328 | 2714069.4903 | 1150851.6246 | 2714064.3924 | 1150835.395 | 2714063.1994 | 1150823.7981 | 2714056.8978 | 1150814.0142
56 | 2714087.7901 | 1150873.7524 | 2714093.6756 | 1150873.9418 | 2714100.6676 | 1150874.4856 | 2714107.8123 | 1150877.9121 | 2714132.3265 | 1150899.4933
57 | 2714172.4543 | 1150467.6295 | 2714174.0291 | 1150468.8049 | 2714181.9157 | 1150477.2711 | 2714186.1745 | 1150488.3481 | 2714193.4118 | 1150499.4704 | 2714201.5017 | 1150512.9994
58 | 2714155.4512 | 1150458.0569 | 2714166.6773 | 1150463.3176 | 2714172.4543 | 1150467.6295
59 | 2713832.8219 | 1150820.5439 | 2713832.5598 | 1150839.9584 | 2713841.8257 | 1150881.4611 | 2713848.2767 | 1150893.6962
60 | 2713885.8325 | 1152182.8703 | 2713888.6703 | 1152208.5633 | 2713887.9314 | 1152226.1166 | 2713882.8348 | 1152247.1011
61 | 2713885.8325 | 1152182.8703 | 2713882.3934 | 1152158.9338 | 2713878.39 | 1152148.8118
62 | 2714131.1461 | 1152399.0336 | 2713882.8348 | 1152247.1011
63 | 2714137.1827 | 1152408.7819 | 2714128.8049 | 1152408.3411 | 2714131.1461 | 1152399.0336
64 | 2714145.6523 | 1152409.2275 | 2714137.1827 | 1152408.7819
65 | 2713459.2511 | 1151221.9269 | 2713458.5875 | 1151218.8457 | 2713456.8824 | 1151212.3648 | 2713452.8625 | 1151208.531 | 2713441.6026 | 1151203.8826 | 2713433.4397 | 1151203.7985
66 | 2713459.3117 | 1151222.3282 | 2713459.2511 | 1151221.9269
67 | 2713420.9764 | 1151203.67 | 2713433.4397 | 1151203.7985
68 | 2713420.9764 | 1151203.67 | 2713418.1523 | 1151203.6409 | 2713409.4931 | 1151201.5432 | 2713402.0056 | 1151195.5316 | 2713394.29 | 1151188.5818 | 2713394.29 | 1151188.5818
69 | 2713296.7971 | 1150922.7046 | 2713304.5982 | 1150936.5605 | 2713322.0883 | 1150969.6114 | 2713340.459 | 1150984.0109 | 2713366.334 | 1151041.8806 | 2713369.7319 | 1151075.0888 | 2713376.3959 | 1151099.9751 | 2713379.6561 | 1151112.7672 | 2713386.0891 | 1151131.9788 | 2713386.7673 | 1151139.5855 | 2713383.0009 | 1151153.6795 | 2713383.069 | 1151161.0746 | 2713387.108 | 1151176.1273 | 2713394.29 | 1151188.5818
70 | 2714145.6523 | 1152409.2275 | 2714154.8189 | 1152399.4392 | 2714162.294 | 1152397.0652
71 | 2714253.1306 | 1152296.879 | 2714246.1968 | 1152303.0627 | 2714235.2378 | 1152310.6155 | 2714223.4787 | 1152326.3474 | 2714211.3151 | 1152340.3484 | 2714201.4933 | 1152356.3395 | 2714191.9398 | 1152369.5227 | 2714180.1932 | 1152384.6102 | 2714166.3487 | 1152395.7774 | 2714162.294 | 1152397.0652
72 | 2714253.1306 | 1152296.879 | 2714256.1808 | 1152274.0883 | 2714257.7965 | 1152258.1194 | 2714263.7561 | 1152237.3407 | 2714277.2947 | 1152214.4156 | 2714279.0248 | 1152211.6015
73 | 2714253.1306 | 1152296.879 | 2714254.4477 | 1152313.226 | 2714255.1625 | 1152319.2245
74 | 2713249.3517 | 1150806.9581 | 2713242.7748 | 1150822.7116 | 2713258.3765 | 1150834.9575 | 2713272.7397 | 1150866.1037 | 2713286.0473 | 1150879.4849 | 2713288.4499 | 1150899.9215 | 2713296.7971 | 1150922.7046
75 | 2713111.8489 | 1150834.1712 | 2713130.2605 | 1150854.6193 | 2713144.5855 | 1150862.4935 | 2713161.2287 | 1150863.0397 | 2713185.3875 | 1150873.0446 | 2713212.8574 | 1150880.0875 | 2713222.4815 | 1150879.0788 | 2713261.9021 | 1150891.2166 | 2713276.7769 | 1150902.5037 | 2713296.7971 | 1150922.7046
76 | 2713111.8489 | 1150834.1712 | 2713100.3511 | 1150816.388 | 2713088.4684 | 1150806.8324
77 | 2713088.4684 | 1150806.8324 | 2713072.3205 | 1150793.8469
78 | 2713069.494 | 1150791.5739 | 2713072.3205 | 1150793.8469
79 | 2713065.0583 | 1150788.0069 | 2713069.494 | 1150791.5739
80 | 2713065.0583 | 1150788.0069 | 2713057.2113 | 1150777.3748 | 2713049.5727 | 1150763.2834
81 | 2713065.0583 | 1150788.0069 | 2713044.2086 | 1150790.2505
82 | 2713049.5727 | 1150763.2834 | 2713045.0306 | 1150754.9043
83 | 2713035.7044 | 1150779.7123 | 2713044.2086 | 1150790.2505
84 | 2713024.6109 | 1150778.1734 | 2713032.8933 | 1150776.229 | 2713035.7044 | 1150779.7123
85 | 2713024.6109 | 1150778.1734 | 2713021.0091 | 1150779.019 | 2713012.5108 | 1150783.5796
86 | 2714260.9188 | 1152338.7116 | 2714269.1342 | 1152346.8897
87 | 2714259.5852 | 1152337.384 | 2714260.9188 | 1152338.7116
88 | 2714259.5852 | 1152337.384 | 2714259.5852 | 1152337.384 | 2714256.9043 | 1152333.8419 | 2714255.1625 | 1152319.2245
89 | 2714635.5019 | 1152318.0239 | 2714629.4203 | 1152319.3424 | 2714604.9559 | 1152347.1844 | 2714594.2465 | 1152367.005 | 2714588.5516 | 1152381.4842 | 2714583.9002 | 1152389.9347 | 2714577.1937 | 1152404.3278 | 2714567.9358 | 1152420.0845 | 2714565.6908 | 1152429.1479 | 2714566.156 | 1152449.07 | 2714563.0671 | 1152462.9539 | 2714553.9233 | 1152492.1306
90 | 2714635.5019 | 1152318.0239 | 2714636.5254 | 1152321.1121 | 2714633.3551 | 1152326.3553 | 2714615.9119 | 1152351.5069 | 2714605.4919 | 1152379.9165 | 2714603.3619 | 1152388.982 | 2714603.6122 | 1152398.8156 | 2714608.5529 | 1152421.1356 | 2714609.6559 | 1152444.2387 | 2714609.5236 | 1152469.3307 | 2714610.4305 | 1152481.3672 | 2714611.4718 | 1152487.1983
91 | 2714635.5019 | 1152318.0239 | 2714638.0138 | 1152314.7028 | 2714646.3008 | 1152306.4105 | 2714648.1799 | 1152302.8661 | 2714648.4942 | 1152299.2586 | 2714645.2926 | 1152290.4251 | 2714644.1873 | 1152284.7781 | 2714643.8256 | 1152265.8808 | 2714642.046 | 1152260.977 | 2714637.9547 | 1152254.1167 | 2714628.1496 | 1152244.168 | 2714621.0359 | 1152236.7943 | 2714614.2625 | 1152226.8699 | 2714600.6621 | 1152206.1974 | 2714589.3185 | 1152192.7837 | 2714586.1662 | 1152187.398 | 2714582.8445 | 1152176.3941 | 2714578.2357 | 1152160.0177 | 2714577.1109 | 1152156.1938 | 2714576.639 | 1152153.1605 | 2714577.0858 | 1152150.6563 | 2714578.5951 | 1152148.7948 | 2714580.5677 | 1152147.5982 | 2714582.5102 | 1152147.5796 | 2714584.0305 | 1152148.3646 | 2714584.0305 | 1152148.3646
92 | 2714611.9334 | 1152501.5756 | 2714612.8791 | 1152495.0785 | 2714611.4718 | 1152487.1983
93 | 2714611.4718 | 1152487.1983 | 2714782.5525 | 1152474.3397
94 | 2714584.0305 | 1152148.3646 | 2714585.0574 | 1152150.8747
95 | 2714611.9334 | 1152501.5756 | 2714610.0531 | 1152514.4932 | 2714606.3064 | 1152530.6661 | 2714604.7368 | 1152535.0975
96 | 2714782.5525 | 1152474.3397 | 2714792.3375 | 1152461.9943
97 | 2714668.5362 | 1152093.8722 | 2714672.8109 | 1152098.2426 | 2714679.1429 | 1152108.7813 | 2714679.9333 | 1152112.8212 | 2714679.5671 | 1152117.1394 | 2714671.9636 | 1152153.6079 | 2714666.3544 | 1152166.3875 | 2714663.3541 | 1152173.5796 | 2714661.3705 | 1152181.4027 | 2714661.1523 | 1152187.2135 | 2714663.6625 | 1152202.1268 | 2714667.9967 | 1152216.3855 | 2714669.1066 | 1152222.9999 | 2714667.9531 | 1152225.1238 | 2714665.4751 | 1152226.2552 | 2714662.3563 | 1152226.3737 | 2714659.3656 | 1152223.3926 | 2714654.3074 | 1152218.5264 | 2714645.1345 | 1152211.2581 | 2714596.7918 | 1152176.0258 | 2714591.3798 | 1152171.1974 | 2714588.8959 | 1152166.9918 | 2714587.0454 | 1152161.3751 | 2714585.9647 | 1152155.6396 | 2714585.0574 | 1152150.8747 | 2714585.0574 | 1152150.8747
98 | 2714604.7368 | 1152535.0975 | 2714598.3811 | 1152553.0414 | 2714584.6285 | 1152580.7316 | 2714583.7849 | 1152582.3846
99 | 2714792.3375 | 1152461.9943 | 2714797.2762 | 1152455.7634 | 2714799.6177 | 1152448.5031 | 2714797.5806 | 1152440.7858
100 | 2714716.2557 | 1152100.1581 | 2714713.0107 | 1152094.7167 | 2714707.9894 | 1152090.3292 | 2714701.1241 | 1152087.6412 | 2714683.9669 | 1152083.2227 | 2714674.9316 | 1152079.6038 | 2714667.9162 | 1152073.9109 | 2714662.3947 | 1152067.168 | 2714657.1062 | 1152057.4609 | 2714652.4361 | 1152049.1442 | 2714649.1344 | 1152045.5567 | 2714645.854 | 1152044.8827 | 2714643.9126 | 1152046.458 | 2714642.9326 | 1152050.7533 | 2714644.8286 | 1152055.1923 | 2714650.1083 | 1152062.5422 | 2714657.8176 | 1152081.3793 | 2714662.0849 | 1152087.4646 | 2714666.3503 | 1152091.6374 | 2714668.5362 | 1152093.8722
101 | 2714505.5815 | 1152688.5339 | 2714509.153 | 1152673.0804 | 2714511.3399 | 1152667.4626 | 2714522.1938 | 1152656.5506 | 2714532.7291 | 1152645.0321 | 2714542.6286 | 1152635.4694 | 2714550.3483 | 1152625.4985 | 2714560.2991 | 1152609.6104 | 2714566.8972 | 1152606.1447 | 2714576.1769 | 1152597.293 | 2714583.7849 | 1152582.3846
102 | 2714716.2557 | 1152100.1581 | 2714880.5928 | 1152087.3567
103 | 2714505.5815 | 1152688.5339 | 2714500.2658 | 1152690.7677 | 2714492.4734 | 1152703.3613 | 2714488.6497 | 1152709.8819 | 2714485.8261 | 1152725.1607 | 2714482.6891 | 1152736.7421 | 2714475.8354 | 1152749.2202 | 2714466.6604 | 1152761.0649 | 2714454.9715 | 1152771.9056 | 2714445.5935 | 1152779.0228
104 | 2714505.5815 | 1152688.5339 | 2714508.3594 | 1152692.2003 | 2714509.3816 | 1152696.1668 | 2714509.0587 | 1152701.442 | 2714504.7135 | 1152718.4263 | 2714503.3079 | 1152728.1616 | 2714504.1519 | 1152734.6375 | 2714505.1936 | 1152746.8544 | 2714504.7782 | 1152753.7622 | 2714502.3639 | 1152760.8433 | 2714491.5019 | 1152786.3205 | 2714489.1902 | 1152795.6717 | 2714488.3849 | 1152804.5179 | 2714489.7784 | 1152813.1724 | 2714489.2862 | 1152822.1023 | 2714489.1766 | 1152832.3071 | 2714485.2481 | 1152849.9887 | 2714485.3657 | 1152859.2078
105 | 2714445.5935 | 1152779.0228 | 2714440.7507 | 1152782.6981 | 2714438.1533 | 1152784.6152
106 | 2714485.3657 | 1152859.2078 | 2714485.4577 | 1152866.4147 | 2714484.8671 | 1152869.6168 | 2714483.3347 | 1152873.1122 | 2714478.681 | 1152881.307 | 2714469.3211 | 1152902.2303
107 | 2714438.1533 | 1152784.6152 | 2714428.7076 | 1152791.5864 | 2714408.4196 | 1152804.5875 | 2714394.5941 | 1152815.1875 | 2714383.8248 | 1152828.9478 | 2714373.4244 | 1152843.4933 | 2714367.5381 | 1152856.3791 | 2714362.2681 | 1152867.5309 | 2714358.1479 | 1152877.5927
108 | 2714469.3211 | 1152902.2303 | 2714667.2478 | 1153003.9372
109 | 2714358.1479 | 1152877.5927 | 2714355.1398 | 1152884.9387
110 | 2714355.1398 | 1152884.9387 | 2714354.3077 | 1152886.9705 | 2714348.8134 | 1152898.8137
111 | 2714881.0072 | 1152083.6216 | 2714880.5928 | 1152087.3567
112 | 2714881.0072 | 1152083.6216 | 2714883.9099 | 1152086.7902 | 2714885.0605 | 1152095.6848 | 2714885.3375 | 1152112.5458 | 2714884.783 | 1152121.0854 | 2714883.9731 | 1152126.518 | 2714886.1021 | 1152128.7935 | 2714889.5153 | 1152129.3478 | 2714891.7569 | 1152128.1342 | 2714894.2488 | 1152124.268 | 2714902.1582 | 1152099.191 | 2714903.3071 | 1152094.8989 | 2714903.6768 | 1152090.8143 | 2714902.7867 | 1152084.3597 | 2714901.9453 | 1152081.3861 | 2714902.5007 | 1152080.0402 | 2714903.8555 | 1152079.8437 | 2714905.9587 | 1152081.863 | 2714909.254 | 1152090.1981 | 2714909.7813 | 1152095.9564 | 2714909.3794 | 1152100.5185 | 2714907.3422 | 1152110.7309 | 2714905.9792 | 1152115.3747 | 2714906.4458 | 1152119.0861 | 2714909.0144 | 1152120.4471 | 2714913.0141 | 1152120.4345 | 2714916.2164 | 1152118.3608 | 2714918.3885 | 1152113.9549 | 2714920.1836 | 1152103.9602 | 2714920.4453 | 1152096.2823 | 2714919.3051 | 1152088.8556 | 2714914.2838 | 1152072.8157 | 2714910.5648 | 1152058.1238 | 2714910.2135 | 1152051.1903 | 2714910.9457 | 1152043.7993 | 2714917.2513 | 1152023.6867
113 | 2714940.0038 | 1152001.8589 | 2714932.8363 | 1152000.121 | 2714925.7394 | 1151996.2941 | 2714922.3762 | 1152008.4048 | 2714918.8011 | 1152018.7435 | 2714917.2513 | 1152023.6867
114 | 2714870.426 | 1151866.519 | 2714940.0038 | 1152001.8589
115 | 2714870.426 | 1151866.519 | 2714872.795 | 1151863.4622 | 2714875.9891 | 1151859.009 | 2714876.8934 | 1151855.8686 | 2714875.6754 | 1151849.2965 | 2714873.8759 | 1151836.587 | 2714874.6436 | 1151828.941 | 2714879.5144 | 1151817.882 | 2714892.9692 | 1151798.7146 | 2714905.8373 | 1151774.088 | 2714908.5315 | 1151766.0674 | 2714908.8833 | 1151758.4912 | 2714906.7453 | 1151748.2325 | 2714901.9294 | 1151731.8741 | 2714901.3369 | 1151726.3147 | 2714901.7299 | 1151723.8553
116 | 2714870.426 | 1151866.519 | 2714876.3812 | 1151869.0343 | 2714883.1632 | 1151870.0643 | 2714889.9646 | 1151869.6715 | 2714900.5368 | 1151865.9818 | 2714906.6218 | 1151863.3071 | 2714913.5805 | 1151861.9167 | 2714919.9578 | 1151859.6146 | 2714924.6261 | 1151855.1451 | 2714933.1109 | 1151842.1761 | 2714937.5437 | 1151835.9209
117 | 2714902.4571 | 1151699.7961 | 2714904.2048 | 1151705.1663 | 2714904.6371 | 1151710.2669 | 2714902.2261 | 1151720.7501 | 2714901.7299 | 1151723.8553
118 | 2714937.5437 | 1151835.9209 | 2714944.1744 | 1151826.5644
119 | 2714902.4571 | 1151699.7961 | 2714896.853 | 1151708.2393 | 2714894.2371 | 1151716.5839
120 | 2714902.4571 | 1151699.7961 | 2714961.8963 | 1151381.054
121 | 2714944.1744 | 1151826.5644 | 2714949.6155 | 1151818.8865 | 2714955.2009 | 1151810.9654
122 | 2714894.2371 | 1151716.5839 | 2714889.8604 | 1151743.9854 | 2714889.2192 | 1151746.6294
123 | 2714966.9264 | 1151372.2198 | 2714961.8963 | 1151381.054
124 | 2714960.6567 | 1151803.2283 | 2714955.2009 | 1151810.9654
125 | 2714886.3078 | 1151757.7585 | 2714887.0773 | 1151755.4622 | 2714889.2192 | 1151746.6294
126 | 2714886.3078 | 1151757.7585 | 2714883.3083 | 1151766.709 | 2714875.8372 | 1151778.0519 | 2714869.4762 | 1151786.7364 | 2714859.9647 | 1151795.9835 | 2714843.8041 | 1151808.9063 | 2714831.183 | 1151823.8201 | 2714820.927 | 1151836.6888 | 2714806.0874 | 1151848.3805 | 2714794.4304 | 1151858.6319 | 2714784.435 | 1151871.9218
127 | 2714784.435 | 1151871.9218 | 2714778.0081 | 1151880.4669 | 2714764.7025 | 1151889.0192 | 2714750.8258 | 1151902.5639 | 2714750.8258 | 1151902.5639

## bus_geodata
| x | y | coords
0 | 2713841.903 | 1151138.7127
1 | 2713835.4478 | 1151160.7072
2 | 2713735.7362 | 1151110.4655
3 | 2713745.3856 | 1150960.1588
4 | 2713633.6433 | 1151316.0537
5 | 2713587.5229 | 1151296.5728
6 | 2713709.678 | 1151444.2401
7 | 2713711.2154 | 1150888.3883
8 | 2713705.899 | 1150832.0394
9 | 2713960.4991 | 1150798.4976
10 | 2714058.5221 | 1150876.1555
11 | 2713925.0786 | 1150746.1611
12 | 2713778.4289 | 1151563.7865
13 | 2713702.8308 | 1151855.9305
14 | 2713510.6097 | 1151217.2578
15 | 2713670.1495 | 1151918.8971
16 | 2713631.8715 | 1152084.3313
17 | 2713604.7061 | 1152233.9518
18 | 2713812.7147 | 1152031.0541
19 | 2713852.122 | 1152104.1643
20 | 2713706.303 | 1150826.9103
21 | 2713851.0368 | 1150690.319
22 | 2713825.3053 | 1150764.4026
23 | 2713862.6768 | 1150689.9015
24 | 2714170.5104 | 1152735.547
25 | 2714148.4967 | 1152755.5125
26 | 2714157.7405 | 1152633.9621
27 | 2714154.1445 | 1152478.8542
28 | 2714392.9607 | 1152199.9011
29 | 2714417.268 | 1152229.4069
30 | 2714380.2925 | 1152057.8753
31 | 2714510.7929 | 1152331.1463
32 | 2714374.2412 | 1152064.3775
33 | 2714513.087 | 1152365.5352
34 | 2714340.9477 | 1152092.2974
35 | 2714502.8394 | 1152506.7269
36 | 2714337.0053 | 1152112.0763
37 | 2714353.0159 | 1152097.7577
38 | 2714365.7882 | 1152134.7529
39 | 2714311.8006 | 1152248.1256
40 | 2713503.5103 | 1151244.4199
41 | 2713879.833 | 1150207.874
42 | 2713878.8681 | 1150448.4936
43 | 2714085.4373 | 1150440.6861
44 | 2714128.3854 | 1150455.1645
45 | 2714034.4726 | 1150773.0444
46 | 2714041.738 | 1150789.9623
47 | 2714198.2668 | 1150605.0328
48 | 2714056.8978 | 1150814.0142
49 | 2714087.7901 | 1150873.7524
50 | 2714172.4543 | 1150467.6295
51 | 2714201.5017 | 1150512.9994
52 | 2714155.4512 | 1150458.0569
53 | 2714132.3265 | 1150899.4933
54 | 2713867.4794 | 1150689.7293
55 | 2713832.8219 | 1150820.5439
56 | 2713848.2767 | 1150893.6962
57 | 2713885.8325 | 1152182.8703
58 | 2713882.8348 | 1152247.1011
59 | 2713878.39 | 1152148.8118
60 | 2714131.1461 | 1152399.0336
61 | 2714137.1827 | 1152408.7819
62 | 2713459.2511 | 1151221.9269
63 | 2713459.3117 | 1151222.3282
64 | 2713433.4397 | 1151203.7985
65 | 2713420.9764 | 1151203.67
66 | 2713394.29 | 1151188.5818
67 | 2714145.6523 | 1152409.2275
68 | 2714162.294 | 1152397.0652
69 | 2714253.1306 | 1152296.879
70 | 2713296.7971 | 1150922.7046
71 | 2713249.3517 | 1150806.9581
72 | 2713111.8489 | 1150834.1712
73 | 2713088.4684 | 1150806.8324
74 | 2713072.3205 | 1150793.8469
75 | 2713069.494 | 1150791.5739
76 | 2713065.0583 | 1150788.0069
77 | 2713049.5727 | 1150763.2834
78 | 2713044.2086 | 1150790.2505
79 | 2713045.0306 | 1150754.9043
80 | 2713035.7044 | 1150779.7123
81 | 2713024.6109 | 1150778.1734
82 | 2713012.5108 | 1150783.5796
83 | 2714269.1342 | 1152346.8897
84 | 2714260.9188 | 1152338.7116
85 | 2714311.765 | 1152248.2028
86 | 2714259.5852 | 1152337.384
87 | 2714279.0248 | 1152211.6015
88 | 2714255.1625 | 1152319.2245
89 | 2714553.9233 | 1152492.1306
90 | 2714635.5019 | 1152318.0239
91 | 2714611.4718 | 1152487.1983
92 | 2714584.0305 | 1152148.3646
93 | 2714611.9334 | 1152501.5756
94 | 2714782.5525 | 1152474.3397
95 | 2714585.0574 | 1152150.8747
96 | 2714604.7368 | 1152535.0975
97 | 2714797.5806 | 1152440.7858
98 | 2714792.3375 | 1152461.9943
99 | 2714668.5362 | 1152093.8722
100 | 2714583.7849 | 1152582.3846
101 | 2714716.2557 | 1152100.1581
102 | 2714505.5815 | 1152688.5339
103 | 2714445.5935 | 1152779.0228
104 | 2714485.3657 | 1152859.2078
105 | 2714438.1533 | 1152784.6152
106 | 2714469.3211 | 1152902.2303
107 | 2714358.1479 | 1152877.5927
108 | 2714667.2478 | 1153003.9372
109 | 2714355.1398 | 1152884.9387
110 | 2714348.8134 | 1152898.8137
111 | 2714880.5928 | 1152087.3567
112 | 2714881.0072 | 1152083.6216
113 | 2714917.2513 | 1152023.6867
114 | 2714940.0038 | 1152001.8589
115 | 2714870.426 | 1151866.519
116 | 2714901.7299 | 1151723.8553
117 | 2714937.5437 | 1151835.9209
118 | 2714902.4571 | 1151699.7961
119 | 2714944.1744 | 1151826.5644
120 | 2714894.2371 | 1151716.5839
121 | 2714961.8963 | 1151381.054
122 | 2714955.2009 | 1151810.9654
123 | 2714960.6567 | 1151803.2283
124 | 2714889.2192 | 1151746.6294
125 | 2714966.9264 | 1151372.2198
126 | 2714886.3078 | 1151757.7585
127 | 2714784.435 | 1151871.9218
128 | 2714750.8258 | 1151902.5639
129 | 2714380.2925 | 1152057.8753

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1