## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5077-5_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5077-5_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5077-5_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5077-5_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5077-5_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5077-5_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5077-5_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_5077-5_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5077-5_0_6_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_5077-5_0_6_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_5077-5_0_6_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_5077-5_0_6_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_5077-5_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_5077-5_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5077-5_0_6_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_5077-5_0_6_node_40 | 0.4 | n |  | TRUE
16 | bus_LV_5077-5_0_6_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_5077-5_0_6_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_5077-5_0_6_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_5077-5_0_6_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_5077-5_0_6_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_5077-5_0_6_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_5077-5_0_6_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_5077-5_0_6_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_5077-5_0_6_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_5077-5_0_6_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_5077-5_0_6_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_5077-5_0_6_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_5077-5_0_6_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_5077-5_0_6_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_5077-5_0_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_5077-5_0_6_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_5077-5_0_6_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_5077-5_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_5077-5_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_5077-5_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_5077-5_0_6_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_5077-5_0_6_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_5077-5_0_6_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_5077-5_0_6_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_5077-5_0_6_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_5077-5_0_6_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_5077-5_0_6_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_5077-5_0_6_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_5077-5_0_6_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_5077-5_0_6_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_5077-5_0_6_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_5077-5_0_6_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_5077-5_0_6_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_5077-5_0_6_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_5077-5_0_6_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_5077-5_0_6_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_5077-5_0_6_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_5077-5_0_6_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_5077-5_0_6_node_57 | 0.4 | n |  | TRUE
55 | bus_LV_5077-5_0_6_node_58 | 0.4 | n |  | TRUE
56 | bus_LV_5077-5_0_6_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_5077-5_0_6_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_5077-5_0_6_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_5077-5_0_6_node_62 | 0.4 | n |  | TRUE
60 | bus_LV_5077-5_0_6_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_5077-5_0_6_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_5077-5_0_6_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_5077-5_0_6_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_5077-5_0_6_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_5077-5_0_6_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_5077-5_0_6_node_70 | 0.4 | n |  | TRUE
67 | bus_LV_5077-5_0_6_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_5077-5_0_6_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_5077-5_0_6_node_71 | 0.4 | n |  | TRUE
70 | bus_MV_186_1_node_153 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5077-5_0_6_load_0 | 0 | 0.0018315 | 0.00045902 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5077-5_0_6_load_3 | 3 | 0.0045594 | 0.0011427 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5077-5_0_6_load_6 | 6 | 0.0033776 | 0.0008465 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5077-5_0_6_load_7 | 7 | 0.0022721 | 0.00056945 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5077-5_0_6_load_27 | 10 | 0.0036517 | 0.00091521 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5077-5_0_6_load_24 | 11 | 0.001489 | 0.00037318 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5077-5_0_6_load_10 | 12 | 0.001104 | 0.00027669 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5077-5_0_6_load_11 | 13 | 0.0018216 | 0.00045653 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5077-5_0_6_load_38 | 14 | 0.0188 | 0.0047117 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5077-5_0_6_load_40 | 15 | 0.024448 | 0.0061273 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5077-5_0_6_load_39 | 16 | 0.028176 | 0.0070615 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5077-5_0_6_load_17 | 17 | 0.020637 | 0.0051721 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5077-5_0_6_load_15 | 18 | 0.0011202 | 0.00028074 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5077-5_0_6_load_23 | 19 | 0.0017159 | 0.00043004 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5077-5_0_6_load_33 | 21 | 0.0028602 | 0.00071682 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5077-5_0_6_load_34 | 22 | 0.0021301 | 0.00053385 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5077-5_0_6_load_30 | 23 | 0.0013826 | 0.00034651 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5077-5_0_6_load_16 | 24 | 0.0014252 | 0.00035718 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5077-5_0_6_load_12 | 25 | 0.0025916 | 0.00064951 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5077-5_0_6_load_20 | 26 | 0.0010245 | 0.00025675 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5077-5_0_6_load_37 | 29 | 0.027854 | 0.006981 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5077-5_0_6_load_36 | 30 | 0.0015235 | 0.00038181 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5077-5_0_6_load_41 | 31 | 0.022087 | 0.0055356 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5077-5_0_6_load_21 | 32 | 0.0014276 | 0.00035779 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5077-5_0_6_load_22 | 33 | 0.0034074 | 0.00085396 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5077-5_0_6_load_26 | 35 | 0.0017858 | 0.00044756 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5077-5_0_6_load_35 | 36 | 0.0016519 | 0.000414 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5077-5_0_6_load_31 | 37 | 0.001759 | 0.00044085 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5077-5_0_6_load_73 | 38 | 0.0017059 | 0.00042754 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5077-5_0_6_load_42 | 39 | 0.00064489 | 0.00016163 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5077-5_0_6_load_43 | 40 | 0.00058354 | 0.00014625 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5077-5_0_6_load_44 | 41 | 0.00090573 | 0.000227 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5077-5_0_6_load_45 | 42 | 0.00059144 | 0.00014823 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5077-5_0_6_load_46 | 43 | 0.00087056 | 0.00021818 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5077-5_0_6_load_47 | 44 | 0.00067685 | 0.00016963 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5077-5_0_6_load_48 | 45 | 0.0011046 | 0.00027683 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5077-5_0_6_load_49 | 46 | 0.00083243 | 0.00020863 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5077-5_0_6_load_50 | 47 | 0.0014898 | 0.00037339 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5077-5_0_6_load_51 | 48 | 0.0007766 | 0.00019463 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5077-5_0_6_load_55 | 49 | 0.00097751 | 0.00024499 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5077-5_0_6_load_52 | 50 | 0.00070469 | 0.00017661 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5077-5_0_6_load_53 | 51 | 0.00063659 | 0.00015954 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5077-5_0_6_load_54 | 52 | 0.00074836 | 0.00018756 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5077-5_0_6_load_56 | 53 | 0.00060893 | 0.00015261 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5077-5_0_6_load_57 | 54 | 0.00062647 | 0.00015701 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5077-5_0_6_load_58 | 55 | 0.00074266 | 0.00018613 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5077-5_0_6_load_59 | 56 | 0.0010187 | 0.00025532 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5077-5_0_6_load_61 | 58 | 0.0014567 | 0.00036507 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5077-5_0_6_load_62 | 59 | 0.00087547 | 0.00021941 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5077-5_0_6_load_63 | 60 | 0.0010054 | 0.00025198 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5077-5_0_6_load_64 | 61 | 0.00058298 | 0.00014611 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5077-5_0_6_load_67 | 62 | 0.0030586 | 0.00076657 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5077-5_0_6_load_65 | 63 | 0.0015784 | 0.00039558 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5077-5_0_6_load_66 | 64 | 0.0015583 | 0.00039056 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5077-5_0_6_load_72 | 65 | 0.0014991 | 0.0003757 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5077-5_0_6_load_70 | 66 | 0.0015736 | 0.00039437 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5077-5_0_6_load_68 | 67 | 0.0016173 | 0.00040532 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5077-5_0_6_load_69 | 68 | 0.0013526 | 0.00033899 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5077-5_0_6_load_71 | 69 | 0.001373 | 0.0003441 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5077-5_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.018777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5077-5_0_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5077-5_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5077-5_0_6_line_3 | NAYY 4x150 SE | 1 | 4 | 0.0459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5077-5_0_6_line_4 | NAYY 4x150 SE | 1 | 5 | 0.014438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5077-5_0_6_line_5 | NAYY 4x150 SE | 2 | 6 | 0.015309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5077-5_0_6_line_6 | NAYY 4x150 SE | 2 | 7 | 0.014343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5077-5_0_6_line_7 | NAYY 4x150 SE | 4 | 8 | 0.012972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5077-5_0_6_line_8 | NAYY 4x150 SE | 4 | 9 | 0.014222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5077-5_0_6_line_9 | NAYY 4x150 SE | 5 | 10 | 0.0097524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5077-5_0_6_line_10 | NAYY 4x150 SE | 6 | 11 | 0.0048827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5077-5_0_6_line_11 | NAYY 4x150 SE | 8 | 14 | 0.016528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5077-5_0_6_line_12 | NAYY 4x150 SE | 9 | 15 | 0.031571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5077-5_0_6_line_13 | NAYY 4x150 SE | 9 | 16 | 0.011022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5077-5_0_6_line_14 | NAYY 4x150 SE | 11 | 19 | 0.0041918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5077-5_0_6_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0093169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5077-5_0_6_line_16 | NAYY 4x150 SE | 13 | 24 | 0.016691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5077-5_0_6_line_17 | NAYY 4x150 SE | 13 | 25 | 0.020988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5077-5_0_6_line_18 | NAYY 4x150 SE | 17 | 18 | 0.0039634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5077-5_0_6_line_19 | NAYY 4x150 SE | 18 | 27 | 0.012527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5077-5_0_6_line_20 | NAYY 4x150 SE | 19 | 34 | 0.0089406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5077-5_0_6_line_21 | NAYY 4x150 SE | 20 | 21 | 0.015332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_5077-5_0_6_line_22 | NAYY 4x150 SE | 20 | 22 | 0.014875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_5077-5_0_6_line_23 | NAYY 4x150 SE | 20 | 23 | 0.023194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5077-5_0_6_line_24 | NAYY 4x150 SE | 21 | 36 | 0.023979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_5077-5_0_6_line_25 | NAYY 4x150 SE | 22 | 35 | 0.00044195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_5077-5_0_6_line_26 | NAYY 4x150 SE | 23 | 37 | 0.0034201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5077-5_0_6_line_27 | NAYY 4x150 SE | 24 | 26 | 0.0021869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5077-5_0_6_line_28 | NAYY 4x150 SE | 25 | 27 | 0.016284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5077-5_0_6_line_29 | NAYY 4x150 SE | 26 | 32 | 0.00080424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5077-5_0_6_line_30 | NAYY 4x150 SE | 27 | 28 | 0.010208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5077-5_0_6_line_31 | NAYY 4x150 SE | 28 | 29 | 0.044522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5077-5_0_6_line_32 | NAYY 4x150 SE | 28 | 30 | 0.016473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5077-5_0_6_line_33 | NAYY 4x150 SE | 29 | 31 | 0.012055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5077-5_0_6_line_34 | NAYY 4x150 SE | 32 | 33 | 0.022638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5077-5_0_6_line_35 | NAYY 4x150 SE | 33 | 34 | 0.0015788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5077-5_0_6_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0083401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_5077-5_0_6_line_37 | NAYY 4x150 SE | 36 | 38 | 0.59403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_5077-5_0_6_line_38 | NAYY 4x150 SE | 38 | 65 | 0.00080354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_5077-5_0_6_line_39 | NAYY 4x150 SE | 39 | 40 | 0.00062583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5077-5_0_6_line_40 | NAYY 4x150 SE | 40 | 41 | 0.0097663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5077-5_0_6_line_41 | NAYY 4x150 SE | 41 | 42 | 0.0076187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5077-5_0_6_line_42 | NAYY 4x150 SE | 42 | 43 | 3.7588e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5077-5_0_6_line_43 | NAYY 4x150 SE | 43 | 44 | 0.0016278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5077-5_0_6_line_44 | NAYY 4x150 SE | 44 | 45 | 0.0021228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5077-5_0_6_line_45 | NAYY 4x150 SE | 45 | 46 | 0.0054198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5077-5_0_6_line_46 | NAYY 4x150 SE | 46 | 47 | 0.0034957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5077-5_0_6_line_47 | NAYY 4x150 SE | 47 | 48 | 0.0013083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5077-5_0_6_line_48 | NAYY 4x150 SE | 48 | 49 | 0.0062111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5077-5_0_6_line_49 | NAYY 4x150 SE | 49 | 51 | 0.019075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5077-5_0_6_line_50 | NAYY 4x150 SE | 50 | 51 | 0.020483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5077-5_0_6_line_51 | NAYY 4x150 SE | 50 | 52 | 0.017569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5077-5_0_6_line_52 | NAYY 4x150 SE | 52 | 53 | 0.039969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5077-5_0_6_line_53 | NAYY 4x150 SE | 53 | 54 | 0.029256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5077-5_0_6_line_54 | NAYY 4x150 SE | 54 | 55 | 0.011369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5077-5_0_6_line_55 | NAYY 4x150 SE | 55 | 56 | 0.23327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5077-5_0_6_line_56 | NAYY 4x150 SE | 56 | 57 | 0.10463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5077-5_0_6_line_57 | NAYY 4x150 SE | 57 | 58 | 0.10797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5077-5_0_6_line_58 | NAYY 4x150 SE | 57 | 59 | 0.11625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5077-5_0_6_line_59 | NAYY 4x150 SE | 58 | 60 | 0.1381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_5077-5_0_6_line_60 | NAYY 4x150 SE | 60 | 61 | 0.0059104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_5077-5_0_6_line_61 | NAYY 4x150 SE | 61 | 62 | 0.069981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_5077-5_0_6_line_62 | NAYY 4x150 SE | 62 | 67 | 0.13598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_5077-5_0_6_line_63 | NAYY 4x150 SE | 63 | 64 | 0.048555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5077-5_0_6_line_64 | NAYY 4x150 SE | 64 | 65 | 0.021632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_5077-5_0_6_line_65 | NAYY 4x150 SE | 64 | 66 | 0.19133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_5077-5_0_6_line_66 | NAYY 4x150 SE | 66 | 69 | 0.18332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5077-5_0_6_line_67 | NAYY 4x150 SE | 66 | 68 | 0.0024638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_5077-5_0_6_line_68 | NAYY 4x150 SE | 67 | 68 | 0.022997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5077-5_0_6_trafo_35 | 0.25 MVA 20/0.4 kV | 70 | 36 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2715798.1022 | 1135981.2334 | 2715790.9806 | 1135986.5449 | 2715784.5296 | 1135994.0448
1 | 2715765.5517 | 1136008.5055 | 2715783.3599 | 1135995.4047 | 2715784.5296 | 1135994.0448
2 | 2715798.1022 | 1135981.2334 | 2715804.5324 | 1135989.4067
3 | 2715837.8177 | 1135958.4464 | 2715817.5601 | 1135967.6085 | 2715805.0142 | 1135976.018 | 2715798.1022 | 1135981.2334
4 | 2715798.1022 | 1135981.2334 | 2715791.1328 | 1135968.5803
5 | 2715765.5517 | 1136008.5055 | 2715773.9302 | 1136021.3183
6 | 2715765.5517 | 1136008.5055 | 2715753.1305 | 1136015.6771
7 | 2715837.8177 | 1135958.4464 | 2715832.7358 | 1135946.5076
8 | 2715837.8177 | 1135958.4464 | 2715846.8952 | 1135947.4798
9 | 2715791.1328 | 1135968.5803 | 2715783.3162 | 1135974.4121
10 | 2715776.6025 | 1136025.4048 | 2715773.9302 | 1136021.3183
11 | 2715832.7358 | 1135946.5076 | 2715825.754 | 1135931.5266
12 | 2715846.8952 | 1135947.4798 | 2715859.1483 | 1135935.8849 | 2715873.6141 | 1135932.927
13 | 2715846.8952 | 1135947.4798 | 2715841.7941 | 1135937.7092
14 | 2715776.6025 | 1136025.4048 | 2715778.8966 | 1136028.9131
15 | 2715823.9744 | 1136019.2215 | 2715819.609 | 1136010.9907
16 | 2715823.9744 | 1136019.2215 | 2715807.9446 | 1136023.8728 | 2715807.9446 | 1136023.8728
17 | 2715823.9744 | 1136019.2215 | 2715844.3829 | 1136014.3227
18 | 2715858.2133 | 1135998.5812 | 2715858.952 | 1135994.6872
19 | 2715860.2173 | 1136010.5219 | 2715857.8933 | 1136006.0855 | 2715858.0946 | 1135999.207 | 2715858.2133 | 1135998.5812
20 | 2715783.7898 | 1136036.3959 | 2715778.8966 | 1136028.9131
21 | 2715762.7838 | 1136047.2783 | 2715752.329 | 1136056.2284 | 2715751.1975 | 1136057.3156
22 | 2715762.7838 | 1136047.2783 | 2715775.992 | 1136040.4356
23 | 2715762.7838 | 1136047.2783 | 2715771.2304 | 1136058.759 | 2715776.6669 | 1136065.8568
24 | 2715751.1975 | 1136057.3156 | 2715745.9304 | 1136062.3765 | 2715745.1035 | 1136066.9638 | 2715749.4903 | 1136078.1478
25 | 2715775.992 | 1136040.4356 | 2715776.3844 | 1136040.2324
26 | 2715776.6669 | 1136065.8568 | 2715779.6835 | 1136067.4684
27 | 2715807.9446 | 1136023.8728 | 2715806.0031 | 1136024.8794
28 | 2715860.2173 | 1136010.5219 | 2715844.3829 | 1136014.3227
29 | 2715805.2891 | 1136025.2496 | 2715806.0031 | 1136024.8794
30 | 2715860.2173 | 1136010.5219 | 2715865.5924 | 1136019.2086
31 | 2715865.5924 | 1136019.2086 | 2715896.943 | 1135987.5958
32 | 2715865.5924 | 1136019.2086 | 2715853.7379 | 1136030.646
33 | 2715896.943 | 1135987.5958 | 2715904.7511 | 1135979.7224 | 2715905.5602 | 1135979.1943
34 | 2715785.1914 | 1136035.6692 | 2715805.2891 | 1136025.2496
35 | 2715783.7898 | 1136036.3959 | 2715785.1914 | 1136035.6692
36 | 2715783.7898 | 1136036.3959 | 2715776.3844 | 1136040.2324
37 | 2715749.4903 | 1136078.1478 | 2715573.3271 | 1136645.4521
38 | 2715572.6051 | 1136645.8048 | 2715573.3271 | 1136645.4521
39 | 2714936.1037 | 1137487.6611 | 2714936.5759 | 1137487.2503
40 | 2714943.4452 | 1137480.3142 | 2714937.5925 | 1137486.3659 | 2714936.5759 | 1137487.2503
41 | 2714943.4452 | 1137480.3142 | 2714945.7013 | 1137477.9813 | 2714949.2606 | 1137475.4402
42 | 2714949.2606 | 1137475.4402 | 2714949.2912 | 1137475.4184
43 | 2714949.2912 | 1137475.4184 | 2714950.616 | 1137474.4725 | 2714950.616 | 1137474.4725
44 | 2714952.613 | 1137473.7524 | 2714950.616 | 1137474.4725
45 | 2714952.613 | 1137473.7524 | 2714956.8535 | 1137472.2231 | 2714957.757 | 1137472.099
46 | 2714957.757 | 1137472.099 | 2714961.2202 | 1137471.6231
47 | 2714961.2202 | 1137471.6231 | 2714962.5163 | 1137471.445
48 | 2714962.5163 | 1137471.445 | 2714968.6502 | 1137470.6022 | 2714968.667 | 1137470.592
49 | 2714981.5481 | 1137457.1256 | 2714978.9246 | 1137462.0476 | 2714974.2862 | 1137467.2072 | 2714968.667 | 1137470.592
50 | 2714989.6641 | 1137438.3303 | 2714982.7791 | 1137454.8162 | 2714981.5481 | 1137457.1256
51 | 2714989.6641 | 1137438.3303 | 2714990.2374 | 1137436.9575 | 2714996.5815 | 1137422.1808
52 | 2714996.5815 | 1137422.1808 | 2714998.1209 | 1137418.5954 | 2715003.3807 | 1137407.8884 | 2715016.3964 | 1137391.1696 | 2715018.2137 | 1137388.8458
53 | 2715018.2137 | 1137388.8458 | 2715036.2366 | 1137365.8
54 | 2715036.2366 | 1137365.8 | 2715043.2403 | 1137356.8444
55 | 2715043.2403 | 1137356.8444 | 2715055.9523 | 1137340.5894 | 2715068.7195 | 1137326.023 | 2715103.7983 | 1137288.7222 | 2715113.0932 | 1137277.4808 | 2715117.669 | 1137270.3744 | 2715132.23 | 1137242.8781 | 2715146.2209 | 1137218.2396 | 2715153.7993 | 1137205.0197 | 2715157.7034 | 1137195.2099 | 2715162.0367 | 1137173.3891 | 2715165.4411 | 1137162.3688
56 | 2715244.0908 | 1137097.3926 | 2715229.779 | 1137102.1227 | 2715207.713 | 1137118.3903 | 2715184.5373 | 1137135.5485 | 2715176.9531 | 1137143.4202 | 2715169.8743 | 1137152.2356 | 2715165.8918 | 1137160.9098 | 2715165.4411 | 1137162.3688
57 | 2715244.0908 | 1137097.3926 | 2715263.2516 | 1137088.5969 | 2715285.8679 | 1137071.7395 | 2715323.512 | 1137046.119 | 2715332.8318 | 1137036.8492
58 | 2715244.0908 | 1137097.3926 | 2715262.7467 | 1137084.4066 | 2715276.0038 | 1137069.2273 | 2715304.5613 | 1137019.7395 | 2715313.8391 | 1137006.4262
59 | 2715332.8318 | 1137036.8492 | 2715363.4893 | 1137006.356 | 2715381.2889 | 1136993.1094 | 2715394.9843 | 1136984.0095 | 2715398.4592 | 1136980.1733 | 2715409.4167 | 1136973.8007 | 2715431.7677 | 1136949.5339 | 2715435.6038 | 1136945.7487
60 | 2715439.811 | 1136941.5976 | 2715435.6038 | 1136945.7487
61 | 2715439.811 | 1136941.5976 | 2715450.5929 | 1136930.9591 | 2715456.641 | 1136927.7837 | 2715471.6851 | 1136918.1983 | 2715488.0644 | 1136903.5906 | 2715494.9874 | 1136899.1618
62 | 2715494.9874 | 1136899.1618 | 2715499.4552 | 1136896.3036 | 2715538.7963 | 1136873.8077 | 2715555.1692 | 1136865.1708 | 2715587.8542 | 1136855.9123 | 2715616.6895 | 1136840.1155
63 | 2715505.6242 | 1136660.2322 | 2715514.2263 | 1136656.5039 | 2715553.399 | 1136655.7527
64 | 2715553.399 | 1136655.7527 | 2715553.399 | 1136655.7527 | 2715567.0909 | 1136648.4988 | 2715572.6051 | 1136645.8048
65 | 2715638.534 | 1136827.0956 | 2715553.399 | 1136655.7527
66 | 2715638.534 | 1136827.0956 | 2715666.8086 | 1136807.6361 | 2715692.1673 | 1136787.5418 | 2715703.7828 | 1136773.7773 | 2715715.0959 | 1136765.3551 | 2715728.3961 | 1136760.4622 | 2715761.0357 | 1136759.2314 | 2715798.3352 | 1136764.6301
67 | 2715638.534 | 1136827.0956 | 2715636.5044 | 1136828.4924
68 | 2715616.6895 | 1136840.1155 | 2715631.0353 | 1136832.2564 | 2715636.5044 | 1136828.4924

## bus_geodata
| x | y | coords
0 | 2715784.5296 | 1135994.0448
1 | 2715798.1022 | 1135981.2334
2 | 2715765.5517 | 1136008.5055
3 | 2715804.5324 | 1135989.4067
4 | 2715837.8177 | 1135958.4464
5 | 2715791.1328 | 1135968.5803
6 | 2715773.9302 | 1136021.3183
7 | 2715753.1305 | 1136015.6771
8 | 2715832.7358 | 1135946.5076
9 | 2715846.8952 | 1135947.4798
10 | 2715783.3162 | 1135974.4121
11 | 2715776.6025 | 1136025.4048
12 | 2715819.609 | 1136010.9907
13 | 2715823.9744 | 1136019.2215
14 | 2715825.754 | 1135931.5266
15 | 2715873.6141 | 1135932.927
16 | 2715841.7941 | 1135937.7092
17 | 2715858.952 | 1135994.6872
18 | 2715858.2133 | 1135998.5812
19 | 2715778.8966 | 1136028.9131
20 | 2715762.7838 | 1136047.2783
21 | 2715751.1975 | 1136057.3156
22 | 2715775.992 | 1136040.4356
23 | 2715776.6669 | 1136065.8568
24 | 2715807.9446 | 1136023.8728
25 | 2715844.3829 | 1136014.3227
26 | 2715806.0031 | 1136024.8794
27 | 2715860.2173 | 1136010.5219
28 | 2715865.5924 | 1136019.2086
29 | 2715896.943 | 1135987.5958
30 | 2715853.7379 | 1136030.646
31 | 2715905.5602 | 1135979.1943
32 | 2715805.2891 | 1136025.2496
33 | 2715785.1914 | 1136035.6692
34 | 2715783.7898 | 1136036.3959
35 | 2715776.3844 | 1136040.2324
36 | 2715749.4903 | 1136078.1478
37 | 2715779.6835 | 1136067.4684
38 | 2715573.3271 | 1136645.4521
39 | 2714936.1038 | 1137487.6611
40 | 2714936.5759 | 1137487.2503
41 | 2714943.4452 | 1137480.3142
42 | 2714949.2606 | 1137475.4402
43 | 2714949.2912 | 1137475.4184
44 | 2714950.616 | 1137474.4725
45 | 2714952.613 | 1137473.7524
46 | 2714957.757 | 1137472.099
47 | 2714961.2202 | 1137471.6231
48 | 2714962.5163 | 1137471.445
49 | 2714968.667 | 1137470.592
50 | 2714989.6641 | 1137438.3303
51 | 2714981.5481 | 1137457.1256
52 | 2714996.5815 | 1137422.1808
53 | 2715018.2137 | 1137388.8458
54 | 2715036.2366 | 1137365.8
55 | 2715043.2403 | 1137356.8444
56 | 2715165.4411 | 1137162.3688
57 | 2715244.0908 | 1137097.3926
58 | 2715332.8318 | 1137036.8492
59 | 2715313.8391 | 1137006.4262
60 | 2715435.6038 | 1136945.7487
61 | 2715439.811 | 1136941.5976
62 | 2715494.9874 | 1136899.1618
63 | 2715505.6242 | 1136660.2322
64 | 2715553.399 | 1136655.7527
65 | 2715572.6051 | 1136645.8048
66 | 2715638.534 | 1136827.0956
67 | 2715616.6895 | 1136840.1155
68 | 2715636.5044 | 1136828.4924
69 | 2715798.3352 | 1136764.6301
70 | 2715742.792 | 1136100.8087

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1