## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5097-34_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5097-34_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5097-34_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5097-34_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_5097-34_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_5097-34_0_6_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_5097-34_0_6_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_5097-34_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5097-34_0_6_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_5097-34_0_6_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_5097-34_0_6_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_5097-34_0_6_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_5097-34_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_5097-34_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_5097-34_0_6_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_5097-34_0_6_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_5097-34_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_5097-34_0_6_node_58 | 0.4 | n |  | TRUE
18 | bus_LV_5097-34_0_6_node_59 | 0.4 | n |  | TRUE
19 | bus_LV_5097-34_0_6_node_63 | 0.4 | n |  | TRUE
20 | bus_LV_5097-34_0_6_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_5097-34_0_6_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_5097-34_0_6_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_5097-34_0_6_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_5097-34_0_6_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_5097-34_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_5097-34_0_6_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_5097-34_0_6_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_5097-34_0_6_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_5097-34_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_5097-34_0_6_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_5097-34_0_6_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_5097-34_0_6_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_5097-34_0_6_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_5097-34_0_6_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_5097-34_0_6_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_5097-34_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_5097-34_0_6_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_5097-34_0_6_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_5097-34_0_6_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_5097-34_0_6_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_5097-34_0_6_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_5097-34_0_6_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_5097-34_0_6_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_5097-34_0_6_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_5097-34_0_6_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_5097-34_0_6_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_5097-34_0_6_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_5097-34_0_6_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_5097-34_0_6_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_5097-34_0_6_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_5097-34_0_6_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_5097-34_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_5097-34_0_6_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_5097-34_0_6_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_5097-34_0_6_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_5097-34_0_6_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_5097-34_0_6_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_5097-34_0_6_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_5097-34_0_6_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_5097-34_0_6_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_5097-34_0_6_node_66 | 0.4 | n |  | TRUE
62 | bus_MV_65_0_node_136 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5097-34_0_6_load_0 | 0 | 0.0024196 | 0.00060641 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5097-34_0_6_load_1 | 1 | 0.002023 | 0.000507 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5097-34_0_6_load_4 | 3 | 0.004019 | 0.0010073 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5097-34_0_6_load_5 | 4 | 0.0038365 | 0.00096151 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5097-34_0_6_load_20 | 8 | 0.0013803 | 0.00034595 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5097-34_0_6_load_18 | 9 | 0.0035305 | 0.00088483 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5097-34_0_6_load_26 | 10 | 0.0039055 | 0.0009788 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5097-34_0_6_load_19 | 11 | 0.0034221 | 0.00085767 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5097-34_0_6_load_8 | 12 | 0.0051183 | 0.0012828 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5097-34_0_6_load_9 | 13 | 0.0028437 | 0.00071269 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5097-34_0_6_load_10 | 14 | 0.003877 | 0.00097167 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5097-34_0_6_load_63 | 19 | 0.002544 | 0.00063758 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5097-34_0_6_load_57 | 21 | 0.0028237 | 0.00070769 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5097-34_0_6_load_42 | 22 | 0.0035969 | 0.00090146 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5097-34_0_6_load_65 | 23 | 0.0033297 | 0.00083449 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5097-34_0_6_load_55 | 24 | 0.0028208 | 0.00070697 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5097-34_0_6_load_16 | 25 | 0.0022524 | 0.00056449 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5097-34_0_6_load_13 | 26 | 0.0032632 | 0.00081783 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5097-34_0_6_load_14 | 27 | 0.0023697 | 0.00059391 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5097-34_0_6_load_15 | 28 | 0.0054503 | 0.001366 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5097-34_0_6_load_17 | 29 | 0.0049838 | 0.0012491 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5097-34_0_6_load_36 | 30 | 0.0046186 | 0.0011575 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5097-34_0_6_load_27 | 32 | 0.0040693 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5097-34_0_6_load_21 | 33 | 0.012569 | 0.00315 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5097-34_0_6_load_22 | 34 | 0.0029998 | 0.00075182 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5097-34_0_6_load_23 | 35 | 0.0059495 | 0.0014911 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5097-34_0_6_load_24 | 36 | 0.0080876 | 0.002027 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5097-34_0_6_load_25 | 37 | 0.0068106 | 0.0017069 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5097-34_0_6_load_30 | 38 | 0.0041467 | 0.0010393 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5097-34_0_6_load_35 | 41 | 0.0087032 | 0.0021812 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5097-34_0_6_load_37 | 42 | 0.0084698 | 0.0021227 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5097-34_0_6_load_28 | 43 | 0.0080433 | 0.0020159 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5097-34_0_6_load_29 | 44 | 0.0085277 | 0.0021373 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5097-34_0_6_load_49 | 46 | 0.005367 | 0.0013451 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5097-34_0_6_load_50 | 48 | 0.0080806 | 0.0020252 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5097-34_0_6_load_32 | 49 | 0.0040144 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5097-34_0_6_load_33 | 50 | 0.0043928 | 0.0011009 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5097-34_0_6_load_38 | 51 | 0.0023526 | 0.00058961 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5097-34_0_6_load_40 | 52 | 0.0069805 | 0.0017495 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5097-34_0_6_load_41 | 53 | 0.013623 | 0.0034142 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5097-34_0_6_load_45 | 54 | 0.0072683 | 0.0018216 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5097-34_0_6_load_60 | 55 | 0.00225 | 0.00056391 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5097-34_0_6_load_52 | 56 | 0.0065134 | 0.0016324 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5097-34_0_6_load_53 | 57 | 0.0042103 | 0.0010552 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5097-34_0_6_load_61 | 58 | 0.0021359 | 0.00053531 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5097-34_0_6_load_64 | 59 | 0.002391 | 0.00059924 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5097-34_0_6_load_62 | 60 | 0.0033341 | 0.00083561 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5097-34_0_6_load_66 | 61 | 0.0032046 | 0.00080315 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5097-34_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0019092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5097-34_0_6_line_1 | NAYY 4x150 SE | 1 | 2 | 0.021892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5097-34_0_6_line_2 | NAYY 4x150 SE | 2 | 3 | 0.082762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5097-34_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.042524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5097-34_0_6_line_4 | NAYY 4x150 SE | 4 | 5 | 0.10241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5097-34_0_6_line_5 | NAYY 4x150 SE | 5 | 6 | 0.025706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5097-34_0_6_line_6 | NAYY 4x150 SE | 6 | 45 | 0.076763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5097-34_0_6_line_7 | NAYY 4x150 SE | 6 | 44 | 0.041448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5097-34_0_6_line_8 | NAYY 4x150 SE | 7 | 8 | 0.01315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5097-34_0_6_line_9 | NAYY 4x150 SE | 7 | 9 | 0.0039161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5097-34_0_6_line_10 | NAYY 4x150 SE | 8 | 10 | 0.00045487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5097-34_0_6_line_11 | NAYY 4x150 SE | 9 | 11 | 0.01793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5097-34_0_6_line_12 | NAYY 4x150 SE | 10 | 32 | 0.016614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5097-34_0_6_line_13 | NAYY 4x150 SE | 12 | 13 | 0.01178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5097-34_0_6_line_14 | NAYY 4x150 SE | 12 | 14 | 0.0022766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5097-34_0_6_line_15 | NAYY 4x150 SE | 13 | 15 | 0.016645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5097-34_0_6_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0078328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5097-34_0_6_line_17 | NAYY 4x150 SE | 15 | 17 | 0.005063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5097-34_0_6_line_18 | NAYY 4x150 SE | 16 | 18 | 0.045947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5097-34_0_6_line_19 | NAYY 4x150 SE | 16 | 19 | 0.0032825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5097-34_0_6_line_20 | NAYY 4x150 SE | 17 | 23 | 0.017713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5097-34_0_6_line_21 | NAYY 4x150 SE | 18 | 24 | 0.029844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5097-34_0_6_line_22 | NAYY 4x150 SE | 19 | 25 | 0.0053235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5097-34_0_6_line_23 | NAYY 4x150 SE | 20 | 21 | 0.028472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5097-34_0_6_line_24 | NAYY 4x150 SE | 20 | 22 | 0.017447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5097-34_0_6_line_25 | NAYY 4x150 SE | 21 | 55 | 0.002349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5097-34_0_6_line_26 | NAYY 4x150 SE | 22 | 53 | 0.01245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5097-34_0_6_line_27 | NAYY 4x150 SE | 23 | 59 | 0.016895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5097-34_0_6_line_28 | NAYY 4x150 SE | 24 | 57 | 0.016245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5097-34_0_6_line_29 | NAYY 4x150 SE | 25 | 27 | 0.00020144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5097-34_0_6_line_30 | NAYY 4x150 SE | 26 | 27 | 0.0058624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5097-34_0_6_line_31 | NAYY 4x150 SE | 26 | 28 | 0.027208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_5097-34_0_6_line_32 | NAYY 4x150 SE | 28 | 29 | 0.014847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_5097-34_0_6_line_33 | NAYY 4x150 SE | 29 | 30 | 0.037079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_5097-34_0_6_line_34 | NAYY 4x150 SE | 30 | 31 | 0.088756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_5097-34_0_6_line_35 | NAYY 4x150 SE | 31 | 49 | 0.10036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_5097-34_0_6_line_36 | NAYY 4x150 SE | 32 | 43 | 0.012746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5097-34_0_6_line_37 | NAYY 4x150 SE | 33 | 34 | 0.01407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5097-34_0_6_line_38 | NAYY 4x150 SE | 33 | 35 | 0.039805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_5097-34_0_6_line_39 | NAYY 4x150 SE | 34 | 36 | 0.013609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5097-34_0_6_line_40 | NAYY 4x150 SE | 35 | 37 | 0.03934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_5097-34_0_6_line_41 | NAYY 4x150 SE | 36 | 38 | 0.036075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5097-34_0_6_line_42 | NAYY 4x150 SE | 37 | 39 | 0.074992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_5097-34_0_6_line_43 | NAYY 4x150 SE | 38 | 40 | 0.022935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5097-34_0_6_line_44 | NAYY 4x150 SE | 39 | 41 | 0.047707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_5097-34_0_6_line_45 | NAYY 4x150 SE | 39 | 42 | 0.022588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5097-34_0_6_line_46 | NAYY 4x150 SE | 40 | 46 | 0.021488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5097-34_0_6_line_47 | NAYY 4x150 SE | 40 | 47 | 0.038956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5097-34_0_6_line_48 | NAYY 4x150 SE | 41 | 50 | 0.0047064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_5097-34_0_6_line_49 | NAYY 4x150 SE | 42 | 51 | 0.0066997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5097-34_0_6_line_50 | NAYY 4x150 SE | 43 | 44 | 0.025808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5097-34_0_6_line_51 | NAYY 4x150 SE | 45 | 48 | 0.056103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5097-34_0_6_line_52 | NAYY 4x150 SE | 46 | 54 | 0.0056793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5097-34_0_6_line_53 | NAYY 4x150 SE | 47 | 48 | 0.0069509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5097-34_0_6_line_54 | NAYY 4x150 SE | 49 | 50 | 0.035854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_5097-34_0_6_line_55 | NAYY 4x150 SE | 51 | 52 | 0.020509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5097-34_0_6_line_56 | NAYY 4x150 SE | 55 | 58 | 0.0080939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5097-34_0_6_line_57 | NAYY 4x150 SE | 56 | 57 | 0.030755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5097-34_0_6_line_58 | NAYY 4x150 SE | 58 | 60 | 0.0044297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5097-34_0_6_line_59 | NAYY 4x150 SE | 59 | 61 | 0.00052447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5097-34_0_6_line_60 | NAYY 4x150 SE | 60 | 61 | 0.0022065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5097-34_0_6_trafo_25 | 0.25 MVA 20/0.4 kV | 62 | 37 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2697955.1973 | 1109085.7341 | 2697957.0377 | 1109086.2423
1 | 2697978.1401 | 1109092.0687 | 2697957.0377 | 1109086.2423
2 | 2697978.1401 | 1109092.0687 | 2697991.1975 | 1109099.2174 | 2698041.1374 | 1109130.2547 | 2698044.8261 | 1109132.0932 | 2698049.2096 | 1109133.5094 | 2698049.5549 | 1109133.5556
3 | 2697978.1401 | 1109092.0687 | 2697970.8033 | 1109085.8797 | 2697999.065 | 1109068.987
4 | 2697965.2622 | 1109012.5667 | 2697980.9856 | 1109037.9698 | 2697992.6596 | 1109037.925 | 2698008.1582 | 1109029.3922 | 2698007.6358 | 1109039.7125 | 2698006.4208 | 1109041.2271 | 2698007.1221 | 1109056.6703 | 2698003.2762 | 1109066.4698 | 2697999.065 | 1109068.987
5 | 2697966.2315 | 1108995.6385 | 2697961.5945 | 1108996.9867 | 2697959.559 | 1108998.0879 | 2697963.368 | 1109002.0518 | 2697967.3153 | 1109005.5955 | 2697967.7071 | 1109008.6149 | 2697966.8976 | 1109010.8699 | 2697965.2622 | 1109012.5667
6 | 2697929.9902 | 1108949.2023 | 2697927.6277 | 1108949.0084 | 2697924.9983 | 1108949.066 | 2697923.4245 | 1108949.3408 | 2697921.7588 | 1108950.0477 | 2697920.1282 | 1108951.9226 | 2697919.4706 | 1108953.3906 | 2697919.2456 | 1108955.3549 | 2697919.6218 | 1108956.4728 | 2697920.2559 | 1108957.4169 | 2697922.4739 | 1108959.3762 | 2697929.5965 | 1108963.5271 | 2697936.1155 | 1108968.1907 | 2697942.0997 | 1108973.8909 | 2697966.2315 | 1108995.6385
7 | 2697966.2315 | 1108995.6385 | 2697972.0676 | 1109000.936 | 2697980.4631 | 1109008.1094 | 2697982.8869 | 1109009.7718 | 2697985.2684 | 1109010.6998 | 2697987.3285 | 1109010.9443 | 2697990.4561 | 1109010.6724 | 2697993.3524 | 1109009.8854 | 2697995.6045 | 1109008.7766 | 2697997.945 | 1109007.458 | 2698000.626 | 1109005.0301
8 | 2698045.9418 | 1109027.2347 | 2698045.7831 | 1109023.6632 | 2698044.9021 | 1109019.3463 | 2698043.7068 | 1109015.8137 | 2698043.0396 | 1109014.5379
9 | 2698045.9418 | 1109027.2347 | 2698047.5823 | 1109029.0512 | 2698048.3541 | 1109030.3004
10 | 2698042.8288 | 1109014.1348 | 2698043.0396 | 1109014.5379
11 | 2698048.3541 | 1109030.3004 | 2698048.3733 | 1109030.3315 | 2698048.9686 | 1109031.7642 | 2698049.1981 | 1109033.3467 | 2698050.433 | 1109048.0376
12 | 2698042.8288 | 1109014.1348 | 2698041.6896 | 1109011.9564 | 2698036.7286 | 1109004.1825 | 2698034.3298 | 1109000.9751 | 2698033.6325 | 1109000.3615
13 | 2698094.6682 | 1108802.9552 | 2698094.4759 | 1108802.0897 | 2698094.1262 | 1108792.6449 | 2698093.7634 | 1108791.2495
14 | 2698094.6682 | 1108802.9552 | 2698095.1621 | 1108805.1776
15 | 2698086.464 | 1108776.4442 | 2698092.5614 | 1108786.6269 | 2698093.7634 | 1108791.2495
16 | 2698096.8612 | 1108812.8239 | 2698095.1621 | 1108805.1776
17 | 2698086.464 | 1108776.4442 | 2698088.4182 | 1108771.7729
18 | 2698132.7212 | 1108793.9475 | 2698131.0779 | 1108799.9469 | 2698126.9754 | 1108805.5174 | 2698121.2453 | 1108810.8614 | 2698115.5944 | 1108811.3147 | 2698104.323 | 1108809.8649 | 2698096.8612 | 1108812.8239
19 | 2698096.8612 | 1108812.8239 | 2698097.3653 | 1108816.0674
20 | 2698088.4182 | 1108771.7729 | 2698077.0768 | 1108775.6031 | 2698075.4192 | 1108774.3644 | 2698072.3513 | 1108776.3844
21 | 2698132.7212 | 1108793.9475 | 2698153.7141 | 1108815.1591
22 | 2698100.5408 | 1108820.3402 | 2698097.3653 | 1108816.0674
23 | 2698023.8294 | 1108778.7334 | 2698041.0553 | 1108797.3011 | 2698043.6546 | 1108795.5313
24 | 2698023.8294 | 1108778.7334 | 2698019.2322 | 1108787.6536 | 2698014.88 | 1108793.653
25 | 2698045.5962 | 1108794.2093 | 2698043.6546 | 1108795.5313
26 | 2698007.5692 | 1108803.7308 | 2698014.88 | 1108793.653
27 | 2698058.2402 | 1108785.6758 | 2698072.3513 | 1108776.3844
28 | 2698153.7141 | 1108815.1591 | 2698165.1412 | 1108826.7052
29 | 2698100.5408 | 1108820.3402 | 2698100.6609 | 1108820.5019
30 | 2698104.1578 | 1108825.2072 | 2698100.6609 | 1108820.5019
31 | 2698119.9028 | 1108847.3917 | 2698119.4826 | 1108846.6997 | 2698108.7979 | 1108831.4508 | 2698104.1578 | 1108825.2072
32 | 2698127.6097 | 1108860.0821 | 2698119.9028 | 1108847.3917
33 | 2698145.2804 | 1108892.6087 | 2698140.5448 | 1108881.8401 | 2698137.0279 | 1108875.5904 | 2698127.6097 | 1108860.0821
34 | 2698179.3362 | 1108966.4649 | 2698182.8947 | 1108963.9321 | 2698184.2794 | 1108959.5851 | 2698184.185 | 1108957.2932 | 2698182.4501 | 1108955.1082 | 2698178.3568 | 1108951.5175 | 2698162.9776 | 1108938.316 | 2698149.9995 | 1108903.3398 | 2698145.2804 | 1108892.6087
35 | 2698179.3362 | 1108966.4649 | 2698127.5957 | 1108923.8791 | 2698105.052 | 1108900.5111 | 2698104.2962 | 1108900.061
36 | 2698022.6825 | 1108994.3528 | 2698023.9602 | 1108994.4479 | 2698028.0014 | 1108996.0031 | 2698030.9836 | 1108998.0303 | 2698033.6325 | 1109000.3615
37 | 2698074.3488 | 1108945.2212 | 2698079.2979 | 1108948.0021 | 2698087.3539 | 1108950.356
38 | 2698074.4167 | 1108919.7752 | 2698091.6168 | 1108939.6405 | 2698092.9727 | 1108944.71 | 2698091.194 | 1108948.0945 | 2698087.3539 | 1108950.356 | 2698087.3539 | 1108950.356
39 | 2698074.3488 | 1108945.2212 | 2698064.7111 | 1108939.8057 | 2698062.3299 | 1108938.8822
40 | 2698074.4167 | 1108919.7752 | 2698064.3874 | 1108908.1918 | 2698047.9994 | 1108890.6327
41 | 2698062.3299 | 1108938.8822 | 2698052.3268 | 1108935.0025 | 2698039.5129 | 1108931.4266 | 2698027.4968 | 1108930.6254
42 | 2698025.7853 | 1108860.038 | 2698017.955 | 1108856.1424 | 2698009.809 | 1108855.5215 | 2698006.3683 | 1108860.3356 | 2698010.7617 | 1108864.9761 | 2698037.3953 | 1108879.2709 | 2698047.9994 | 1108890.6327
43 | 2698005.2263 | 1108934.8192 | 2698021.2416 | 1108930.2084 | 2698027.4968 | 1108930.6254
44 | 2698025.7853 | 1108860.038 | 2698030.0187 | 1108862.141 | 2698058.9313 | 1108876.5283 | 2698068.835 | 1108880.5404
45 | 2698025.7853 | 1108860.038 | 2698026.6744 | 1108850.9467 | 2698032.3193 | 1108851.3381 | 2698036.6158 | 1108850.4959 | 2698038.6246 | 1108847.7324
46 | 2698005.2263 | 1108934.8192 | 2698003.1501 | 1108930.7831 | 2698003.7327 | 1108927.257 | 2698011.5094 | 1108921.0677 | 2698011.8507 | 1108917.6488
47 | 2698005.2263 | 1108934.8192 | 2698004.6739 | 1108936.9449 | 2698002.6817 | 1108941.1042 | 2697989.6007 | 1108968.41 | 2697988.0451 | 1108969.4744
48 | 2698068.835 | 1108880.5404 | 2698073.1971 | 1108882.3075
49 | 2698038.6246 | 1108847.7324 | 2698042.0873 | 1108842.9685 | 2698042.7809 | 1108842.5496
50 | 2698022.6825 | 1108994.3528 | 2698019.9528 | 1108994.1497 | 2698016.3876 | 1108994.2366 | 2698013.9434 | 1108994.7974 | 2698011.4803 | 1108995.5692 | 2698009.8858 | 1108996.6442 | 2698000.626 | 1109005.0301
51 | 2697929.9902 | 1108949.2023 | 2697933.9764 | 1108950.334 | 2697939.7651 | 1108952.3509 | 2697942.1502 | 1108953.5346 | 2697971.8749 | 1108968.3682 | 2697977.7316 | 1108970.4752 | 2697981.4099 | 1108971.046
52 | 2698008.7169 | 1108913.7952 | 2698010.6323 | 1108914.1158 | 2698011.8507 | 1108917.6488
53 | 2697988.0451 | 1108969.4744 | 2697985.6925 | 1108970.5816 | 2697983.5192 | 1108971.1246 | 2697981.4099 | 1108971.046
54 | 2698104.2962 | 1108900.061 | 2698077.2263 | 1108883.9398 | 2698073.1971 | 1108882.3075
55 | 2698059.4447 | 1108837.6123 | 2698052.623 | 1108834.4557 | 2698049.9569 | 1108838.2149 | 2698042.7809 | 1108842.5496
56 | 2698045.5962 | 1108794.2093 | 2698052.2865 | 1108789.6539
57 | 2698186.239 | 1108849.0787 | 2698170.7309 | 1108832.3531 | 2698165.1412 | 1108826.7052
58 | 2698052.2865 | 1108789.6539 | 2698054.868 | 1108787.8962 | 2698055.9593 | 1108787.1776
59 | 2698058.2402 | 1108785.6758 | 2698057.8021 | 1108785.9642
60 | 2698057.8021 | 1108785.9642 | 2698055.9593 | 1108787.1776

## bus_geodata
| x | y | coords
0 | 2697955.1973 | 1109085.7341
1 | 2697957.0377 | 1109086.2423
2 | 2697978.1401 | 1109092.0687
3 | 2698049.5549 | 1109133.5556
4 | 2697999.065 | 1109068.987
5 | 2697965.2622 | 1109012.5667
6 | 2697966.2315 | 1108995.6385
7 | 2698045.9418 | 1109027.2347
8 | 2698043.0396 | 1109014.5379
9 | 2698048.3541 | 1109030.3004
10 | 2698042.8288 | 1109014.1348
11 | 2698050.433 | 1109048.0376
12 | 2698094.6682 | 1108802.9552
13 | 2698093.7634 | 1108791.2495
14 | 2698095.1621 | 1108805.1776
15 | 2698086.464 | 1108776.4442
16 | 2698096.8612 | 1108812.8239
17 | 2698088.4182 | 1108771.7729
18 | 2698132.7212 | 1108793.9475
19 | 2698097.3653 | 1108816.0674
20 | 2698023.8294 | 1108778.7334
21 | 2698043.6546 | 1108795.5313
22 | 2698014.88 | 1108793.653
23 | 2698072.3513 | 1108776.3844
24 | 2698153.7141 | 1108815.1591
25 | 2698100.5408 | 1108820.3402
26 | 2698104.1578 | 1108825.2072
27 | 2698100.6609 | 1108820.5019
28 | 2698119.9028 | 1108847.3917
29 | 2698127.6097 | 1108860.0821
30 | 2698145.2804 | 1108892.6087
31 | 2698179.3362 | 1108966.4649
32 | 2698033.6325 | 1109000.3615
33 | 2698087.3539 | 1108950.356
34 | 2698074.3488 | 1108945.2212
35 | 2698074.4167 | 1108919.7752
36 | 2698062.3299 | 1108938.8822
37 | 2698047.9994 | 1108890.6327
38 | 2698027.4968 | 1108930.6254
39 | 2698025.7853 | 1108860.038
40 | 2698005.2263 | 1108934.8192
41 | 2698068.835 | 1108880.5404
42 | 2698038.6246 | 1108847.7324
43 | 2698022.6825 | 1108994.3528
44 | 2698000.626 | 1109005.0301
45 | 2697929.9902 | 1108949.2022
46 | 2698011.8507 | 1108917.6488
47 | 2697988.0451 | 1108969.4744
48 | 2697981.4099 | 1108971.046
49 | 2698104.2962 | 1108900.061
50 | 2698073.1971 | 1108882.3075
51 | 2698042.7809 | 1108842.5496
52 | 2698059.4447 | 1108837.6123
53 | 2698007.5692 | 1108803.7308
54 | 2698008.7169 | 1108913.7952
55 | 2698045.5962 | 1108794.2093
56 | 2698186.239 | 1108849.0787
57 | 2698165.1412 | 1108826.7052
58 | 2698052.2865 | 1108789.6539
59 | 2698058.2402 | 1108785.6758
60 | 2698055.9593 | 1108787.1776
61 | 2698057.8021 | 1108785.9642
62 | 2698025.7853 | 1108860.038

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1