## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5399-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5399-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5399-7_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5399-7_0_3_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_5399-7_0_3_node_10 | 0.4 | n |  | TRUE
5 | bus_LV_5399-7_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_5399-7_0_3_node_56 | 0.4 | n |  | TRUE
7 | bus_LV_5399-7_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_5399-7_0_3_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_5399-7_0_3_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_5399-7_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_5399-7_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_5399-7_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_5399-7_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5399-7_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_5399-7_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_5399-7_0_3_node_57 | 0.4 | n |  | TRUE
17 | bus_LV_5399-7_0_3_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_5399-7_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_5399-7_0_3_node_60 | 0.4 | n |  | TRUE
20 | bus_LV_5399-7_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_5399-7_0_3_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_5399-7_0_3_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_5399-7_0_3_node_59 | 0.4 | n |  | TRUE
24 | bus_LV_5399-7_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_5399-7_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_5399-7_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_5399-7_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_5399-7_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_5399-7_0_3_node_155 | 0.4 | n |  | TRUE
30 | bus_LV_5399-7_0_3_node_153 | 0.4 | n |  | TRUE
31 | bus_LV_5399-7_0_3_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_5399-7_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_5399-7_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_5399-7_0_3_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_5399-7_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_5399-7_0_3_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_5399-7_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_5399-7_0_3_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_5399-7_0_3_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_5399-7_0_3_node_147 | 0.4 | n |  | TRUE
41 | bus_LV_5399-7_0_3_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_5399-7_0_3_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_5399-7_0_3_node_157 | 0.4 | n |  | TRUE
44 | bus_LV_5399-7_0_3_node_154 | 0.4 | n |  | TRUE
45 | bus_LV_5399-7_0_3_node_156 | 0.4 | n |  | TRUE
46 | bus_LV_5399-7_0_3_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_5399-7_0_3_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_5399-7_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_5399-7_0_3_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_5399-7_0_3_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_5399-7_0_3_node_187 | 0.4 | n |  | TRUE
52 | bus_LV_5399-7_0_3_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_5399-7_0_3_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_5399-7_0_3_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_5399-7_0_3_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_5399-7_0_3_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_5399-7_0_3_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_5399-7_0_3_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_5399-7_0_3_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_5399-7_0_3_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_5399-7_0_3_node_159 | 0.4 | n |  | TRUE
62 | bus_LV_5399-7_0_3_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_5399-7_0_3_node_158 | 0.4 | n |  | TRUE
64 | bus_LV_5399-7_0_3_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_5399-7_0_3_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_5399-7_0_3_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_5399-7_0_3_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_5399-7_0_3_node_192 | 0.4 | n |  | TRUE
69 | bus_LV_5399-7_0_3_node_144 | 0.4 | n |  | TRUE
70 | bus_LV_5399-7_0_3_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_5399-7_0_3_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_5399-7_0_3_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_5399-7_0_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_5399-7_0_3_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_5399-7_0_3_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_5399-7_0_3_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_5399-7_0_3_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_5399-7_0_3_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_5399-7_0_3_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_5399-7_0_3_node_82 | 0.4 | n |  | TRUE
81 | bus_LV_5399-7_0_3_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_5399-7_0_3_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_5399-7_0_3_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_5399-7_0_3_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_5399-7_0_3_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_5399-7_0_3_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_5399-7_0_3_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_5399-7_0_3_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_5399-7_0_3_node_121 | 0.4 | n |  | TRUE
90 | bus_LV_5399-7_0_3_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_5399-7_0_3_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_5399-7_0_3_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_5399-7_0_3_node_120 | 0.4 | n |  | TRUE
94 | bus_LV_5399-7_0_3_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_5399-7_0_3_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_5399-7_0_3_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_5399-7_0_3_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_5399-7_0_3_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_5399-7_0_3_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_5399-7_0_3_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_5399-7_0_3_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_5399-7_0_3_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_5399-7_0_3_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_5399-7_0_3_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_5399-7_0_3_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_5399-7_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_5399-7_0_3_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_5399-7_0_3_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_5399-7_0_3_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_5399-7_0_3_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_5399-7_0_3_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_5399-7_0_3_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_5399-7_0_3_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_5399-7_0_3_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_5399-7_0_3_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_5399-7_0_3_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_5399-7_0_3_node_119 | 0.4 | n |  | TRUE
118 | bus_LV_5399-7_0_3_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_5399-7_0_3_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_5399-7_0_3_node_107 | 0.4 | n |  | TRUE
121 | bus_LV_5399-7_0_3_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_5399-7_0_3_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_5399-7_0_3_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_5399-7_0_3_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_5399-7_0_3_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_5399-7_0_3_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_5399-7_0_3_node_122 | 0.4 | n |  | TRUE
128 | bus_LV_5399-7_0_3_node_132 | 0.4 | n |  | TRUE
129 | bus_LV_5399-7_0_3_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_5399-7_0_3_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_5399-7_0_3_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_5399-7_0_3_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_5399-7_0_3_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_5399-7_0_3_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_5399-7_0_3_node_145 | 0.4 | n |  | TRUE
136 | bus_LV_5399-7_0_3_node_143 | 0.4 | n |  | TRUE
137 | bus_LV_5399-7_0_3_node_124 | 0.4 | n |  | TRUE
138 | bus_LV_5399-7_0_3_node_125 | 0.4 | n |  | TRUE
139 | bus_LV_5399-7_0_3_node_126 | 0.4 | n |  | TRUE
140 | bus_LV_5399-7_0_3_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_5399-7_0_3_node_128 | 0.4 | n |  | TRUE
142 | bus_LV_5399-7_0_3_node_189 | 0.4 | n |  | TRUE
143 | bus_LV_5399-7_0_3_node_135 | 0.4 | n |  | TRUE
144 | bus_LV_5399-7_0_3_node_133 | 0.4 | n |  | TRUE
145 | bus_LV_5399-7_0_3_node_136 | 0.4 | n |  | TRUE
146 | bus_LV_5399-7_0_3_node_134 | 0.4 | n |  | TRUE
147 | bus_LV_5399-7_0_3_node_139 | 0.4 | n |  | TRUE
148 | bus_LV_5399-7_0_3_node_137 | 0.4 | n |  | TRUE
149 | bus_LV_5399-7_0_3_node_140 | 0.4 | n |  | TRUE
150 | bus_LV_5399-7_0_3_node_138 | 0.4 | n |  | TRUE
151 | bus_LV_5399-7_0_3_node_141 | 0.4 | n |  | TRUE
152 | bus_LV_5399-7_0_3_node_142 | 0.4 | n |  | TRUE
153 | bus_LV_5399-7_0_3_node_186 | 0.4 | n |  | TRUE
154 | bus_MV_77_0_node_48 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5399-7_0_3_load_0 | 0 | 0.013226 | 0.0033147 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5399-7_0_3_load_1 | 1 | 0.0021936 | 0.00054976 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5399-7_0_3_load_3 | 2 | 0.0020051 | 0.00050252 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5399-7_0_3_load_7 | 5 | 0.0084361 | 0.0021143 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5399-7_0_3_load_54 | 8 | 0.0048256 | 0.0012094 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5399-7_0_3_load_58 | 9 | 0.0017578 | 0.00044054 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5399-7_0_3_load_13 | 10 | 0.0019834 | 0.00049709 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5399-7_0_3_load_8 | 11 | 0.0048863 | 0.0012246 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5399-7_0_3_load_9 | 12 | 0.0015103 | 0.00037851 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5399-7_0_3_load_11 | 13 | 0.0031532 | 0.00079027 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5399-7_0_3_load_14 | 14 | 0.0017977 | 0.00045055 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5399-7_0_3_load_57 | 16 | 0.0083833 | 0.002101 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5399-7_0_3_load_55 | 17 | 0.0039718 | 0.00099543 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5399-7_0_3_load_15 | 18 | 0.00259 | 0.00064911 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5399-7_0_3_load_60 | 19 | 0.0037203 | 0.00093241 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5399-7_0_3_load_16 | 20 | 0.0020566 | 0.00051543 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5399-7_0_3_load_62 | 22 | 0.0061412 | 0.0015391 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5399-7_0_3_load_59 | 23 | 0.0044415 | 0.0011132 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5399-7_0_3_load_17 | 24 | 0.00042946 | 0.00010763 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5399-7_0_3_load_25 | 27 | 0.00040688 | 0.00010197 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5399-7_0_3_load_153 | 30 | 0.00054274 | 0.00013602 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5399-7_0_3_load_31 | 32 | 0.00036261 | 9.0879e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5399-7_0_3_load_30 | 33 | 0.00049011 | 0.00012283 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5399-7_0_3_load_29 | 35 | 0.00038459 | 9.6387e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5399-7_0_3_load_34 | 37 | 0.00044702 | 0.00011203 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5399-7_0_3_load_33 | 39 | 0.00063218 | 0.00015844 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5399-7_0_3_load_147 | 40 | 0.0020284 | 0.00050837 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5399-7_0_3_load_28 | 41 | 0.00079072 | 0.00019817 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5399-7_0_3_load_157 | 43 | 0.00049393 | 0.00012379 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5399-7_0_3_load_156 | 45 | 0.00042022 | 0.00010532 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5399-7_0_3_load_32 | 46 | 0.00053535 | 0.00013417 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5399-7_0_3_load_27 | 47 | 0.00084632 | 0.00021211 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5399-7_0_3_load_36 | 48 | 0.00051012 | 0.00012785 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5399-7_0_3_load_47 | 49 | 0.0003602 | 9.0276e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5399-7_0_3_load_45 | 50 | 0.00049551 | 0.00012419 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5399-7_0_3_load_187 | 51 | 0.00037124 | 9.3041e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5399-7_0_3_load_37 | 52 | 0.00069982 | 0.00017539 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5399-7_0_3_load_48 | 53 | 0.00070359 | 0.00017634 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5399-7_0_3_load_43 | 54 | 0.00045575 | 0.00011422 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5399-7_0_3_load_39 | 56 | 0.00037478 | 9.3928e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5399-7_0_3_load_40 | 57 | 0.0003413 | 8.5538e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5399-7_0_3_load_41 | 58 | 0.00050687 | 0.00012703 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5399-7_0_3_load_46 | 60 | 0.00082801 | 0.00020752 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5399-7_0_3_load_44 | 62 | 0.00042032 | 0.00010534 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5399-7_0_3_load_158 | 63 | 0.00034756 | 8.7107e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5399-7_0_3_load_49 | 64 | 0.00040721 | 0.00010206 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5399-7_0_3_load_50 | 65 | 0.000579 | 0.00014511 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5399-7_0_3_load_51 | 66 | 0.00037893 | 9.4968e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5399-7_0_3_load_52 | 67 | 0.00072416 | 0.00018149 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5399-7_0_3_load_192 | 68 | 0.0083343 | 0.0020888 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5399-7_0_3_load_63 | 70 | 0.0057055 | 0.0014299 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5399-7_0_3_load_70 | 71 | 0.0024864 | 0.00062316 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5399-7_0_3_load_71 | 72 | 0.0016135 | 0.00040438 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5399-7_0_3_load_64 | 73 | 0.0015947 | 0.00039967 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5399-7_0_3_load_65 | 74 | 0.0031124 | 0.00078005 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5399-7_0_3_load_66 | 75 | 0.0025339 | 0.00063506 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5399-7_0_3_load_67 | 76 | 0.0016304 | 0.00040862 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5399-7_0_3_load_68 | 77 | 0.0026955 | 0.00067557 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5399-7_0_3_load_69 | 78 | 0.001864 | 0.00046716 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5399-7_0_3_load_81 | 79 | 0.0015864 | 0.00039759 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5399-7_0_3_load_72 | 81 | 0.002844 | 0.00071277 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5399-7_0_3_load_73 | 82 | 0.0018612 | 0.00046645 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5399-7_0_3_load_75 | 84 | 0.0035871 | 0.000899 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5399-7_0_3_load_76 | 85 | 0.0029054 | 0.00072816 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5399-7_0_3_load_77 | 86 | 0.0020958 | 0.00052526 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5399-7_0_3_load_78 | 87 | 0.0024186 | 0.00060616 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5399-7_0_3_load_79 | 88 | 0.0030667 | 0.00076858 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5399-7_0_3_load_83 | 90 | 0.0016304 | 0.00040861 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5399-7_0_3_load_80 | 91 | 0.0022222 | 0.00055693 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5399-7_0_3_load_84 | 92 | 0.0017163 | 0.00043015 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5399-7_0_3_load_120 | 93 | 0.001515 | 0.00037969 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5399-7_0_3_load_88 | 95 | 0.0027393 | 0.00068653 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5399-7_0_3_load_89 | 96 | 0.0024489 | 0.00061376 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5399-7_0_3_load_86 | 97 | 0.0016125 | 0.00040414 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5399-7_0_3_load_87 | 98 | 0.0020059 | 0.00050273 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5399-7_0_3_load_97 | 99 | 0.0015242 | 0.00038201 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5399-7_0_3_load_96 | 100 | 0.003307 | 0.00082881 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5399-7_0_3_load_93 | 101 | 0.0015595 | 0.00039085 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5399-7_0_3_load_91 | 102 | 0.0014502 | 0.00036346 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5399-7_0_3_load_98 | 103 | 0.0025991 | 0.00065139 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5399-7_0_3_load_95 | 104 | 0.0019286 | 0.00048334 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5399-7_0_3_load_90 | 105 | 0.0023433 | 0.00058729 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5399-7_0_3_load_92 | 106 | 0.0015555 | 0.00038984 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5399-7_0_3_load_94 | 107 | 0.0023722 | 0.00059454 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5399-7_0_3_load_99 | 108 | 0.0029797 | 0.00074679 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5399-7_0_3_load_100 | 109 | 0.0025661 | 0.00064311 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5399-7_0_3_load_101 | 110 | 0.0020848 | 0.0005225 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5399-7_0_3_load_112 | 113 | 0.00034385 | 8.6177e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5399-7_0_3_load_106 | 114 | 0.00063906 | 0.00016016 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5399-7_0_3_load_119 | 117 | 0.00047986 | 0.00012026 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5399-7_0_3_load_104 | 118 | 0.0014099 | 0.00035336 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5399-7_0_3_load_105 | 119 | 0.00070164 | 0.00017585 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5399-7_0_3_load_108 | 121 | 0.0010266 | 0.0002573 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5399-7_0_3_load_109 | 122 | 0.00034262 | 8.5868e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5399-7_0_3_load_110 | 123 | 0.00056204 | 0.00014086 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5399-7_0_3_load_114 | 125 | 0.00047187 | 0.00011826 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5399-7_0_3_load_115 | 126 | 0.00051048 | 0.00012794 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5399-7_0_3_load_122 | 127 | 0.00034856 | 8.7356e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5399-7_0_3_load_116 | 129 | 0.00057692 | 0.00014459 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5399-7_0_3_load_123 | 131 | 0.0004476 | 0.00011218 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5399-7_0_3_load_131 | 134 | 0.00055118 | 0.00013814 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5399-7_0_3_load_143 | 136 | 0.0020659 | 0.00051776 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5399-7_0_3_load_124 | 137 | 0.00044798 | 0.00011228 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5399-7_0_3_load_125 | 138 | 0.00036856 | 9.237e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5399-7_0_3_load_126 | 139 | 0.00058461 | 0.00014652 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5399-7_0_3_load_127 | 140 | 0.00038604 | 9.675e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5399-7_0_3_load_128 | 141 | 0.00030731 | 7.702e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5399-7_0_3_load_189 | 142 | 0.0005536 | 0.00013874 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5399-7_0_3_load_135 | 143 | 0.00083884 | 0.00021023 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5399-7_0_3_load_136 | 145 | 0.0015514 | 0.00038882 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5399-7_0_3_load_139 | 147 | 0.00042963 | 0.00010767 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5399-7_0_3_load_140 | 149 | 0.00054947 | 0.00013771 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5399-7_0_3_load_138 | 150 | 0.00036776 | 9.217e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5399-7_0_3_load_142 | 152 | 0.00035053 | 8.785e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5399-7_0_3_load_186 | 153 | 0.00065698 | 0.00016465 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 81 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5399-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5399-7_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0025824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5399-7_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.016241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5399-7_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.014076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5399-7_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5399-7_0_3_line_5 | NAYY 4x150 SE | 4 | 10 | 0.02459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5399-7_0_3_line_6 | NAYY 4x150 SE | 5 | 11 | 0.039307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5399-7_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.39155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_5399-7_0_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.053734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_5399-7_0_3_line_9 | NAYY 4x150 SE | 7 | 40 | 0.066588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5399-7_0_3_line_10 | NAYY 4x150 SE | 7 | 36 | 0.22186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5399-7_0_3_line_11 | NAYY 4x150 SE | 8 | 68 | 0.12198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_5399-7_0_3_line_12 | NAYY 4x150 SE | 8 | 17 | 0.02018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_5399-7_0_3_line_13 | NAYY 4x150 SE | 9 | 10 | 0.00078291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5399-7_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.0078272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5399-7_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.010003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5399-7_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.012687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5399-7_0_3_line_17 | NAYY 4x150 SE | 14 | 18 | 0.006588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5399-7_0_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.020663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_5399-7_0_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.026726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_5399-7_0_3_line_20 | NAYY 4x150 SE | 16 | 19 | 0.020981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_5399-7_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.010321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5399-7_0_3_line_22 | NAYY 4x150 SE | 19 | 23 | 0.0084414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_5399-7_0_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.012583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5399-7_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.010313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_5399-7_0_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.034819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_5399-7_0_3_line_26 | NAYY 4x150 SE | 22 | 70 | 0.0075516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_5399-7_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.0064226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5399-7_0_3_line_28 | NAYY 4x150 SE | 25 | 26 | 0.0151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5399-7_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.018106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5399-7_0_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.087111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5399-7_0_3_line_31 | NAYY 4x150 SE | 27 | 41 | 0.01104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5399-7_0_3_line_32 | NAYY 4x150 SE | 28 | 29 | 0.11539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5399-7_0_3_line_33 | NAYY 4x150 SE | 28 | 30 | 0.057209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5399-7_0_3_line_34 | NAYY 4x150 SE | 29 | 45 | 0.098591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5399-7_0_3_line_35 | NAYY 4x150 SE | 30 | 44 | 0.064032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5399-7_0_3_line_36 | NAYY 4x150 SE | 31 | 32 | 0.0084235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5399-7_0_3_line_37 | NAYY 4x150 SE | 31 | 33 | 0.0037917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5399-7_0_3_line_38 | NAYY 4x150 SE | 32 | 46 | 0.025954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5399-7_0_3_line_39 | NAYY 4x150 SE | 33 | 34 | 0.031056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5399-7_0_3_line_40 | NAYY 4x150 SE | 34 | 35 | 0.0016686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5399-7_0_3_line_41 | NAYY 4x150 SE | 35 | 47 | 0.010674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5399-7_0_3_line_42 | NAYY 4x150 SE | 36 | 37 | 0.032458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5399-7_0_3_line_43 | NAYY 4x150 SE | 36 | 38 | 0.1042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5399-7_0_3_line_44 | NAYY 4x150 SE | 36 | 39 | 0.050979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5399-7_0_3_line_45 | NAYY 4x150 SE | 37 | 48 | 0.0036998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5399-7_0_3_line_46 | NAYY 4x150 SE | 38 | 49 | 0.039604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5399-7_0_3_line_47 | NAYY 4x150 SE | 38 | 50 | 0.010971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5399-7_0_3_line_48 | NAYY 4x150 SE | 39 | 46 | 0.025798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5399-7_0_3_line_49 | NAYY 4x150 SE | 41 | 47 | 0.012698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5399-7_0_3_line_50 | NAYY 4x150 SE | 42 | 43 | 0.25685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5399-7_0_3_line_51 | NAYY 4x150 SE | 42 | 44 | 0.057683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5399-7_0_3_line_52 | NAYY 4x150 SE | 43 | 51 | 0.079375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5399-7_0_3_line_53 | NAYY 4x150 SE | 48 | 52 | 0.036241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5399-7_0_3_line_54 | NAYY 4x150 SE | 49 | 53 | 0.082624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5399-7_0_3_line_55 | NAYY 4x150 SE | 50 | 54 | 0.0076322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5399-7_0_3_line_56 | NAYY 4x150 SE | 51 | 153 | 0.041259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5399-7_0_3_line_57 | NAYY 4x150 SE | 53 | 64 | 0.063327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5399-7_0_3_line_58 | NAYY 4x150 SE | 54 | 62 | 0.023912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5399-7_0_3_line_59 | NAYY 4x150 SE | 55 | 56 | 0.16045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5399-7_0_3_line_60 | NAYY 4x150 SE | 55 | 57 | 0.010617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5399-7_0_3_line_61 | NAYY 4x150 SE | 56 | 58 | 0.023039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5399-7_0_3_line_62 | NAYY 4x150 SE | 57 | 59 | 0.016632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5399-7_0_3_line_63 | NAYY 4x150 SE | 58 | 60 | 0.0041619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5399-7_0_3_line_64 | NAYY 4x150 SE | 59 | 61 | 0.17238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5399-7_0_3_line_65 | NAYY 4x150 SE | 60 | 62 | 0.012499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5399-7_0_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.28536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5399-7_0_3_line_67 | NAYY 4x150 SE | 64 | 65 | 0.0093683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5399-7_0_3_line_68 | NAYY 4x150 SE | 65 | 66 | 0.013966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5399-7_0_3_line_69 | NAYY 4x150 SE | 66 | 67 | 0.020348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5399-7_0_3_line_70 | NAYY 4x150 SE | 68 | 69 | 0.01181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_5399-7_0_3_line_71 | NAYY 4x150 SE | 69 | 89 | 0.10417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
72 | LV_5399-7_0_3_line_72 | NAYY 4x150 SE | 70 | 71 | 0.015055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
73 | LV_5399-7_0_3_line_73 | NAYY 4x150 SE | 71 | 72 | 0.010501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
74 | LV_5399-7_0_3_line_74 | NAYY 4x150 SE | 72 | 81 | 0.010013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
75 | LV_5399-7_0_3_line_75 | NAYY 4x150 SE | 73 | 74 | 0.017694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_5399-7_0_3_line_76 | NAYY 4x150 SE | 74 | 75 | 0.023457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_5399-7_0_3_line_77 | NAYY 4x150 SE | 75 | 76 | 0.057621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_5399-7_0_3_line_78 | NAYY 4x150 SE | 76 | 77 | 0.015853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_5399-7_0_3_line_79 | NAYY 4x150 SE | 77 | 78 | 0.018966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_5399-7_0_3_line_80 | NAYY 4x150 SE | 78 | 79 | 0.016475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_5399-7_0_3_line_81 | NAYY 4x150 SE | 79 | 80 | 0.0011791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_5399-7_0_3_line_82 | NAYY 4x150 SE | 80 | 97 | 0.0059942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_5399-7_0_3_line_83 | NAYY 4x150 SE | 80 | 92 | 0.015778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_5399-7_0_3_line_84 | NAYY 4x150 SE | 81 | 82 | 0.014706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_5399-7_0_3_line_85 | NAYY 4x150 SE | 82 | 83 | 0.0011069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_5399-7_0_3_line_86 | NAYY 4x150 SE | 83 | 84 | 0.017692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_5399-7_0_3_line_87 | NAYY 4x150 SE | 83 | 85 | 0.020591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_5399-7_0_3_line_88 | NAYY 4x150 SE | 84 | 86 | 0.018759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_5399-7_0_3_line_89 | NAYY 4x150 SE | 85 | 87 | 0.0092517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_5399-7_0_3_line_90 | NAYY 4x150 SE | 86 | 88 | 0.017382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_5399-7_0_3_line_91 | NAYY 4x150 SE | 87 | 90 | 0.0086899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_5399-7_0_3_line_92 | NAYY 4x150 SE | 88 | 91 | 0.010491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_5399-7_0_3_line_93 | NAYY 4x150 SE | 89 | 93 | 0.13115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_5399-7_0_3_line_94 | NAYY 4x150 SE | 90 | 92 | 0.0055218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_5399-7_0_3_line_95 | NAYY 4x150 SE | 93 | 135 | 0.14605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_5399-7_0_3_line_96 | NAYY 4x150 SE | 94 | 95 | 0.035452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_5399-7_0_3_line_97 | NAYY 4x150 SE | 94 | 96 | 0.0051866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_5399-7_0_3_line_98 | NAYY 4x150 SE | 95 | 99 | 0.002161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_5399-7_0_3_line_99 | NAYY 4x150 SE | 96 | 100 | 0.020664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_5399-7_0_3_line_100 | NAYY 4x150 SE | 97 | 98 | 0.0011753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_5399-7_0_3_line_101 | NAYY 4x150 SE | 98 | 101 | 0.0030245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_5399-7_0_3_line_102 | NAYY 4x150 SE | 99 | 103 | 0.00029832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_5399-7_0_3_line_103 | NAYY 4x150 SE | 100 | 104 | 0.015206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_5399-7_0_3_line_104 | NAYY 4x150 SE | 101 | 102 | 0.0062486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_5399-7_0_3_line_105 | NAYY 4x150 SE | 102 | 105 | 0.00058892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_5399-7_0_3_line_106 | NAYY 4x150 SE | 103 | 108 | 0.024114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_5399-7_0_3_line_107 | NAYY 4x150 SE | 104 | 107 | 0.0021205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_5399-7_0_3_line_108 | NAYY 4x150 SE | 105 | 106 | 0.014446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_5399-7_0_3_line_109 | NAYY 4x150 SE | 106 | 107 | 0.035379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_5399-7_0_3_line_110 | NAYY 4x150 SE | 108 | 109 | 0.016576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_5399-7_0_3_line_111 | NAYY 4x150 SE | 110 | 111 | 0.18117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_5399-7_0_3_line_112 | NAYY 4x150 SE | 111 | 112 | 0.11652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_5399-7_0_3_line_113 | NAYY 4x150 SE | 112 | 113 | 0.055759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_5399-7_0_3_line_114 | NAYY 4x150 SE | 112 | 114 | 0.082643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_5399-7_0_3_line_115 | NAYY 4x150 SE | 114 | 118 | 0.0069175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_5399-7_0_3_line_116 | NAYY 4x150 SE | 115 | 116 | 0.045102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_5399-7_0_3_line_117 | NAYY 4x150 SE | 115 | 117 | 0.002239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_5399-7_0_3_line_118 | NAYY 4x150 SE | 116 | 128 | 0.012148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_5399-7_0_3_line_119 | NAYY 4x150 SE | 116 | 129 | 0.013113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_5399-7_0_3_line_120 | NAYY 4x150 SE | 118 | 119 | 0.010547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_5399-7_0_3_line_121 | NAYY 4x150 SE | 119 | 120 | 0.0068964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_5399-7_0_3_line_122 | NAYY 4x150 SE | 120 | 121 | 0.019284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_5399-7_0_3_line_123 | NAYY 4x150 SE | 120 | 122 | 0.016456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_5399-7_0_3_line_124 | NAYY 4x150 SE | 120 | 123 | 0.02703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_5399-7_0_3_line_125 | NAYY 4x150 SE | 121 | 124 | 0.0025655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_5399-7_0_3_line_126 | NAYY 4x150 SE | 122 | 125 | 0.016089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_5399-7_0_3_line_127 | NAYY 4x150 SE | 124 | 126 | 0.035614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_5399-7_0_3_line_128 | NAYY 4x150 SE | 125 | 127 | 0.0091057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_5399-7_0_3_line_129 | NAYY 4x150 SE | 126 | 130 | 0.091395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
130 | LV_5399-7_0_3_line_130 | NAYY 4x150 SE | 127 | 131 | 0.020344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_5399-7_0_3_line_131 | NAYY 4x150 SE | 128 | 134 | 0.0072674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_5399-7_0_3_line_132 | NAYY 4x150 SE | 130 | 132 | 0.1054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
133 | LV_5399-7_0_3_line_133 | NAYY 4x150 SE | 131 | 137 | 0.025022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_5399-7_0_3_line_134 | NAYY 4x150 SE | 132 | 133 | 0.073189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
135 | LV_5399-7_0_3_line_135 | NAYY 4x150 SE | 132 | 134 | 0.0070299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_5399-7_0_3_line_136 | NAYY 4x150 SE | 133 | 144 | 0.017922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
137 | LV_5399-7_0_3_line_137 | NAYY 4x150 SE | 133 | 143 | 0.012259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_5399-7_0_3_line_138 | NAYY 4x150 SE | 135 | 136 | 0.11578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
139 | LV_5399-7_0_3_line_139 | NAYY 4x150 SE | 136 | 152 | 0.15721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
140 | LV_5399-7_0_3_line_140 | NAYY 4x150 SE | 137 | 138 | 0.010462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_5399-7_0_3_line_141 | NAYY 4x150 SE | 138 | 139 | 0.053606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_5399-7_0_3_line_142 | NAYY 4x150 SE | 140 | 141 | 0.11948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_5399-7_0_3_line_143 | NAYY 4x150 SE | 140 | 142 | 0.4836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_5399-7_0_3_line_144 | NAYY 4x150 SE | 142 | 143 | 0.062984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_5399-7_0_3_line_145 | NAYY 4x150 SE | 144 | 145 | 0.005679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
146 | LV_5399-7_0_3_line_146 | NAYY 4x150 SE | 145 | 148 | 0.055628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
147 | LV_5399-7_0_3_line_147 | NAYY 4x150 SE | 146 | 147 | 0.043722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
148 | LV_5399-7_0_3_line_148 | NAYY 4x150 SE | 146 | 148 | 0.028795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
149 | LV_5399-7_0_3_line_149 | NAYY 4x150 SE | 147 | 149 | 0.011678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
150 | LV_5399-7_0_3_line_150 | NAYY 4x150 SE | 148 | 150 | 0.034218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_5399-7_0_3_line_151 | NAYY 4x150 SE | 149 | 151 | 0.014075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
152 | LV_5399-7_0_3_line_152 | NAYY 4x150 SE | 151 | 152 | 0.028507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5399-7_0_3_trafo_72 | 0.25 MVA 20/0.4 kV | 154 | 81 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2704127.3229 | 1128158.8065 | 2704135.1385 | 1128163.0779 | 2704138.5591 | 1128166.2684
1 | 2704138.5591 | 1128166.2684 | 2704140.4475 | 1128168.0298
2 | 2704153.6007 | 1128177.5383 | 2704141.3807 | 1128168.9002 | 2704140.4475 | 1128168.0298
3 | 2704167.6632 | 1128176.3019 | 2704153.6007 | 1128177.5383
4 | 2704153.6007 | 1128177.5383 | 2704153.2199 | 1128184.8808 | 2704154.5927 | 1128190.9757
5 | 2704167.6632 | 1128176.3019 | 2704172.0301 | 1128159.0217 | 2704172.7838 | 1128153.7425 | 2704172.8441 | 1128152.3096
6 | 2704154.5927 | 1128190.9757 | 2704156.3196 | 1128198.6429 | 2704160.4472 | 1128211.3443 | 2704168.5613 | 1128227.5152
7 | 2704281.9851 | 1128108.1843 | 2704286.159 | 1128097.1938 | 2704287.9103 | 1128088.5963 | 2704300.976 | 1128029.9177 | 2704321.0268 | 1127934.025 | 2704325.63 | 1127912.0126 | 2704326.8897 | 1127906.0083 | 2704331.402 | 1127883.9055 | 2704332.9038 | 1127877.7164 | 2704335.2237 | 1127867.4388 | 2704346.2135 | 1127814.7727 | 2704350.2043 | 1127795.6517 | 2704355.0451 | 1127797.3918 | 2704358.229 | 1127801.8051 | 2704364.0618 | 1127805.4525 | 2704378.2505 | 1127808.1213 | 2704403.2345 | 1127809.5756 | 2704409.247 | 1127809.068 | 2704417.3259 | 1127806.2723
8 | 2704281.9851 | 1128108.1843 | 2704270.1265 | 1128128.6262 | 2704252.8411 | 1128153.2697
9 | 2704417.3259 | 1127806.2723 | 2704421.9056 | 1127800.3699 | 2704434.9695 | 1127779.8157 | 2704445.6885 | 1127759.8326 | 2704448.6622 | 1127748.1174
10 | 2704381.8276 | 1127648.7264 | 2704380.5707 | 1127652.3292 | 2704378.1056 | 1127662.0817 | 2704371.5136 | 1127693.9104 | 2704359.5983 | 1127755.5216 | 2704350.2043 | 1127795.6517 | 2704355.0451 | 1127797.3918 | 2704358.229 | 1127801.8051 | 2704364.0618 | 1127805.4525 | 2704378.2505 | 1127808.1213 | 2704403.2345 | 1127809.5756 | 2704409.247 | 1127809.068 | 2704417.3259 | 1127806.2723
11 | 2704252.8411 | 1128153.2697 | 2704347.2442 | 1128230.5096
12 | 2704252.8411 | 1128153.2697 | 2704241.2529 | 1128169.7907
13 | 2704172.8769 | 1128151.5274 | 2704172.8441 | 1128152.3096
14 | 2704168.5613 | 1128227.5152 | 2704172.0716 | 1128234.511
15 | 2704177.281 | 1128243.0329 | 2704173.4409 | 1128237.24 | 2704172.0716 | 1128234.511
16 | 2704177.281 | 1128243.0329 | 2704178.4583 | 1128244.809 | 2704185.5078 | 1128252.666
17 | 2704185.5078 | 1128252.666 | 2704188.0534 | 1128255.5033 | 2704190.2521 | 1128257.1982
18 | 2704225.9059 | 1128191.6706 | 2704214.9027 | 1128209.1607
19 | 2704225.9059 | 1128191.6706 | 2704241.2529 | 1128169.7907
20 | 2704203.9947 | 1128227.0822 | 2704207.1531 | 1128221.7888 | 2704210.8906 | 1128215.5381 | 2704214.9027 | 1128209.1607
21 | 2704190.2521 | 1128257.1982 | 2704198.426 | 1128263.4996
22 | 2704203.9947 | 1128227.0822 | 2704203.9947 | 1128227.0822 | 2704201.7392 | 1128231.8574 | 2704201.0876 | 1128234.9497
23 | 2704209.5721 | 1128267.426 | 2704205.5834 | 1128268.1355 | 2704199.3093 | 1128264.1805 | 2704198.426 | 1128263.4996
24 | 2704209.5721 | 1128267.426 | 2704214.8914 | 1128274.0219 | 2704215.9708 | 1128275.5109
25 | 2704209.5721 | 1128267.426 | 2704205.094 | 1128261.2116 | 2704201.8491 | 1128253.6398 | 2704200.4124 | 1128245.7878 | 2704200.1613 | 1128239.3461 | 2704201.0876 | 1128234.9497
26 | 2704215.9708 | 1128275.5109 | 2704220.4028 | 1128281.6251
27 | 2704541.1011 | 1127504.9413 | 2704545.4518 | 1127500.2169
28 | 2704541.1011 | 1127504.9413 | 2704529.541 | 1127514.6922
29 | 2704529.541 | 1127514.6922 | 2704517.6758 | 1127524.7046 | 2704515.697 | 1127526.3609
30 | 2704529.541 | 1127514.6922 | 2704533.3517 | 1127518.516 | 2704533.693 | 1127522.4022 | 2704541.5502 | 1127528.4418 | 2704580.0573 | 1127558.6599 | 2704583.7312 | 1127563.7044 | 2704583.1291 | 1127567.3186 | 2704583.8672 | 1127576.337
31 | 2704507.2309 | 1127533.447 | 2704515.697 | 1127526.3609
32 | 2704601.0088 | 1127687.2038 | 2704597.1881 | 1127678.6212 | 2704601.9042 | 1127641.2457 | 2704590.6574 | 1127620.8716 | 2704583.8672 | 1127576.337
33 | 2704583.8672 | 1127576.337 | 2704591.3064 | 1127588.2621 | 2704597.0747 | 1127588.0729 | 2704599.3825 | 1127580.3078 | 2704618.2069 | 1127572.106 | 2704615.2129 | 1127580.3261
34 | 2704601.0088 | 1127687.2038 | 2704600.8131 | 1127696.7287 | 2704575.0907 | 1127737.0429 | 2704560.3928 | 1127759.3474 | 2704552.8759 | 1127771.783
35 | 2704676.2281 | 1127598.76 | 2704659.0609 | 1127595.383 | 2704646.8666 | 1127590.1243 | 2704628.8149 | 1127583.0742 | 2704615.2129 | 1127580.3261
36 | 2704461.2382 | 1127571.804 | 2704454.7389 | 1127577.1626
37 | 2704461.2382 | 1127571.804 | 2704464.1636 | 1127569.3918
38 | 2704454.7389 | 1127577.1626 | 2704439.4711 | 1127589.7506 | 2704434.7428 | 1127593.7085
39 | 2704488.0284 | 1127549.5193 | 2704484.2747 | 1127552.6564 | 2704472.5831 | 1127562.4496 | 2704464.1636 | 1127569.3918
40 | 2704488.0284 | 1127549.5193 | 2704489.308 | 1127548.4483
41 | 2704489.308 | 1127548.4483 | 2704497.4932 | 1127541.5973
42 | 2704381.8276 | 1127648.7264 | 2704380.6002 | 1127643.4796 | 2704387.0642 | 1127630.2272 | 2704388.0037 | 1127622.6831 | 2704383.4394 | 1127621.4696
43 | 2704381.8276 | 1127648.7264 | 2704380.5707 | 1127652.3292 | 2704374.9814 | 1127651.5322 | 2704369.2816 | 1127652.6679 | 2704359.1705 | 1127657.541 | 2704344.4335 | 1127666.9705 | 2704324.6183 | 1127677.2464 | 2704311.973 | 1127685.1666 | 2704295.4102 | 1127698.5784 | 2704294.4925 | 1127699.9523
44 | 2704381.8276 | 1127648.7264 | 2704388.5043 | 1127638.3239 | 2704397.6421 | 1127627.3413 | 2704412.5457 | 1127612.289 | 2704414.9604 | 1127610.2677
45 | 2704383.4394 | 1127621.4696 | 2704379.8638 | 1127620.519
46 | 2704294.4925 | 1127699.9523 | 2704280.7684 | 1127720.3731 | 2704270.8064 | 1127731.5871
47 | 2704294.4925 | 1127699.9523 | 2704291.0337 | 1127696.2793 | 2704288.1315 | 1127691.1134
48 | 2704414.9604 | 1127610.2677 | 2704434.7428 | 1127593.7085
49 | 2704507.2309 | 1127533.447 | 2704497.4932 | 1127541.5973
50 | 2704704.5217 | 1127548.4622 | 2704810.153 | 1127497.1924 | 2704876.7734 | 1127374.7026 | 2704876.7734 | 1127374.7026
51 | 2704704.5217 | 1127548.4622 | 2704676.2281 | 1127598.76
52 | 2704936.6558 | 1127322.6013 | 2704876.7734 | 1127374.7026
53 | 2704354.798 | 1127608.579 | 2704354.798 | 1127608.579 | 2704357.1377 | 1127610.9986 | 2704359.6341 | 1127616.4007 | 2704364.7297 | 1127621.2472 | 2704371.0152 | 1127625.9142 | 2704374.5807 | 1127626.9764 | 2704379.8638 | 1127620.519 | 2704379.8638 | 1127620.519
54 | 2704194.032 | 1127758.6706 | 2704198.8865 | 1127757.5967 | 2704243.9685 | 1127744.8765 | 2704257.6804 | 1127740.788 | 2704265.1748 | 1127737.9265 | 2704270.8064 | 1127731.5871
55 | 2704285.9772 | 1127683.83 | 2704287.5268 | 1127690.0371 | 2704288.1315 | 1127691.1134
56 | 2704967.7822 | 1127295.5196 | 2704936.6558 | 1127322.6013
57 | 2704194.032 | 1127758.6706 | 2704170.7721 | 1127763.8164 | 2704146.0093 | 1127767.4033 | 2704131.6157 | 1127769.0121
58 | 2704285.9772 | 1127683.83 | 2704285.9769 | 1127683.8286 | 2704283.5728 | 1127679.7735 | 2704280.2129 | 1127676.6247 | 2704278.3139 | 1127672.7784 | 2704275.9465 | 1127662.7524
59 | 2704265.135 | 1127474.8146 | 2704282.0868 | 1127500.0895 | 2704275.2157 | 1127523.9973 | 2704267.6102 | 1127565.9039 | 2704271.3225 | 1127612.5197 | 2704265.294 | 1127627.1113
60 | 2704265.135 | 1127474.8146 | 2704257.9164 | 1127467.0297
61 | 2704265.294 | 1127627.1113 | 2704262.7889 | 1127633.1746 | 2704270.4724 | 1127642.146 | 2704271.6085 | 1127646.6724
62 | 2704263.1504 | 1127452.2439 | 2704259.8989 | 1127455.7567 | 2704260.6489 | 1127458.7493 | 2704258.3615 | 1127464.458 | 2704257.9164 | 1127467.0297
63 | 2704272.6431 | 1127650.7031 | 2704272.4988 | 1127650.2194 | 2704271.6085 | 1127646.6724
64 | 2704263.1504 | 1127452.2439 | 2704264.4235 | 1127447.6963 | 2704267.0423 | 1127445.5623 | 2704266.9138 | 1127441.3908 | 2704261.6699 | 1127433.9623 | 2704261.0457 | 1127426.8026 | 2704258.0522 | 1127414.0207 | 2704257.3168 | 1127405.7138 | 2704254.4489 | 1127398.6043 | 2704252.3029 | 1127392.0966 | 2704252.6925 | 1127389.1681 | 2704252.5139 | 1127383.8839 | 2704248.5148 | 1127374.4312 | 2704245.9248 | 1127368.1937 | 2704247.4158 | 1127362.1823 | 2704242.7632 | 1127353.0852 | 2704241.5416 | 1127343.0244 | 2704236.4069 | 1127335.9537 | 2704234.5454 | 1127333.9537 | 2704235.7779 | 1127330.4171 | 2704232.3824 | 1127323.9545 | 2704230.0691 | 1127315.9652 | 2704227.6239 | 1127307.5844 | 2704227.9131 | 1127302.4305 | 2704228.7709 | 1127291.127
65 | 2704272.6431 | 1127650.7031 | 2704274.8448 | 1127658.0871 | 2704275.9465 | 1127662.7524
66 | 2704228.7709 | 1127291.127 | 2704236.414 | 1127285.0327 | 2704239.7247 | 1127278.9859 | 2704238.881 | 1127272.9342 | 2704236.0013 | 1127262.4779 | 2704231.6659 | 1127247.049 | 2704230.328 | 1127235.6854 | 2704226.8063 | 1127204.794 | 2704225.9948 | 1127195.085 | 2704223.3301 | 1127180.2074 | 2704219.2428 | 1127171.8428 | 2704221.2241 | 1127149.9075 | 2704229.6971 | 1127124.3039 | 2704233.7046 | 1127105.1164 | 2704239.6847 | 1127093.1118 | 2704244.1529 | 1127081.626 | 2704246.9745 | 1127078.9173 | 2704255.8384 | 1127072.6661 | 2704261.5069 | 1127065.7817 | 2704267.1291 | 1127052.6369 | 2704269.7685 | 1127043.51 | 2704277.4677 | 1127028.1209
67 | 2704131.6157 | 1127769.0121 | 2704131.6157 | 1127769.0121 | 2704123.2171 | 1127773.1628
68 | 2704123.2171 | 1127773.1628 | 2704110.6963 | 1127779.3507
69 | 2704095.2367 | 1127792.5792 | 2704110.6593 | 1127779.369 | 2704110.6963 | 1127779.3507
70 | 2704347.2442 | 1128230.5096 | 2704351.1159 | 1128233.4561 | 2704354.9224 | 1128239.281
71 | 2704354.9224 | 1128239.281 | 2704358.3452 | 1128239.6625 | 2704364.6867 | 1128240.6059 | 2704367.7306 | 1128241.0587 | 2704374.2565 | 1128240.2486 | 2704382.3632 | 1128237.5979 | 2704386.3693 | 1128234.0982 | 2704388.6403 | 1128237.8064 | 2704389.3917 | 1128254.0964 | 2704389.139 | 1128268.7235 | 2704395.6974 | 1128283.8796 | 2704402.5658 | 1128301.6094
72 | 2704229.2388 | 1128293.8148 | 2704220.4028 | 1128281.6251
73 | 2704229.2388 | 1128293.8148 | 2704235.3355 | 1128302.2254 | 2704235.4092 | 1128302.3112
74 | 2704235.4092 | 1128302.3112 | 2704241.9335 | 1128309.9067
75 | 2704154.006 | 1128267.534 | 2704159.0111 | 1128275.0043 | 2704162.4904 | 1128282.9806
76 | 2704162.4904 | 1128282.9806 | 2704166.1651 | 1128291.4046 | 2704174.4298 | 1128303.0336
77 | 2704208.5288 | 1128346.3323 | 2704201.6339 | 1128344.3491 | 2704194.4781 | 1128339.6895 | 2704189.1205 | 1128326.8224 | 2704184.1002 | 1128318.086 | 2704175.6527 | 1128304.7542 | 2704174.4298 | 1128303.0336
78 | 2704208.5288 | 1128346.3323 | 2704209.2408 | 1128346.5371 | 2704216.6296 | 1128349.7554 | 2704222.095 | 1128354.2126
79 | 2704222.095 | 1128354.2126 | 2704224.3734 | 1128356.0706 | 2704233.841 | 1128358.5019 | 2704239.3057 | 1128361.5371
80 | 2704239.3057 | 1128361.5371 | 2704242.642 | 1128363.3901 | 2704248.9593 | 1128368.858 | 2704251.5801 | 1128372.2719
81 | 2704252.2981 | 1128373.2072 | 2704251.5801 | 1128372.2719
82 | 2704252.2981 | 1128373.2072 | 2704256.1058 | 1128377.8367
83 | 2704252.2981 | 1128373.2072 | 2704253.4974 | 1128371.1376 | 2704248.0605 | 1128363.3279 | 2704249.7696 | 1128359.8551
84 | 2704241.9335 | 1128309.9067 | 2704242.9355 | 1128311.0731 | 2704251.8172 | 1128320.7952
85 | 2704252.5638 | 1128321.6124 | 2704251.8172 | 1128320.7952
86 | 2704252.5638 | 1128321.6124 | 2704259.4901 | 1128327.0686 | 2704266.8001 | 1128332.1005
87 | 2704252.5638 | 1128321.6124 | 2704251.0797 | 1128324.5553 | 2704253.3046 | 1128334.5111 | 2704255.373 | 1128341.2966
88 | 2704266.8001 | 1128332.1005 | 2704273.5719 | 1128336.7619 | 2704280.6459 | 1128344.5721
89 | 2704249.2768 | 1128346.427 | 2704249.2768 | 1128346.427 | 2704253.9533 | 1128344.7065 | 2704255.8428 | 1128342.8379 | 2704255.373 | 1128341.2966
90 | 2704280.6459 | 1128344.5721 | 2704281.9811 | 1128346.0461 | 2704286.1229 | 1128351.1986 | 2704286.8169 | 1128352.0667 | 2704290.3191 | 1128358.8917
91 | 2704249.2768 | 1128346.427 | 2704247.4716 | 1128349.2199 | 2704248.3221 | 1128353.9709 | 2704248.4506 | 1128354.4932
92 | 2704294.3438 | 1128368.5626 | 2704291.8419 | 1128361.8595 | 2704290.3191 | 1128358.8917
93 | 2704402.5658 | 1128301.6094 | 2704403.8125 | 1128304.833 | 2704406.9519 | 1128313.1369 | 2704411.6567 | 1128326.7379 | 2704414.5611 | 1128330.8017 | 2704420.1121 | 1128331.5536 | 2704449.4913 | 1128331.3941 | 2704484.9251 | 1128349.2063 | 2704505.0267 | 1128363.7073
94 | 2704248.4506 | 1128354.4932 | 2704249.7696 | 1128359.8551
95 | 2704649.8259 | 1128344.6545 | 2704505.0267 | 1128363.7073
96 | 2704305.2994 | 1128463.5338 | 2704302.7817 | 1128486.6273 | 2704302.1863 | 1128492.9988 | 2704301.8193 | 1128498.8092
97 | 2704305.2994 | 1128463.5338 | 2704300.1129 | 1128463.5555 | 2704300.1129 | 1128463.5555
98 | 2704301.6831 | 1128500.9659 | 2704301.8193 | 1128498.8092
99 | 2704295.994 | 1128443.7826 | 2704298.3009 | 1128449.3263 | 2704298.5757 | 1128454.3899 | 2704298.5848 | 1128461.0053 | 2704300.1129 | 1128463.5555
100 | 2704256.8524 | 1128378.7444 | 2704256.1058 | 1128377.8367
101 | 2704256.8524 | 1128378.7444 | 2704258.7737 | 1128381.0803
102 | 2704301.6831 | 1128500.9659 | 2704301.6643 | 1128501.2636
103 | 2704290.1521 | 1128429.7434 | 2704295.994 | 1128443.7826
104 | 2704262.743 | 1128385.9062 | 2704258.7737 | 1128381.0803
105 | 2704262.743 | 1128385.9062 | 2704263.1171 | 1128386.361
106 | 2704301.6643 | 1128501.2636 | 2704300.5534 | 1128518.8537 | 2704300.9578 | 1128525.3295
107 | 2704290.1521 | 1128429.7434 | 2704289.3375 | 1128427.7856
108 | 2704263.1171 | 1128386.361 | 2704264.6541 | 1128388.2297 | 2704269.7816 | 1128398.7803 | 2704269.989 | 1128398.9908
109 | 2704269.989 | 1128398.9908 | 2704273.2806 | 1128402.3318 | 2704281.298 | 1128409.7525 | 2704283.5244 | 1128413.8157 | 2704289.3375 | 1128427.7856
110 | 2704300.9578 | 1128525.3295 | 2704301.8213 | 1128539.1551 | 2704302.2826 | 1128541.8393
111 | 2704460.0764 | 1128992.7742 | 2704445.0664 | 1128938.814 | 2704440.3276 | 1128921.8659 | 2704434.8244 | 1128905.4493 | 2704424.3911 | 1128881.365 | 2704420.5094 | 1128873.2262 | 2704416.1019 | 1128864.7447 | 2704391.974 | 1128833.6084 | 2704388.6787 | 1128828.5483 | 2704388.6787 | 1128828.5483
112 | 2704460.0764 | 1128992.7742 | 2704464.4728 | 1128993.4172 | 2704470.583 | 1128999.6712 | 2704475.1324 | 1129011.9687 | 2704553.3919 | 1128989.0733 | 2704561.696 | 1128986.5375
113 | 2704561.696 | 1128986.5375 | 2704560.9106 | 1129015.4534 | 2704566.8557 | 1129037.926 | 2704568.0698 | 1129041.3007
114 | 2704561.696 | 1128986.5375 | 2704592.458 | 1128977.9752 | 2704609.41 | 1128966.4055 | 2704626.3866 | 1128948.0764 | 2704630.5735 | 1128946.5813 | 2704630.7408 | 1128945.8417
115 | 2704632.2673 | 1128939.0947 | 2704630.7408 | 1128945.8417
116 | 2704598.6557 | 1128821.5609 | 2704608.2055 | 1128817.8571 | 2704630.4244 | 1128807.8684 | 2704640.3744 | 1128804.1938
117 | 2704598.6557 | 1128821.5609 | 2704598.3132 | 1128819.3482
118 | 2704640.3744 | 1128804.1938 | 2704641.8007 | 1128792.1331
119 | 2704640.3744 | 1128804.1938 | 2704642.8247 | 1128817.0754
120 | 2704632.2673 | 1128939.0947 | 2704632.2673 | 1128939.0947 | 2704642.8019 | 1128939.5998
121 | 2704649.6904 | 1128939.9301 | 2704642.8019 | 1128939.5998
122 | 2704649.6904 | 1128939.9301 | 2704655.1656 | 1128921.4396
123 | 2704649.6904 | 1128939.9301 | 2704647.1731 | 1128949.5815 | 2704647.9557 | 1128956.0158
124 | 2704649.6904 | 1128939.9301 | 2704676.5372 | 1128943.076
125 | 2704655.894 | 1128918.9797 | 2704655.1656 | 1128921.4396
126 | 2704647.9557 | 1128956.0158 | 2704649.8982 | 1128971.9873 | 2704649.8982 | 1128971.9873
127 | 2704655.894 | 1128918.9797 | 2704660.837 | 1128915.2073 | 2704668.6704 | 1128910.4954 | 2704674.7669 | 1128904.6305 | 2704679.3378 | 1128896.9826 | 2704681.7216 | 1128895.3575
128 | 2704653.9351 | 1128980.1492 | 2704649.8982 | 1128971.9873
129 | 2704747.2473 | 1128834.2853 | 2704739.8646 | 1128839.2161 | 2704730.0509 | 1128844.8053 | 2704714.9741 | 1128856.1847 | 2704708.8095 | 1128865.9731 | 2704694.106 | 1128879.8273 | 2704689.1712 | 1128890.2485 | 2704686.5584 | 1128892.06 | 2704681.7216 | 1128895.3575
130 | 2704653.9351 | 1128980.1492 | 2704659.9487 | 1128992.3075 | 2704661.4811 | 1128998.9115
131 | 2704641.8007 | 1128792.1331 | 2704649.0674 | 1128792.0308
132 | 2704656.0268 | 1128792.9464 | 2704656.6957 | 1128793.4805 | 2704657.2821 | 1128798.3271 | 2704659.701 | 1128801.9268 | 2704669.2679 | 1128804.3606 | 2704675.2059 | 1128807.6543 | 2704683.2405 | 1128809.1277 | 2704698.4097 | 1128810.2132 | 2704709.8425 | 1128812.5793 | 2704715.4361 | 1128817.5126 | 2704722.8115 | 1128821.454 | 2704730.2423 | 1128827.9757 | 2704741.1235 | 1128832.378 | 2704747.2473 | 1128834.2853
133 | 2704661.4811 | 1128998.9115 | 2704661.5262 | 1128999.1058 | 2704664.0472 | 1129016.8273 | 2704667.1805 | 1129023.0003
134 | 2704656.0268 | 1128792.9464 | 2704662.8894 | 1128790.9083 | 2704669.2558 | 1128787.2606 | 2704674.4689 | 1128784.3601 | 2704693.3734 | 1128775.7708 | 2704708.1644 | 1128769.3339 | 2704718.9592 | 1128766.2744 | 2704723.1152 | 1128763.9004
135 | 2704656.0268 | 1128792.9464 | 2704649.9477 | 1128792.0184 | 2704649.0674 | 1128792.0308
136 | 2704714.8881 | 1128748.1813 | 2704717.6645 | 1128754.7225 | 2704721.1507 | 1128762.0986 | 2704723.1152 | 1128763.9004
137 | 2704723.1152 | 1128763.9004 | 2704724.0027 | 1128764.7163 | 2704729.3594 | 1128765.5318 | 2704734.5874 | 1128767.6356
138 | 2704649.8259 | 1128344.6545 | 2704654.6386 | 1128361.782 | 2704659.0476 | 1128379.5251 | 2704662.402 | 1128392.7471 | 2704661.4028 | 1128406.8388 | 2704655.8108 | 1128425.8207 | 2704646.1708 | 1128448.0458 | 2704645.1115 | 1128455.8954
139 | 2704645.2783 | 1128612.646 | 2704643.0107 | 1128600.2989 | 2704641.2426 | 1128560.8877 | 2704643.7499 | 1128515.3244 | 2704642.9972 | 1128471.5614 | 2704645.1115 | 1128455.8954
140 | 2704667.1805 | 1129023.0003 | 2704671.9156 | 1129032.3289 | 2704671.9156 | 1129032.3289
141 | 2704654.4964 | 1129073.9983 | 2704674.9853 | 1129060.6333 | 2704670.3085 | 1129046.3767 | 2704671.9156 | 1129032.3289
142 | 2705226.7028 | 1128661.2304 | 2705260.7554 | 1128671.3755 | 2705274.987 | 1128613.9311 | 2705294.5656 | 1128629.1038
143 | 2704769.6613 | 1128819.2751 | 2705226.7028 | 1128661.2304
144 | 2704769.6613 | 1128819.2751 | 2704762.3828 | 1128810.1877 | 2704758.5755 | 1128803.1173 | 2704753.0223 | 1128795.4051 | 2704751.639 | 1128792.079 | 2704749.3513 | 1128786.6915 | 2704747.568 | 1128782.4357 | 2704742.0079 | 1128775.1236 | 2704734.7008 | 1128767.6813 | 2704734.5874 | 1128767.6356
145 | 2704714.8881 | 1128748.1813 | 2704714.1353 | 1128742.5524
146 | 2704672.4473 | 1128710.2114 | 2704682.5725 | 1128716.4573 | 2704704.6299 | 1128725.6005 | 2704710.002 | 1128731.7641 | 2704713.6943 | 1128739.255 | 2704714.1353 | 1128742.5524
147 | 2704643.5676 | 1128710.1116 | 2704643.2676 | 1128698.9548 | 2704644.556 | 1128682.4 | 2704642.8909 | 1128666.531
148 | 2704643.5676 | 1128710.1116 | 2704672.4473 | 1128710.2114
149 | 2704641.6723 | 1128654.9168 | 2704642.8909 | 1128666.531
150 | 2704672.4473 | 1128710.2114 | 2704684.3958 | 1128706.3936 | 2704698.4004 | 1128703.5453 | 2704705.709 | 1128702.4955
151 | 2704643.0063 | 1128641.058 | 2704641.1562 | 1128649.9983 | 2704641.6723 | 1128654.9168
152 | 2704643.0063 | 1128641.058 | 2704644.3342 | 1128627.5613 | 2704645.2783 | 1128612.646

## bus_geodata
| x | y | coords
0 | 2704127.3229 | 1128158.8065
1 | 2704138.5591 | 1128166.2684
2 | 2704140.4475 | 1128168.0298
3 | 2704153.6007 | 1128177.5383
4 | 2704167.6632 | 1128176.3019
5 | 2704154.5927 | 1128190.9757
6 | 2704281.9851 | 1128108.1843
7 | 2704417.3259 | 1127806.2723
8 | 2704252.8411 | 1128153.2697
9 | 2704172.8769 | 1128151.5274
10 | 2704172.8441 | 1128152.3096
11 | 2704168.5613 | 1128227.5152
12 | 2704172.0716 | 1128234.511
13 | 2704177.281 | 1128243.0329
14 | 2704185.5078 | 1128252.666
15 | 2704225.9059 | 1128191.6706
16 | 2704214.9027 | 1128209.1607
17 | 2704241.2529 | 1128169.7907
18 | 2704190.2521 | 1128257.1982
19 | 2704203.9947 | 1128227.0822
20 | 2704198.426 | 1128263.4996
21 | 2704209.5721 | 1128267.426
22 | 2704215.9708 | 1128275.5109
23 | 2704201.0876 | 1128234.9497
24 | 2704545.4518 | 1127500.2169
25 | 2704541.1011 | 1127504.9413
26 | 2704529.541 | 1127514.6922
27 | 2704515.697 | 1127526.3609
28 | 2704583.8672 | 1127576.337
29 | 2704601.0088 | 1127687.2038
30 | 2704615.2129 | 1127580.3261
31 | 2704461.2381 | 1127571.804
32 | 2704454.7389 | 1127577.1626
33 | 2704464.1636 | 1127569.3918
34 | 2704488.0284 | 1127549.5193
35 | 2704489.308 | 1127548.4483
36 | 2704381.8276 | 1127648.7264
37 | 2704383.4394 | 1127621.4696
38 | 2704294.4925 | 1127699.9523
39 | 2704414.9604 | 1127610.2677
40 | 2704448.6622 | 1127748.1174
41 | 2704507.2309 | 1127533.447
42 | 2704704.5217 | 1127548.4622
43 | 2704876.7734 | 1127374.7026
44 | 2704676.2281 | 1127598.76
45 | 2704552.8759 | 1127771.783
46 | 2704434.7428 | 1127593.7085
47 | 2704497.4932 | 1127541.5973
48 | 2704379.8638 | 1127620.519
49 | 2704270.8064 | 1127731.5871
50 | 2704288.1315 | 1127691.1134
51 | 2704936.6558 | 1127322.6013
52 | 2704354.798 | 1127608.579
53 | 2704194.032 | 1127758.6706
54 | 2704285.9772 | 1127683.83
55 | 2704265.135 | 1127474.8146
56 | 2704265.294 | 1127627.1113
57 | 2704257.9164 | 1127467.0297
58 | 2704271.6085 | 1127646.6724
59 | 2704263.1504 | 1127452.2439
60 | 2704272.6431 | 1127650.7031
61 | 2704228.7709 | 1127291.127
62 | 2704275.9465 | 1127662.7524
63 | 2704277.4677 | 1127028.1209
64 | 2704131.6157 | 1127769.0121
65 | 2704123.2171 | 1127773.1628
66 | 2704110.6963 | 1127779.3507
67 | 2704095.2367 | 1127792.5792
68 | 2704347.2442 | 1128230.5096
69 | 2704354.9224 | 1128239.281
70 | 2704220.4028 | 1128281.6251
71 | 2704229.2388 | 1128293.8148
72 | 2704235.4092 | 1128302.3112
73 | 2704154.006 | 1128267.534
74 | 2704162.4905 | 1128282.9806
75 | 2704174.4298 | 1128303.0336
76 | 2704208.5288 | 1128346.3323
77 | 2704222.095 | 1128354.2126
78 | 2704239.3057 | 1128361.5371
79 | 2704251.5801 | 1128372.2719
80 | 2704252.2981 | 1128373.2072
81 | 2704241.9335 | 1128309.9067
82 | 2704251.8172 | 1128320.7952
83 | 2704252.5638 | 1128321.6124
84 | 2704266.8001 | 1128332.1005
85 | 2704255.373 | 1128341.2966
86 | 2704280.6459 | 1128344.5721
87 | 2704249.2768 | 1128346.427
88 | 2704290.3191 | 1128358.8917
89 | 2704402.5658 | 1128301.6094
90 | 2704248.4506 | 1128354.4932
91 | 2704294.3438 | 1128368.5626
92 | 2704249.7696 | 1128359.8551
93 | 2704505.0267 | 1128363.7073
94 | 2704305.2994 | 1128463.5338
95 | 2704301.8193 | 1128498.8092
96 | 2704300.1129 | 1128463.5555
97 | 2704256.1058 | 1128377.8367
98 | 2704256.8524 | 1128378.7444
99 | 2704301.6831 | 1128500.9659
100 | 2704295.994 | 1128443.7826
101 | 2704258.7737 | 1128381.0803
102 | 2704262.743 | 1128385.9062
103 | 2704301.6643 | 1128501.2636
104 | 2704290.1521 | 1128429.7434
105 | 2704263.1171 | 1128386.361
106 | 2704269.989 | 1128398.9908
107 | 2704289.3375 | 1128427.7856
108 | 2704300.9578 | 1128525.3295
109 | 2704302.2826 | 1128541.8393
110 | 2704388.6787 | 1128828.5483
111 | 2704460.0764 | 1128992.7742
112 | 2704561.696 | 1128986.5375
113 | 2704568.0698 | 1129041.3007
114 | 2704630.7408 | 1128945.8417
115 | 2704598.6557 | 1128821.5609
116 | 2704640.3744 | 1128804.1938
117 | 2704598.3132 | 1128819.3482
118 | 2704632.2673 | 1128939.0947
119 | 2704642.8019 | 1128939.5998
120 | 2704649.6904 | 1128939.9301
121 | 2704655.1656 | 1128921.4396
122 | 2704647.9557 | 1128956.0158
123 | 2704676.5372 | 1128943.076
124 | 2704655.894 | 1128918.9797
125 | 2704649.8982 | 1128971.9873
126 | 2704681.7216 | 1128895.3575
127 | 2704653.9351 | 1128980.1492
128 | 2704641.8007 | 1128792.1331
129 | 2704642.8247 | 1128817.0754
130 | 2704747.2473 | 1128834.2853
131 | 2704661.4811 | 1128998.9115
132 | 2704656.0268 | 1128792.9464
133 | 2704723.1152 | 1128763.9004
134 | 2704649.0674 | 1128792.0308
135 | 2704649.8259 | 1128344.6545
136 | 2704645.1115 | 1128455.8954
137 | 2704667.1805 | 1129023.0003
138 | 2704671.9156 | 1129032.3289
139 | 2704654.4964 | 1129073.9983
140 | 2705226.7028 | 1128661.2304
141 | 2705294.5656 | 1128629.1038
142 | 2704769.6613 | 1128819.2751
143 | 2704734.5874 | 1128767.6356
144 | 2704714.8881 | 1128748.1813
145 | 2704714.1353 | 1128742.5524
146 | 2704643.5676 | 1128710.1116
147 | 2704642.8909 | 1128666.531
148 | 2704672.4473 | 1128710.2114
149 | 2704641.6723 | 1128654.9168
150 | 2704705.709 | 1128702.4955
151 | 2704643.0063 | 1128641.058
152 | 2704645.2783 | 1128612.646
153 | 2704967.7822 | 1127295.5196
154 | 2704252.5638 | 1128321.6124

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1