## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5402-4_2_3_node_119 | 0.4 | n |  | TRUE
1 | bus_LV_5402-4_2_3_node_120 | 0.4 | n |  | TRUE
2 | bus_LV_5402-4_2_3_node_121 | 0.4 | n |  | TRUE
3 | bus_LV_5402-4_2_3_node_122 | 0.4 | n |  | TRUE
4 | bus_LV_5402-4_2_3_node_123 | 0.4 | n |  | TRUE
5 | bus_LV_5402-4_2_3_node_124 | 0.4 | n |  | TRUE
6 | bus_LV_5402-4_2_3_node_125 | 0.4 | n |  | TRUE
7 | bus_LV_5402-4_2_3_node_126 | 0.4 | n |  | TRUE
8 | bus_LV_5402-4_2_3_node_127 | 0.4 | n |  | TRUE
9 | bus_LV_5402-4_2_3_node_128 | 0.4 | n |  | TRUE
10 | bus_LV_5402-4_2_3_node_162 | 0.4 | n |  | TRUE
11 | bus_LV_5402-4_2_3_node_223 | 0.4 | n |  | TRUE
12 | bus_LV_5402-4_2_3_node_237 | 0.4 | n |  | TRUE
13 | bus_LV_5402-4_2_3_node_129 | 0.4 | n |  | TRUE
14 | bus_LV_5402-4_2_3_node_130 | 0.4 | n |  | TRUE
15 | bus_LV_5402-4_2_3_node_131 | 0.4 | n |  | TRUE
16 | bus_LV_5402-4_2_3_node_190 | 0.4 | n |  | TRUE
17 | bus_LV_5402-4_2_3_node_132 | 0.4 | n |  | TRUE
18 | bus_LV_5402-4_2_3_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_5402-4_2_3_node_280 | 0.4 | n |  | TRUE
20 | bus_LV_5402-4_2_3_node_134 | 0.4 | n |  | TRUE
21 | bus_LV_5402-4_2_3_node_135 | 0.4 | n |  | TRUE
22 | bus_LV_5402-4_2_3_node_136 | 0.4 | n |  | TRUE
23 | bus_LV_5402-4_2_3_node_137 | 0.4 | n |  | TRUE
24 | bus_LV_5402-4_2_3_node_250 | 0.4 | n |  | TRUE
25 | bus_LV_5402-4_2_3_node_242 | 0.4 | n |  | TRUE
26 | bus_LV_5402-4_2_3_node_138 | 0.4 | n |  | TRUE
27 | bus_LV_5402-4_2_3_node_139 | 0.4 | n |  | TRUE
28 | bus_LV_5402-4_2_3_node_364 | 0.4 | n |  | TRUE
29 | bus_LV_5402-4_2_3_node_388 | 0.4 | n |  | TRUE
30 | bus_LV_5402-4_2_3_node_140 | 0.4 | n |  | TRUE
31 | bus_LV_5402-4_2_3_node_141 | 0.4 | n |  | TRUE
32 | bus_LV_5402-4_2_3_node_142 | 0.4 | n |  | TRUE
33 | bus_LV_5402-4_2_3_node_143 | 0.4 | n |  | TRUE
34 | bus_LV_5402-4_2_3_node_144 | 0.4 | n |  | TRUE
35 | bus_LV_5402-4_2_3_node_145 | 0.4 | n |  | TRUE
36 | bus_LV_5402-4_2_3_node_146 | 0.4 | n |  | TRUE
37 | bus_LV_5402-4_2_3_node_147 | 0.4 | n |  | TRUE
38 | bus_LV_5402-4_2_3_node_224 | 0.4 | n |  | TRUE
39 | bus_LV_5402-4_2_3_node_161 | 0.4 | n |  | TRUE
40 | bus_LV_5402-4_2_3_node_227 | 0.4 | n |  | TRUE
41 | bus_LV_5402-4_2_3_node_148 | 0.4 | n |  | TRUE
42 | bus_LV_5402-4_2_3_node_149 | 0.4 | n |  | TRUE
43 | bus_LV_5402-4_2_3_node_150 | 0.4 | n |  | TRUE
44 | bus_LV_5402-4_2_3_node_151 | 0.4 | n |  | TRUE
45 | bus_LV_5402-4_2_3_node_152 | 0.4 | n |  | TRUE
46 | bus_LV_5402-4_2_3_node_153 | 0.4 | n |  | TRUE
47 | bus_LV_5402-4_2_3_node_154 | 0.4 | n |  | TRUE
48 | bus_LV_5402-4_2_3_node_176 | 0.4 | n |  | TRUE
49 | bus_LV_5402-4_2_3_node_167 | 0.4 | n |  | TRUE
50 | bus_LV_5402-4_2_3_node_155 | 0.4 | n |  | TRUE
51 | bus_LV_5402-4_2_3_node_156 | 0.4 | n |  | TRUE
52 | bus_LV_5402-4_2_3_node_157 | 0.4 | n |  | TRUE
53 | bus_LV_5402-4_2_3_node_158 | 0.4 | n |  | TRUE
54 | bus_LV_5402-4_2_3_node_159 | 0.4 | n |  | TRUE
55 | bus_LV_5402-4_2_3_node_160 | 0.4 | n |  | TRUE
56 | bus_LV_5402-4_2_3_node_208 | 0.4 | n |  | TRUE
57 | bus_LV_5402-4_2_3_node_205 | 0.4 | n |  | TRUE
58 | bus_LV_5402-4_2_3_node_194 | 0.4 | n |  | TRUE
59 | bus_LV_5402-4_2_3_node_169 | 0.4 | n |  | TRUE
60 | bus_LV_5402-4_2_3_node_163 | 0.4 | n |  | TRUE
61 | bus_LV_5402-4_2_3_node_164 | 0.4 | n |  | TRUE
62 | bus_LV_5402-4_2_3_node_165 | 0.4 | n |  | TRUE
63 | bus_LV_5402-4_2_3_node_166 | 0.4 | n |  | TRUE
64 | bus_LV_5402-4_2_3_node_168 | 0.4 | n |  | TRUE
65 | bus_LV_5402-4_2_3_node_170 | 0.4 | n |  | TRUE
66 | bus_LV_5402-4_2_3_node_193 | 0.4 | n |  | TRUE
67 | bus_LV_5402-4_2_3_node_370 | 0.4 | n |  | TRUE
68 | bus_LV_5402-4_2_3_node_382 | 0.4 | n |  | TRUE
69 | bus_LV_5402-4_2_3_node_171 | 0.4 | n |  | TRUE
70 | bus_LV_5402-4_2_3_node_172 | 0.4 | n |  | TRUE
71 | bus_LV_5402-4_2_3_node_173 | 0.4 | n |  | TRUE
72 | bus_LV_5402-4_2_3_node_174 | 0.4 | n |  | TRUE
73 | bus_LV_5402-4_2_3_node_175 | 0.4 | n |  | TRUE
74 | bus_LV_5402-4_2_3_node_177 | 0.4 | n |  | TRUE
75 | bus_LV_5402-4_2_3_node_178 | 0.4 | n |  | TRUE
76 | bus_LV_5402-4_2_3_node_179 | 0.4 | n |  | TRUE
77 | bus_LV_5402-4_2_3_node_197 | 0.4 | n |  | TRUE
78 | bus_LV_5402-4_2_3_node_200 | 0.4 | n |  | TRUE
79 | bus_LV_5402-4_2_3_node_260 | 0.4 | n |  | TRUE
80 | bus_LV_5402-4_2_3_node_180 | 0.4 | n |  | TRUE
81 | bus_LV_5402-4_2_3_node_181 | 0.4 | n |  | TRUE
82 | bus_LV_5402-4_2_3_node_182 | 0.4 | n |  | TRUE
83 | bus_LV_5402-4_2_3_node_183 | 0.4 | n |  | TRUE
84 | bus_LV_5402-4_2_3_node_184 | 0.4 | n |  | TRUE
85 | bus_LV_5402-4_2_3_node_186 | 0.4 | n |  | TRUE
86 | bus_LV_5402-4_2_3_node_187 | 0.4 | n |  | TRUE
87 | bus_LV_5402-4_2_3_node_185 | 0.4 | n |  | TRUE
88 | bus_LV_5402-4_2_3_node_195 | 0.4 | n |  | TRUE
89 | bus_LV_5402-4_2_3_node_188 | 0.4 | n |  | TRUE
90 | bus_LV_5402-4_2_3_node_189 | 0.4 | n |  | TRUE
91 | bus_LV_5402-4_2_3_node_191 | 0.4 | n |  | TRUE
92 | bus_LV_5402-4_2_3_node_192 | 0.4 | n |  | TRUE
93 | bus_LV_5402-4_2_3_node_215 | 0.4 | n |  | TRUE
94 | bus_LV_5402-4_2_3_node_211 | 0.4 | n |  | TRUE
95 | bus_LV_5402-4_2_3_node_196 | 0.4 | n |  | TRUE
96 | bus_LV_5402-4_2_3_node_199 | 0.4 | n |  | TRUE
97 | bus_LV_5402-4_2_3_node_198 | 0.4 | n |  | TRUE
98 | bus_LV_5402-4_2_3_node_266 | 0.4 | n |  | TRUE
99 | bus_LV_5402-4_2_3_node_231 | 0.4 | n |  | TRUE
100 | bus_LV_5402-4_2_3_node_252 | 0.4 | n |  | TRUE
101 | bus_LV_5402-4_2_3_node_251 | 0.4 | n |  | TRUE
102 | bus_LV_5402-4_2_3_node_201 | 0.4 | n |  | TRUE
103 | bus_LV_5402-4_2_3_node_202 | 0.4 | n |  | TRUE
104 | bus_LV_5402-4_2_3_node_203 | 0.4 | n |  | TRUE
105 | bus_LV_5402-4_2_3_node_204 | 0.4 | n |  | TRUE
106 | bus_LV_5402-4_2_3_node_276 | 0.4 | n |  | TRUE
107 | bus_LV_5402-4_2_3_node_206 | 0.4 | n |  | TRUE
108 | bus_LV_5402-4_2_3_node_207 | 0.4 | n |  | TRUE
109 | bus_LV_5402-4_2_3_node_226 | 0.4 | n |  | TRUE
110 | bus_LV_5402-4_2_3_node_263 | 0.4 | n |  | TRUE
111 | bus_LV_5402-4_2_3_node_220 | 0.4 | n |  | TRUE
112 | bus_LV_5402-4_2_3_node_218 | 0.4 | n |  | TRUE
113 | bus_LV_5402-4_2_3_node_209 | 0.4 | n |  | TRUE
114 | bus_LV_5402-4_2_3_node_210 | 0.4 | n |  | TRUE
115 | bus_LV_5402-4_2_3_node_212 | 0.4 | n |  | TRUE
116 | bus_LV_5402-4_2_3_node_213 | 0.4 | n |  | TRUE
117 | bus_LV_5402-4_2_3_node_214 | 0.4 | n |  | TRUE
118 | bus_LV_5402-4_2_3_node_239 | 0.4 | n |  | TRUE
119 | bus_LV_5402-4_2_3_node_240 | 0.4 | n |  | TRUE
120 | bus_LV_5402-4_2_3_node_236 | 0.4 | n |  | TRUE
121 | bus_LV_5402-4_2_3_node_221 | 0.4 | n |  | TRUE
122 | bus_LV_5402-4_2_3_node_216 | 0.4 | n |  | TRUE
123 | bus_LV_5402-4_2_3_node_217 | 0.4 | n |  | TRUE
124 | bus_LV_5402-4_2_3_node_219 | 0.4 | n |  | TRUE
125 | bus_LV_5402-4_2_3_node_222 | 0.4 | n |  | TRUE
126 | bus_LV_5402-4_2_3_node_233 | 0.4 | n |  | TRUE
127 | bus_LV_5402-4_2_3_node_234 | 0.4 | n |  | TRUE
128 | bus_LV_5402-4_2_3_node_225 | 0.4 | n |  | TRUE
129 | bus_LV_5402-4_2_3_node_228 | 0.4 | n |  | TRUE
130 | bus_LV_5402-4_2_3_node_229 | 0.4 | n |  | TRUE
131 | bus_LV_5402-4_2_3_node_230 | 0.4 | n |  | TRUE
132 | bus_LV_5402-4_2_3_node_232 | 0.4 | n |  | TRUE
133 | bus_LV_5402-4_2_3_node_268 | 0.4 | n |  | TRUE
134 | bus_LV_5402-4_2_3_node_253 | 0.4 | n |  | TRUE
135 | bus_LV_5402-4_2_3_node_235 | 0.4 | n |  | TRUE
136 | bus_LV_5402-4_2_3_node_238 | 0.4 | n |  | TRUE
137 | bus_LV_5402-4_2_3_node_244 | 0.4 | n |  | TRUE
138 | bus_LV_5402-4_2_3_node_241 | 0.4 | n |  | TRUE
139 | bus_LV_5402-4_2_3_node_243 | 0.4 | n |  | TRUE
140 | bus_LV_5402-4_2_3_node_247 | 0.4 | n |  | TRUE
141 | bus_LV_5402-4_2_3_node_245 | 0.4 | n |  | TRUE
142 | bus_LV_5402-4_2_3_node_246 | 0.4 | n |  | TRUE
143 | bus_LV_5402-4_2_3_node_262 | 0.4 | n |  | TRUE
144 | bus_LV_5402-4_2_3_node_248 | 0.4 | n |  | TRUE
145 | bus_LV_5402-4_2_3_node_255 | 0.4 | n |  | TRUE
146 | bus_LV_5402-4_2_3_node_369 | 0.4 | n |  | TRUE
147 | bus_LV_5402-4_2_3_node_256 | 0.4 | n |  | TRUE
148 | bus_LV_5402-4_2_3_node_257 | 0.4 | n |  | TRUE
149 | bus_LV_5402-4_2_3_node_258 | 0.4 | n |  | TRUE
150 | bus_LV_5402-4_2_3_node_259 | 0.4 | n |  | TRUE
151 | bus_LV_5402-4_2_3_node_261 | 0.4 | n |  | TRUE
152 | bus_LV_5402-4_2_3_node_264 | 0.4 | n |  | TRUE
153 | bus_LV_5402-4_2_3_node_265 | 0.4 | n |  | TRUE
154 | bus_LV_5402-4_2_3_node_387 | 0.4 | n |  | TRUE
155 | bus_LV_5402-4_2_3_node_267 | 0.4 | n |  | TRUE
156 | bus_LV_5402-4_2_3_node_277 | 0.4 | n |  | TRUE
157 | bus_LV_5402-4_2_3_node_269 | 0.4 | n |  | TRUE
158 | bus_LV_5402-4_2_3_node_271 | 0.4 | n |  | TRUE
159 | bus_LV_5402-4_2_3_node_270 | 0.4 | n |  | TRUE
160 | bus_LV_5402-4_2_3_node_272 | 0.4 | n |  | TRUE
161 | bus_LV_5402-4_2_3_node_273 | 0.4 | n |  | TRUE
162 | bus_LV_5402-4_2_3_node_274 | 0.4 | n |  | TRUE
163 | bus_LV_5402-4_2_3_node_275 | 0.4 | n |  | TRUE
164 | bus_LV_5402-4_2_3_node_281 | 0.4 | n |  | TRUE
165 | bus_LV_5402-4_2_3_node_365 | 0.4 | n |  | TRUE
166 | bus_LV_5402-4_2_3_node_366 | 0.4 | n |  | TRUE
167 | bus_LV_5402-4_2_3_node_367 | 0.4 | n |  | TRUE
168 | bus_LV_5402-4_2_3_node_390 | 0.4 | n |  | TRUE
169 | bus_LV_5402-4_2_3_node_368 | 0.4 | n |  | TRUE
170 | bus_LV_5402-4_2_3_node_371 | 0.4 | n |  | TRUE
171 | bus_LV_5402-4_2_3_node_372 | 0.4 | n |  | TRUE
172 | bus_LV_5402-4_2_3_node_383 | 0.4 | n |  | TRUE
173 | bus_LV_5402-4_2_3_node_399 | 0.4 | n |  | TRUE
174 | bus_LV_5402-4_2_3_node_389 | 0.4 | n |  | TRUE
175 | bus_MV_190_0_node_233 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5402-4_2_3_load_119 | 0 | 0.00021842 | 5.474e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5402-4_2_3_load_120 | 1 | 0.00035911 | 9.0002e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5402-4_2_3_load_123 | 4 | 0.00015973 | 4.0032e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5402-4_2_3_load_124 | 5 | 0.00053315 | 0.00013362 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5402-4_2_3_load_125 | 6 | 0.00018395 | 4.6102e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5402-4_2_3_load_126 | 7 | 0.00020248 | 5.0748e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5402-4_2_3_load_127 | 8 | 0.00022182 | 5.5594e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5402-4_2_3_load_128 | 9 | 0.00029043 | 7.2788e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5402-4_2_3_load_223 | 11 | 0.00027805 | 6.9687e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5402-4_2_3_load_237 | 12 | 0.00060538 | 0.00015172 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5402-4_2_3_load_129 | 13 | 0.002911 | 0.00072955 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5402-4_2_3_load_130 | 14 | 0.0068524 | 0.0017174 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5402-4_2_3_load_280 | 19 | 0.0025243 | 0.00063266 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5402-4_2_3_load_134 | 20 | 0.00036246 | 9.0841e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5402-4_2_3_load_136 | 22 | 0.0007409 | 0.00018569 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5402-4_2_3_load_250 | 24 | 0.00044907 | 0.00011255 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5402-4_2_3_load_242 | 25 | 0.00036489 | 9.1449e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5402-4_2_3_load_138 | 26 | 0.00041865 | 0.00010492 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5402-4_2_3_load_364 | 28 | 0.00049175 | 0.00012324 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5402-4_2_3_load_388 | 29 | 0.00043192 | 0.00010825 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5402-4_2_3_load_140 | 30 | 0.0004612 | 0.00011559 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5402-4_2_3_load_141 | 31 | 0.00042761 | 0.00010717 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5402-4_2_3_load_142 | 32 | 0.000367 | 9.1979e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5402-4_2_3_load_143 | 33 | 0.00036242 | 9.083e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5402-4_2_3_load_145 | 35 | 0.00109 | 0.00027318 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5402-4_2_3_load_146 | 36 | 0.00017886 | 4.4826e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5402-4_2_3_load_147 | 37 | 0.00032887 | 8.2423e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5402-4_2_3_load_224 | 38 | 0.00035914 | 9.0008e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5402-4_2_3_load_161 | 39 | 0.00013796 | 3.4577e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5402-4_2_3_load_148 | 41 | 0.00070599 | 0.00017694 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5402-4_2_3_load_149 | 42 | 0.0012214 | 0.00030612 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5402-4_2_3_load_150 | 43 | 0.0013014 | 0.00032617 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5402-4_2_3_load_151 | 44 | 0.0013143 | 0.0003294 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5402-4_2_3_load_152 | 45 | 0.00011659 | 2.922e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5402-4_2_3_load_153 | 46 | 0.0013908 | 0.00034857 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5402-4_2_3_load_154 | 47 | 0.00071886 | 0.00018016 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5402-4_2_3_load_167 | 49 | 0.0004938 | 0.00012376 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5402-4_2_3_load_155 | 50 | 0.00030231 | 7.5765e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5402-4_2_3_load_156 | 51 | 0.00053734 | 0.00013467 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5402-4_2_3_load_157 | 52 | 0.00031137 | 7.8036e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5402-4_2_3_load_159 | 54 | 0.00031574 | 7.9132e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5402-4_2_3_load_160 | 55 | 0.0015064 | 0.00037753 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5402-4_2_3_load_205 | 57 | 0.0013288 | 0.00033302 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5402-4_2_3_load_194 | 58 | 0.00047528 | 0.00011912 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5402-4_2_3_load_163 | 60 | 0.0006154 | 0.00015423 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5402-4_2_3_load_164 | 61 | 0.0013778 | 0.0003453 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5402-4_2_3_load_166 | 63 | 0.0007842 | 0.00019654 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5402-4_2_3_load_168 | 64 | 0.00032685 | 8.1915e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5402-4_2_3_load_170 | 65 | 0.00017546 | 4.3975e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5402-4_2_3_load_193 | 66 | 0.00070494 | 0.00017668 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5402-4_2_3_load_370 | 67 | 0.00017719 | 4.4408e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5402-4_2_3_load_171 | 69 | 0.0021336 | 0.00053473 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5402-4_2_3_load_172 | 70 | 0.00096476 | 0.00024179 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5402-4_2_3_load_174 | 72 | 0.0020718 | 0.00051925 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5402-4_2_3_load_177 | 74 | 0.0010429 | 0.00026138 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5402-4_2_3_load_178 | 75 | 0.00079586 | 0.00019946 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5402-4_2_3_load_179 | 76 | 0.0012301 | 0.0003083 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5402-4_2_3_load_197 | 77 | 0.0014111 | 0.00035365 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5402-4_2_3_load_260 | 79 | 0.0016441 | 0.00041204 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5402-4_2_3_load_180 | 80 | 0.0011398 | 0.00028566 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5402-4_2_3_load_181 | 81 | 0.00069398 | 0.00017393 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5402-4_2_3_load_184 | 84 | 0.0005715 | 0.00014323 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5402-4_2_3_load_186 | 85 | 0.0018255 | 0.00045752 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5402-4_2_3_load_187 | 86 | 0.00124 | 0.00031078 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5402-4_2_3_load_185 | 87 | 0.00040204 | 0.00010076 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5402-4_2_3_load_195 | 88 | 0.0018942 | 0.00047473 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5402-4_2_3_load_188 | 89 | 0.00014503 | 3.6348e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5402-4_2_3_load_189 | 90 | 0.00030723 | 7.6999e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5402-4_2_3_load_191 | 91 | 0.00019569 | 4.9045e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5402-4_2_3_load_215 | 93 | 0.00035239 | 8.8318e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5402-4_2_3_load_266 | 98 | 0.00055564 | 0.00013926 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5402-4_2_3_load_231 | 99 | 0.0005934 | 0.00014872 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5402-4_2_3_load_252 | 100 | 0.00071949 | 0.00018032 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5402-4_2_3_load_251 | 101 | 0.00092573 | 0.00023201 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5402-4_2_3_load_201 | 102 | 0.0020966 | 0.00052545 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5402-4_2_3_load_203 | 104 | 0.00096588 | 0.00024207 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5402-4_2_3_load_204 | 105 | 0.00020541 | 5.1481e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5402-4_2_3_load_206 | 107 | 0.00065318 | 0.0001637 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5402-4_2_3_load_226 | 109 | 0.001207 | 0.0003025 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5402-4_2_3_load_220 | 111 | 0.0011658 | 0.00029218 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5402-4_2_3_load_209 | 113 | 0.00013466 | 3.3749e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5402-4_2_3_load_210 | 114 | 0.00023056 | 5.7784e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5402-4_2_3_load_212 | 115 | 0.00022956 | 5.7534e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5402-4_2_3_load_213 | 116 | 0.00033003 | 8.2713e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5402-4_2_3_load_240 | 119 | 0.00031204 | 7.8204e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5402-4_2_3_load_236 | 120 | 0.00023844 | 5.976e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5402-4_2_3_load_221 | 121 | 0.00028421 | 7.123e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5402-4_2_3_load_216 | 122 | 0.0006359 | 0.00015937 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5402-4_2_3_load_217 | 123 | 0.00064358 | 0.0001613 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5402-4_2_3_load_219 | 124 | 0.00020786 | 5.2095e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5402-4_2_3_load_233 | 126 | 0.00033134 | 8.3042e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5402-4_2_3_load_225 | 128 | 0.00026162 | 6.5568e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5402-4_2_3_load_229 | 130 | 0.00034444 | 8.6324e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5402-4_2_3_load_230 | 131 | 0.0017525 | 0.00043921 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5402-4_2_3_load_268 | 133 | 0.0017995 | 0.000451 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5402-4_2_3_load_235 | 135 | 0.00027205 | 6.8182e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5402-4_2_3_load_238 | 136 | 0.00082185 | 0.00020598 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5402-4_2_3_load_244 | 137 | 0.00063239 | 0.00015849 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5402-4_2_3_load_241 | 138 | 0.00033054 | 8.2841e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5402-4_2_3_load_243 | 139 | 0.00038697 | 9.6985e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5402-4_2_3_load_247 | 140 | 0.00045781 | 0.00011474 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5402-4_2_3_load_245 | 141 | 0.00032078 | 8.0394e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5402-4_2_3_load_246 | 142 | 0.00049874 | 0.00012499 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5402-4_2_3_load_262 | 143 | 0.00028769 | 7.2101e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5402-4_2_3_load_248 | 144 | 0.00044962 | 0.00011268 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5402-4_2_3_load_255 | 145 | 0.00038943 | 9.76e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5402-4_2_3_load_369 | 146 | 0.00094171 | 0.00023601 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5402-4_2_3_load_256 | 147 | 0.00038313 | 9.6022e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5402-4_2_3_load_257 | 148 | 0.0002479 | 6.2131e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5402-4_2_3_load_258 | 149 | 0.00078312 | 0.00019627 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5402-4_2_3_load_259 | 150 | 0.0009694 | 0.00024295 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5402-4_2_3_load_261 | 151 | 0.0010922 | 0.00027373 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5402-4_2_3_load_264 | 152 | 0.0004045 | 0.00010138 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5402-4_2_3_load_265 | 153 | 0.0005308 | 0.00013303 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5402-4_2_3_load_267 | 155 | 0.00058678 | 0.00014706 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5402-4_2_3_load_277 | 156 | 0.00033514 | 8.3994e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_5402-4_2_3_load_269 | 157 | 0.00029824 | 7.4747e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_5402-4_2_3_load_272 | 160 | 0.00039457 | 9.8888e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_5402-4_2_3_load_273 | 161 | 0.0003337 | 8.3633e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_5402-4_2_3_load_275 | 163 | 0.00025058 | 6.2802e-05 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_5402-4_2_3_load_281 | 164 | 0.0010794 | 0.00027053 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_5402-4_2_3_load_365 | 165 | 0.00041963 | 0.00010517 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_5402-4_2_3_load_367 | 167 | 0.0010305 | 0.00025827 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_5402-4_2_3_load_368 | 169 | 0.0017551 | 0.00043986 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_5402-4_2_3_load_371 | 170 | 0.00023334 | 5.8481e-05 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_5402-4_2_3_load_372 | 171 | 0.00019877 | 4.9817e-05 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_5402-4_2_3_load_383 | 172 | 0.00028986 | 7.2646e-05 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_5402-4_2_3_load_399 | 173 | 0.00012922 | 3.2386e-05 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_5402-4_2_3_load_389 | 174 | 0.00027006 | 6.7684e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 123 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5402-4_2_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_5402-4_2_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0090771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_5402-4_2_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0098389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_5402-4_2_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0089026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5402-4_2_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.010206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_5402-4_2_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.023842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_5402-4_2_3_line_6 | NAYY 4x150 SE | 3 | 7 | 0.010598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5402-4_2_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.011165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5402-4_2_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.035987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_5402-4_2_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.035864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_5402-4_2_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.0042288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5402-4_2_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.030959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_5402-4_2_3_line_12 | NAYY 4x150 SE | 10 | 58 | 0.024021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5402-4_2_3_line_13 | NAYY 4x150 SE | 10 | 59 | 0.041724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_5402-4_2_3_line_14 | NAYY 4x150 SE | 12 | 136 | 0.018113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_5402-4_2_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.024961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5402-4_2_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.048465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5402-4_2_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.66175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5402-4_2_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.052853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5402-4_2_3_line_19 | NAYY 4x150 SE | 16 | 89 | 0.1203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5402-4_2_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.12097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5402-4_2_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.18002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5402-4_2_3_line_22 | NAYY 4x150 SE | 19 | 164 | 0.00032778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5402-4_2_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.024507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5402-4_2_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.073044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5402-4_2_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.00042339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5402-4_2_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.01273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5402-4_2_3_line_27 | NAYY 4x150 SE | 23 | 25 | 0.047144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5402-4_2_3_line_28 | NAYY 4x150 SE | 25 | 118 | 0.017288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5402-4_2_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.15551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5402-4_2_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5402-4_2_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.68714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5402-4_2_3_line_32 | NAYY 4x150 SE | 29 | 154 | 0.077235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5402-4_2_3_line_33 | NAYY 4x150 SE | 30 | 31 | 0.019884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5402-4_2_3_line_34 | NAYY 4x150 SE | 30 | 32 | 0.027309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5402-4_2_3_line_35 | NAYY 4x150 SE | 31 | 33 | 0.020715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5402-4_2_3_line_36 | NAYY 4x150 SE | 32 | 34 | 0.021977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5402-4_2_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.038034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5402-4_2_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.017461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5402-4_2_3_line_39 | NAYY 4x150 SE | 34 | 37 | 0.015931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5402-4_2_3_line_40 | NAYY 4x150 SE | 35 | 38 | 0.012007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5402-4_2_3_line_41 | NAYY 4x150 SE | 36 | 39 | 0.011644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5402-4_2_3_line_42 | NAYY 4x150 SE | 37 | 40 | 0.056459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5402-4_2_3_line_43 | NAYY 4x150 SE | 38 | 128 | 0.011436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5402-4_2_3_line_44 | NAYY 4x150 SE | 40 | 129 | 0.039609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5402-4_2_3_line_45 | NAYY 4x150 SE | 40 | 130 | 0.041704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5402-4_2_3_line_46 | NAYY 4x150 SE | 41 | 42 | 0.008136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5402-4_2_3_line_47 | NAYY 4x150 SE | 41 | 43 | 0.024356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5402-4_2_3_line_48 | NAYY 4x150 SE | 42 | 44 | 0.021313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5402-4_2_3_line_49 | NAYY 4x150 SE | 43 | 45 | 0.0020018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5402-4_2_3_line_50 | NAYY 4x150 SE | 44 | 46 | 0.018555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5402-4_2_3_line_51 | NAYY 4x150 SE | 45 | 47 | 0.015042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5402-4_2_3_line_52 | NAYY 4x150 SE | 46 | 48 | 0.043899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5402-4_2_3_line_53 | NAYY 4x150 SE | 47 | 49 | 0.062944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5402-4_2_3_line_54 | NAYY 4x150 SE | 48 | 76 | 0.007583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5402-4_2_3_line_55 | NAYY 4x150 SE | 48 | 71 | 0.027342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5402-4_2_3_line_56 | NAYY 4x150 SE | 49 | 62 | 0.044157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_5402-4_2_3_line_57 | NAYY 4x150 SE | 50 | 51 | 0.056719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5402-4_2_3_line_58 | NAYY 4x150 SE | 50 | 52 | 0.0020585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5402-4_2_3_line_59 | NAYY 4x150 SE | 51 | 53 | 0.012379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5402-4_2_3_line_60 | NAYY 4x150 SE | 53 | 54 | 0.022961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_5402-4_2_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.010937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_5402-4_2_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.0098875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_5402-4_2_3_line_63 | NAYY 4x150 SE | 55 | 57 | 0.0424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_5402-4_2_3_line_64 | NAYY 4x150 SE | 56 | 111 | 0.013158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_5402-4_2_3_line_65 | NAYY 4x150 SE | 56 | 112 | 0.021928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_5402-4_2_3_line_66 | NAYY 4x150 SE | 57 | 107 | 0.011507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_5402-4_2_3_line_67 | NAYY 4x150 SE | 59 | 66 | 0.021636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5402-4_2_3_line_68 | NAYY 4x150 SE | 59 | 63 | 0.051086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_5402-4_2_3_line_69 | NAYY 4x150 SE | 60 | 61 | 0.058141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_5402-4_2_3_line_70 | NAYY 4x150 SE | 60 | 62 | 0.005241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_5402-4_2_3_line_71 | NAYY 4x150 SE | 61 | 63 | 0.0010463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_5402-4_2_3_line_72 | NAYY 4x150 SE | 62 | 64 | 0.15458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5402-4_2_3_line_73 | NAYY 4x150 SE | 64 | 65 | 0.14318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5402-4_2_3_line_74 | NAYY 4x150 SE | 65 | 67 | 0.039489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_5402-4_2_3_line_75 | NAYY 4x150 SE | 65 | 68 | 0.12627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_5402-4_2_3_line_76 | NAYY 4x150 SE | 67 | 170 | 0.077808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_5402-4_2_3_line_77 | NAYY 4x150 SE | 68 | 172 | 0.056749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_5402-4_2_3_line_78 | NAYY 4x150 SE | 69 | 70 | 0.027808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_5402-4_2_3_line_79 | NAYY 4x150 SE | 69 | 71 | 0.020785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_5402-4_2_3_line_80 | NAYY 4x150 SE | 70 | 72 | 0.030209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_5402-4_2_3_line_81 | NAYY 4x150 SE | 71 | 73 | 0.003419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_5402-4_2_3_line_82 | NAYY 4x150 SE | 73 | 74 | 0.040962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_5402-4_2_3_line_83 | NAYY 4x150 SE | 73 | 75 | 0.017348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_5402-4_2_3_line_84 | NAYY 4x150 SE | 74 | 77 | 0.046047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_5402-4_2_3_line_85 | NAYY 4x150 SE | 75 | 78 | 0.07276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_5402-4_2_3_line_86 | NAYY 4x150 SE | 76 | 79 | 0.037853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_5402-4_2_3_line_87 | NAYY 4x150 SE | 77 | 95 | 0.017776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_5402-4_2_3_line_88 | NAYY 4x150 SE | 78 | 102 | 0.020631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_5402-4_2_3_line_89 | NAYY 4x150 SE | 78 | 103 | 0.066301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_5402-4_2_3_line_90 | NAYY 4x150 SE | 79 | 150 | 0.0091049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_5402-4_2_3_line_91 | NAYY 4x150 SE | 80 | 81 | 0.0028867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_5402-4_2_3_line_92 | NAYY 4x150 SE | 80 | 82 | 0.017879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_5402-4_2_3_line_93 | NAYY 4x150 SE | 81 | 83 | 0.031712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_5402-4_2_3_line_94 | NAYY 4x150 SE | 82 | 84 | 0.0069188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_5402-4_2_3_line_95 | NAYY 4x150 SE | 83 | 85 | 0.071424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_5402-4_2_3_line_96 | NAYY 4x150 SE | 83 | 86 | 0.025156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_5402-4_2_3_line_97 | NAYY 4x150 SE | 84 | 87 | 0.0085884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_5402-4_2_3_line_98 | NAYY 4x150 SE | 86 | 88 | 0.043485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_5402-4_2_3_line_99 | NAYY 4x150 SE | 88 | 95 | 0.032097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_5402-4_2_3_line_100 | NAYY 4x150 SE | 89 | 90 | 0.045066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_5402-4_2_3_line_101 | NAYY 4x150 SE | 90 | 91 | 0.013524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_5402-4_2_3_line_102 | NAYY 4x150 SE | 91 | 92 | 0.030576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_5402-4_2_3_line_103 | NAYY 4x150 SE | 92 | 93 | 0.073009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_5402-4_2_3_line_104 | NAYY 4x150 SE | 92 | 94 | 0.01198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_5402-4_2_3_line_105 | NAYY 4x150 SE | 93 | 121 | 0.01278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_5402-4_2_3_line_106 | NAYY 4x150 SE | 94 | 116 | 0.1605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_5402-4_2_3_line_107 | NAYY 4x150 SE | 94 | 113 | 0.099037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_5402-4_2_3_line_108 | NAYY 4x150 SE | 95 | 96 | 0.037858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_5402-4_2_3_line_109 | NAYY 4x150 SE | 96 | 100 | 0.0097716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_5402-4_2_3_line_110 | NAYY 4x150 SE | 96 | 101 | 0.062412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_5402-4_2_3_line_111 | NAYY 4x150 SE | 97 | 98 | 0.027812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_5402-4_2_3_line_112 | NAYY 4x150 SE | 97 | 99 | 0.022754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_5402-4_2_3_line_113 | NAYY 4x150 SE | 98 | 155 | 0.0050466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_5402-4_2_3_line_114 | NAYY 4x150 SE | 99 | 129 | 0.032758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_5402-4_2_3_line_115 | NAYY 4x150 SE | 103 | 104 | 0.045618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_5402-4_2_3_line_116 | NAYY 4x150 SE | 103 | 105 | 0.076023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_5402-4_2_3_line_117 | NAYY 4x150 SE | 105 | 106 | 0.025127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_5402-4_2_3_line_118 | NAYY 4x150 SE | 106 | 162 | 0.08114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_5402-4_2_3_line_119 | NAYY 4x150 SE | 107 | 108 | 0.013566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_5402-4_2_3_line_120 | NAYY 4x150 SE | 108 | 109 | 0.034145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_5402-4_2_3_line_121 | NAYY 4x150 SE | 108 | 110 | 0.008084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
122 | LV_5402-4_2_3_line_122 | NAYY 4x150 SE | 109 | 128 | 0.0097226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_5402-4_2_3_line_123 | NAYY 4x150 SE | 110 | 152 | 0.034141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_5402-4_2_3_line_124 | NAYY 4x150 SE | 110 | 151 | 0.0075299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_5402-4_2_3_line_125 | NAYY 4x150 SE | 111 | 125 | 0.015595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_5402-4_2_3_line_126 | NAYY 4x150 SE | 112 | 124 | 0.01257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_5402-4_2_3_line_127 | NAYY 4x150 SE | 112 | 122 | 0.031003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_5402-4_2_3_line_128 | NAYY 4x150 SE | 113 | 114 | 0.044146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_5402-4_2_3_line_129 | NAYY 4x150 SE | 114 | 115 | 0.085674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_5402-4_2_3_line_130 | NAYY 4x150 SE | 115 | 117 | 0.048774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_5402-4_2_3_line_131 | NAYY 4x150 SE | 117 | 118 | 0.039043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_5402-4_2_3_line_132 | NAYY 4x150 SE | 117 | 119 | 0.014573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_5402-4_2_3_line_133 | NAYY 4x150 SE | 117 | 120 | 0.015217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_5402-4_2_3_line_134 | NAYY 4x150 SE | 118 | 138 | 0.030302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_5402-4_2_3_line_135 | NAYY 4x150 SE | 119 | 139 | 0.011661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_5402-4_2_3_line_136 | NAYY 4x150 SE | 120 | 127 | 0.039944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
137 | LV_5402-4_2_3_line_137 | NAYY 4x150 SE | 122 | 123 | 0.0043423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
138 | LV_5402-4_2_3_line_138 | NAYY 4x150 SE | 125 | 126 | 0.022545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_5402-4_2_3_line_139 | NAYY 4x150 SE | 125 | 127 | 0.022343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
140 | LV_5402-4_2_3_line_140 | NAYY 4x150 SE | 126 | 135 | 0.042409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_5402-4_2_3_line_141 | NAYY 4x150 SE | 129 | 131 | 0.028165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_5402-4_2_3_line_142 | NAYY 4x150 SE | 130 | 132 | 0.045345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_5402-4_2_3_line_143 | NAYY 4x150 SE | 131 | 133 | 0.021997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_5402-4_2_3_line_144 | NAYY 4x150 SE | 132 | 134 | 0.053543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_5402-4_2_3_line_145 | NAYY 4x150 SE | 133 | 156 | 0.0032408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_5402-4_2_3_line_146 | NAYY 4x150 SE | 134 | 145 | 0.01592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_5402-4_2_3_line_147 | NAYY 4x150 SE | 136 | 137 | 0.0024503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
148 | LV_5402-4_2_3_line_148 | NAYY 4x150 SE | 137 | 141 | 0.037528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
149 | LV_5402-4_2_3_line_149 | NAYY 4x150 SE | 139 | 140 | 0.061392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_5402-4_2_3_line_150 | NAYY 4x150 SE | 140 | 144 | 0.0062655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_5402-4_2_3_line_151 | NAYY 4x150 SE | 141 | 142 | 0.009257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
152 | LV_5402-4_2_3_line_152 | NAYY 4x150 SE | 142 | 143 | 0.0051363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
153 | LV_5402-4_2_3_line_153 | NAYY 4x150 SE | 143 | 151 | 0.021802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
154 | LV_5402-4_2_3_line_154 | NAYY 4x150 SE | 145 | 146 | 0.12038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_5402-4_2_3_line_155 | NAYY 4x150 SE | 146 | 166 | 0.018017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_5402-4_2_3_line_156 | NAYY 4x150 SE | 147 | 148 | 0.016563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_5402-4_2_3_line_157 | NAYY 4x150 SE | 147 | 149 | 0.010962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_5402-4_2_3_line_158 | NAYY 4x150 SE | 148 | 150 | 0.023793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_5402-4_2_3_line_159 | NAYY 4x150 SE | 152 | 153 | 0.18497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_5402-4_2_3_line_160 | NAYY 4x150 SE | 153 | 154 | 0.069756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_5402-4_2_3_line_161 | NAYY 4x150 SE | 157 | 158 | 0.015584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_5402-4_2_3_line_162 | NAYY 4x150 SE | 158 | 160 | 0.017427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_5402-4_2_3_line_163 | NAYY 4x150 SE | 158 | 162 | 0.025358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_5402-4_2_3_line_164 | NAYY 4x150 SE | 159 | 160 | 0.0053928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_5402-4_2_3_line_165 | NAYY 4x150 SE | 159 | 161 | 0.03045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_5402-4_2_3_line_166 | NAYY 4x150 SE | 162 | 163 | 0.014613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_5402-4_2_3_line_167 | NAYY 4x150 SE | 165 | 166 | 0.10642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_5402-4_2_3_line_168 | NAYY 4x150 SE | 165 | 167 | 0.013815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_5402-4_2_3_line_169 | NAYY 4x150 SE | 165 | 168 | 0.1907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
170 | LV_5402-4_2_3_line_170 | NAYY 4x150 SE | 166 | 169 | 0.01041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_5402-4_2_3_line_171 | NAYY 4x150 SE | 168 | 174 | 0.059535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
172 | LV_5402-4_2_3_line_172 | NAYY 4x150 SE | 170 | 171 | 0.0047551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
173 | LV_5402-4_2_3_line_173 | NAYY 4x150 SE | 172 | 173 | 0.26388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5402-4_2_3_trafo_217 | 0.25 MVA 20/0.4 kV | 175 | 123 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2573310.6136 | 1122968.6747 | 2573322.4559 | 1122973.469
1 | 2573330.8696 | 1122976.8753 | 2573322.4559 | 1122973.469
2 | 2573301.5913 | 1122964.7544 | 2573307.3475 | 1122967.3524 | 2573310.6136 | 1122968.6747
3 | 2573330.8696 | 1122976.8753 | 2573327.5614 | 1122985.1404
4 | 2573330.8696 | 1122976.8753 | 2573340.328 | 1122980.7089
5 | 2573301.5913 | 1122964.7544 | 2573294.2695 | 1122962.1077 | 2573278.2558 | 1122960.9297
6 | 2573301.5913 | 1122964.7544 | 2573301.297 | 1122954.1601
7 | 2573327.5614 | 1122985.1404 | 2573325.9352 | 1122989.2033 | 2573325.4919 | 1122991.8399 | 2573326.2267 | 1122994.1044 | 2573327.5042 | 1122995.2771
8 | 2573375.1672 | 1122989.5992 | 2573364.4127 | 1122987.4101 | 2573341.9934 | 1122981.3839 | 2573340.328 | 1122980.7089
9 | 2573242.5698 | 1122964.4379 | 2573277.8783 | 1122960.9019 | 2573278.2558 | 1122960.9297
10 | 2573327.3372 | 1122999.3577 | 2573327.9684 | 1122997.3539 | 2573327.5042 | 1122995.2771
11 | 2573405.9042 | 1122988.5626 | 2573399.5509 | 1122989.0003 | 2573381.0371 | 1122990.794 | 2573375.1672 | 1122989.5992
12 | 2573242.5698 | 1122964.4379 | 2573245.6028 | 1122973.6958 | 2573249.0794 | 1122980.417 | 2573250.2577 | 1122987.0262
13 | 2573242.5698 | 1122964.4379 | 2573200.7434 | 1122965.7465
14 | 2573405.9042 | 1122988.5626 | 2573423.9742 | 1122987.3178
15 | 2574680.3704 | 1122343.3381 | 2574668.9619 | 1122321.1369 | 2574668.9619 | 1122321.1369
16 | 2574710.2816 | 1122317.4172 | 2574699.7969 | 1122307.2116 | 2574668.9619 | 1122321.1369
17 | 2574131.3707 | 1122712.8133 | 2574680.3704 | 1122343.3381
18 | 2574733.0002 | 1122365.1568 | 2574710.2816 | 1122317.4172
19 | 2574131.3707 | 1122712.8133 | 2574087.3394 | 1122716.4707 | 2574068.5792 | 1122720.3866 | 2574053.8974 | 1122724.1072 | 2574045.0117 | 1122725.3794 | 2574034.7724 | 1122731.0485 | 2574019.519 | 1122738.1066 | 2574015.3345 | 1122739.172
20 | 2574733.0002 | 1122365.1568 | 2574741.3897 | 1122392.5686 | 2574744.7528 | 1122414.8434 | 2574748.7986 | 1122430.7232 | 2574767.5031 | 1122420.5621 | 2574783.859 | 1122414.8798 | 2574798.5584 | 1122413.2731
21 | 2574798.5584 | 1122413.2731 | 2574802.9863 | 1122426.5168 | 2574809.7792 | 1122439.1613 | 2574822.6127 | 1122446.856 | 2574836.1574 | 1122462.3739 | 2574842.4981 | 1122479.4226 | 2574843.3586 | 1122486.0445 | 2574844.5459 | 1122495.2219 | 2574845.797 | 1122504.8992 | 2574843.3903 | 1122525.0637 | 2574833.8761 | 1122549.5156 | 2574825.8875 | 1122564.423 | 2574823.3577 | 1122572.8577
22 | 2574823.3577 | 1122572.8577 | 2574823.2636 | 1122573.1716
23 | 2573758.2217 | 1122920.5062 | 2573747.7573 | 1122927.4775 | 2573736.8728 | 1122932.3693
24 | 2573758.2217 | 1122920.5062 | 2573762.3429 | 1122910.6723 | 2573759.8049 | 1122894.4975 | 2573750.6079 | 1122880.8641 | 2573734.439 | 1122872.2969 | 2573723.5829 | 1122869.2907
25 | 2573723.1748 | 1122869.1777 | 2573723.5829 | 1122869.2907
26 | 2573726.2442 | 1122856.8582 | 2573725.6159 | 1122859.5623 | 2573724.0927 | 1122863.9267 | 2573723.1748 | 1122869.1777
27 | 2573723.1748 | 1122869.1777 | 2573717.315 | 1122867.5469 | 2573710.0185 | 1122861.8425 | 2573690.9912 | 1122845.0282 | 2573685.9008 | 1122841.1364
28 | 2573672.1671 | 1122830.6365 | 2573685.9008 | 1122841.1364
29 | 2573835.5993 | 1123719.2784 | 2573845.5338 | 1123723.7487 | 2573859.1899 | 1123729.459 | 2573865.4003 | 1123735.6685 | 2573883.2789 | 1123755.034 | 2573893.7132 | 1123760.9918 | 2573902.1564 | 1123764.7237 | 2573923.2661 | 1123766.4555 | 2573941.8923 | 1123766.2082 | 2573956.546 | 1123763.7326 | 2573969.4563 | 1123759.2524 | 2573974.4525 | 1123758.2753
30 | 2573835.5993 | 1123719.2784 | 2573834.9851 | 1123735.8671 | 2573834.9339 | 1123739.9671
31 | 2573835.5993 | 1123719.2784 | 2573573.6264 | 1123084.038
32 | 2573573.6264 | 1123084.038 | 2573599.9573 | 1123074.8514 | 2573615.7431 | 1123066.4337 | 2573627.4868 | 1123055.8771 | 2573643.3133 | 1123056.7306
33 | 2573363.822 | 1122897.1314 | 2573352.5598 | 1122892.9488 | 2573347.1341 | 1122890.1047 | 2573345.5167 | 1122889.4505
34 | 2573320.2004 | 1122879.2113 | 2573345.5167 | 1122889.4505
35 | 2573363.822 | 1122897.1314 | 2573383.2409 | 1122904.3432
36 | 2573299.8265 | 1122870.971 | 2573320.2004 | 1122879.2113
37 | 2573418.8965 | 1122917.5821 | 2573388.7379 | 1122906.3846 | 2573383.2409 | 1122904.3432
38 | 2573299.8265 | 1122870.971 | 2573298.9844 | 1122877.5669 | 2573300.5983 | 1122881.5618 | 2573300.5728 | 1122888.0651
39 | 2573299.8265 | 1122870.971 | 2573292.6728 | 1122867.9901 | 2573285.4632 | 1122864.1241
40 | 2573430.1526 | 1122921.7614 | 2573418.8965 | 1122917.5821
41 | 2573300.5728 | 1122888.0651 | 2573300.5272 | 1122899.7089
42 | 2573239.6512 | 1122831.5292 | 2573251.7935 | 1122837.8562 | 2573271.882 | 1122853.7084 | 2573282.2071 | 1122862.3781 | 2573285.4632 | 1122864.1241
43 | 2573430.1526 | 1122921.7614 | 2573440.8733 | 1122925.7418
44 | 2573239.6512 | 1122831.5292 | 2573207.3823 | 1122814.7196 | 2573204.2392 | 1122813.6664
45 | 2573239.6512 | 1122831.5292 | 2573250.7451 | 1122818.807 | 2573260.4576 | 1122795.9617
46 | 2573032.3748 | 1122919.4738 | 2573032.3748 | 1122919.4738 | 2573030.1102 | 1122926.921 | 2573029.9471 | 1122927.2331
47 | 2573018.3234 | 1122948.6353 | 2573026.2492 | 1122934.3086 | 2573029.9471 | 1122927.2331
48 | 2573032.3748 | 1122919.4738 | 2573029.8944 | 1122898.3059
49 | 2573017.3544 | 1122950.3868 | 2573018.3234 | 1122948.6353
50 | 2573029.8944 | 1122898.3059 | 2573027.735 | 1122879.877
51 | 2573017.3544 | 1122950.3868 | 2573012.0753 | 1122959.9292 | 2573010.2983 | 1122963.6653
52 | 2573022.6259 | 1122836.276 | 2573027.735 | 1122879.877
53 | 2573010.2983 | 1122963.6653 | 2573008.1488 | 1122968.1842 | 2573005.6128 | 1122978.7119 | 2573005.0712 | 1122983.4723 | 2573007.3858 | 1122987.2193 | 2573010.7148 | 1122990.1837 | 2573016.6693 | 1122992.2692 | 2573026.5576 | 1122992.9031 | 2573043.6716 | 1122990.8162
54 | 2573022.6259 | 1122836.276 | 2573017.3207 | 1122841.6942
55 | 2573022.6259 | 1122836.276 | 2573040.2216 | 1122815.3091
56 | 2573087.5028 | 1122985.4605 | 2573075.3878 | 1122986.9486 | 2573043.6716 | 1122990.8162
57 | 2573543.2513 | 1122887.5152 | 2573551.7878 | 1122895.6288 | 2573562.0389 | 1122905.1219 | 2573572.5372 | 1122912.9576 | 2573584.5566 | 1122919.5193 | 2573588.4117 | 1122921.1258
58 | 2573590.3119 | 1122921.9176 | 2573588.4117 | 1122921.1258
59 | 2573534.1341 | 1122879.1425 | 2573541.7988 | 1122886.1346 | 2573543.2513 | 1122887.5152
60 | 2573534.1341 | 1122879.1425 | 2573551.7001 | 1122864.3559
61 | 2573534.1341 | 1122879.1425 | 2573526.5205 | 1122885.5569 | 2573525.8615 | 1122886.2845
62 | 2573559.2644 | 1122857.9884 | 2573551.7001 | 1122864.3559
63 | 2573497.398 | 1122917.7108 | 2573525.8615 | 1122886.2845
64 | 2573559.2644 | 1122857.9884 | 2573560.3705 | 1122857.0164 | 2573570.5518 | 1122851.2815
65 | 2573545.971 | 1122840.5492 | 2573546.9731 | 1122842.2345 | 2573554.6178 | 1122851.7057 | 2573559.2644 | 1122857.9884
66 | 2573497.398 | 1122917.7108 | 2573491.1901 | 1122924.5648 | 2573489.9951 | 1122926.4828
67 | 2573200.7434 | 1122965.7465 | 2573203.6722 | 1122982.7864 | 2573207.758 | 1122984.2912
68 | 2573200.7434 | 1122965.7465 | 2573193.0035 | 1122966.17 | 2573159.168 | 1122967.9992 | 2573151.5622 | 1122969.1113 | 2573149.8735 | 1122969.6169
69 | 2573092.6307 | 1122984.3779 | 2573124.4036 | 1122977.6699 | 2573142.9297 | 1122971.6955 | 2573148.8711 | 1122969.9169
70 | 2573087.5028 | 1122985.4605 | 2573092.6307 | 1122984.3779
71 | 2573149.8735 | 1122969.6169 | 2573148.8711 | 1122969.9169
72 | 2573087.5028 | 1122985.4605 | 2573079.2848 | 1122994.5239 | 2573071.0651 | 1123001.4752 | 2573050.2119 | 1123012.9296 | 2573026.4269 | 1123020.5619 | 2573008.8076 | 1123022.3305 | 2572995.9386 | 1123020.7206 | 2572969.157 | 1123013.5147 | 2572953.8878 | 1123011.4599 | 2572944.94 | 1123012.334
73 | 2572944.94 | 1123012.334 | 2572941.8409 | 1123012.6368 | 2572918.0585 | 1123019.1023 | 2572902.4877 | 1123020.2728 | 2572852.2722 | 1123016.4522 | 2572802.8602 | 1123014.6698
74 | 2572802.8602 | 1123014.6698 | 2572787.0733 | 1123014.1004 | 2572763.3845 | 1123014.4778
75 | 2572802.8602 | 1123014.6698 | 2572790.2337 | 1123140.3046
76 | 2572687.2262 | 1123026.0023 | 2572706.6064 | 1123018.5106 | 2572731.5662 | 1123014.9848 | 2572763.3845 | 1123014.4778
77 | 2572808.2324 | 1123164.6022 | 2572818.077 | 1123169.2935 | 2572819.0656 | 1123169.6559 | 2572819.5769 | 1123168.4641 | 2572817.857 | 1123164.9701 | 2572815.2863 | 1123157.4557 | 2572813.0912 | 1123152.8744 | 2572809.5627 | 1123150.1112 | 2572801.4869 | 1123147.8242 | 2572794.8021 | 1123144.5083 | 2572790.4452 | 1123141.0262 | 2572790.2337 | 1123140.3046
78 | 2573075.6039 | 1122848.3869 | 2573074.2411 | 1122845.8724 | 2573055.683 | 1122829.1997
79 | 2573040.2216 | 1122815.3091 | 2573055.683 | 1122829.1997
80 | 2573077.9903 | 1122877.3046 | 2573080.4271 | 1122865.2322 | 2573079.5904 | 1122855.7423 | 2573075.6039 | 1122848.3869
81 | 2573042.4075 | 1122812.6758 | 2573040.2216 | 1122815.3091
82 | 2573042.4075 | 1122812.6758 | 2573065.0846 | 1122778.5634
83 | 2573042.4075 | 1122812.6758 | 2573026.635 | 1122805.4514
84 | 2573065.0846 | 1122778.5634 | 2573082.2919 | 1122752.6789 | 2573093.3991 | 1122742.65
85 | 2572959.328 | 1122824.9427 | 2572983.825 | 1122819.4524 | 2572992.7654 | 1122814.9879 | 2573005.9291 | 1122806.5359 | 2573013.1302 | 1122802.8129 | 2573023.059 | 1122803.8135 | 2573026.635 | 1122805.4514
86 | 2573017.3207 | 1122841.6942 | 2573003.0673 | 1122856.2512 | 2572991.6648 | 1122869.4996
87 | 2573106.5925 | 1122730.7374 | 2573093.3991 | 1122742.65
88 | 2572959.328 | 1122824.9427 | 2572961.9028 | 1122845.408
89 | 2572959.328 | 1122824.9427 | 2572950.5461 | 1122826.9052 | 2572943.592 | 1122832.3725 | 2572929.6861 | 1122845.5303 | 2572918.2608 | 1122852.9853 | 2572910.0183 | 1122860.0036 | 2572907.0442 | 1122863.9745
90 | 2572991.6648 | 1122869.4996 | 2572985.7254 | 1122876.4005
91 | 2572989.4797 | 1122700.1713 | 2572988.0452 | 1122697.6663
92 | 2572974.5987 | 1122686.1495 | 2572978.7417 | 1122688.3209 | 2572983.5757 | 1122693.2462 | 2572987.8584 | 1122697.3402 | 2572988.0452 | 1122697.6663
93 | 2573010.4332 | 1122722.2738 | 2573005.0264 | 1122720.3081 | 2573000.4661 | 1122716.2153 | 2572994.9441 | 1122710.8819 | 2572991.8933 | 1122706.371 | 2572990.9128 | 1122702.6736 | 2572989.4797 | 1122700.1713
94 | 2572974.5987 | 1122686.1495 | 2572976.2474 | 1122684.0856 | 2572976.637 | 1122679.8261
95 | 2572943.5885 | 1122743.9618 | 2572958.9907 | 1122734.2657 | 2572970.661 | 1122728.0658 | 2573010.4332 | 1122722.2738
96 | 2573010.4332 | 1122722.2738 | 2573023.8036 | 1122720.3352 | 2573035.328 | 1122718.6581
97 | 2572976.637 | 1122679.8261 | 2572975.514 | 1122675.3067 | 2572973.8478 | 1122671.7457
98 | 2573035.328 | 1122718.6581 | 2573068.0147 | 1122713.9011 | 2573075.714 | 1122714.656 | 2573078.1244 | 1122715.9113
99 | 2573106.5925 | 1122730.7374 | 2573078.1244 | 1122715.9113
100 | 2574015.3345 | 1122739.172 | 2573994.4694 | 1122744.4844 | 2573975.5691 | 1122744.477 | 2573971.0421 | 1122745.4721
101 | 2573957.8331 | 1122748.3756 | 2573971.0421 | 1122745.4721
102 | 2573929.109 | 1122758.8292 | 2573956.8947 | 1122748.5819 | 2573957.8331 | 1122748.3756
103 | 2573929.109 | 1122758.8292 | 2573935.7914 | 1122749.1511 | 2573940.2019 | 1122738.3711 | 2573944.596 | 1122725.5791 | 2573950.0609 | 1122719.6637 | 2573959.1733 | 1122715.5556 | 2573970.3306 | 1122715.3295 | 2573977.0091 | 1122716.9231
104 | 2573929.109 | 1122758.8292 | 2573918.4373 | 1122764.3336
105 | 2573977.0091 | 1122716.9231 | 2573979.8948 | 1122717.6116 | 2573987.4076 | 1122718.0683 | 2573989.5132 | 1122718.9586
106 | 2573918.4373 | 1122764.3336 | 2573912.7205 | 1122770.8283 | 2573886.1679 | 1122796.8895 | 2573865.5992 | 1122819.3564 | 2573845.532 | 1122840.0537 | 2573838.8725 | 1122849.6206 | 2573836.7305 | 1122855.3439 | 2573836.5651 | 1122861.6477 | 2573840.2292 | 1122867.2902 | 2573846.371 | 1122871.7102 | 2573853.461 | 1122874.2919 | 2573858.0534 | 1122873.5049 | 2573862.6329 | 1122871.5174
107 | 2573918.4373 | 1122764.3336 | 2573914.9903 | 1122766.1161 | 2573886.9859 | 1122775.6754 | 2573859.2039 | 1122781.3763 | 2573844.2932 | 1122782.0302 | 2573832.2864 | 1122780.1591 | 2573822.4734 | 1122777.6527
108 | 2573106.5925 | 1122730.7374 | 2573112.0533 | 1122734.4594 | 2573114.9025 | 1122728.377 | 2573121.5436 | 1122716.6415 | 2573124.2513 | 1122711.6937 | 2573126.3111 | 1122706.6931
109 | 2573126.3111 | 1122706.6931 | 2573126.4608 | 1122702.2124 | 2573125.8214 | 1122697.1683 | 2573125.8165 | 1122696.9644
110 | 2573126.3111 | 1122706.6931 | 2573133.5646 | 1122712.9639 | 2573141.4028 | 1122718.9431 | 2573156.4877 | 1122729.6813 | 2573172.875 | 1122740.2692 | 2573177.8014 | 1122740.6144
111 | 2573151.6011 | 1122796.0361 | 2573155.2164 | 1122788.8164 | 2573157.1219 | 1122783.8054 | 2573159.3022 | 1122781.6169 | 2573162.5159 | 1122781.2135 | 2573166.8944 | 1122782.6058 | 2573170.1392 | 1122783.7883
112 | 2573151.6011 | 1122796.0361 | 2573173.1775 | 1122803.2628
113 | 2573174.8808 | 1122785.5162 | 2573170.1392 | 1122783.7883
114 | 2573204.2392 | 1122813.6664 | 2573173.1775 | 1122803.2628
115 | 2572879.9394 | 1122829.6458 | 2572883.2733 | 1122830.2534 | 2572889.9475 | 1122834.5811 | 2572894.3315 | 1122838.908 | 2572897.2665 | 1122845.1201 | 2572901.0541 | 1122854.0075 | 2572907.0442 | 1122863.9745
116 | 2572907.0442 | 1122863.9745 | 2572899.4941 | 1122874.069 | 2572890.9109 | 1122880.7775 | 2572876.237 | 1122886.0017 | 2572854.4302 | 1122887.7562 | 2572843.2064 | 1122891.9644 | 2572840.6242 | 1122893.649
117 | 2572819.5796 | 1122907.3784 | 2572840.6242 | 1122893.649
118 | 2572819.5796 | 1122907.3784 | 2572813.2064 | 1122899.67 | 2572809.9579 | 1122894.0819 | 2572806.5891 | 1122880.6126 | 2572800.1549 | 1122871.3814 | 2572782.817 | 1122855.2627 | 2572776.4476 | 1122845.0308 | 2572774.4739 | 1122841.6936
119 | 2573482.821 | 1122937.9972 | 2573489.9951 | 1122926.4828
120 | 2573482.821 | 1122937.9972 | 2573478.4317 | 1122937.6051 | 2573463.1558 | 1122934.015 | 2573449.9879 | 1122929.126
121 | 2573485.8921 | 1122945.4763 | 2573482.821 | 1122937.9972
122 | 2573449.9879 | 1122929.126 | 2573440.8733 | 1122925.7418
123 | 2573485.8921 | 1122945.4763 | 2573507.8136 | 1122955.7851 | 2573516.0652 | 1122961.2852
124 | 2573485.8921 | 1122945.4763 | 2573486.0156 | 1122950.7784 | 2573485.5296 | 1122952.951
125 | 2573584.1393 | 1122843.6279 | 2573570.5518 | 1122851.2815
126 | 2573545.971 | 1122840.5492 | 2573539.36 | 1122843.4907 | 2573535.1953 | 1122846.8662
127 | 2573545.971 | 1122840.5492 | 2573543.5472 | 1122836.48 | 2573538.9612 | 1122826.4284 | 2573531.4391 | 1122818.5464 | 2573529.0459 | 1122814.9466
128 | 2573822.4734 | 1122777.6527 | 2573815.1253 | 1122775.7758 | 2573785.6228 | 1122772.4023 | 2573778.8883 | 1122773.7444
129 | 2573694.1815 | 1122784.5051 | 2573699.9607 | 1122783.4807 | 2573731.073 | 1122782.9115 | 2573756.3686 | 1122778.2324 | 2573778.8883 | 1122773.7444
130 | 2573648.1752 | 1122800.0928 | 2573667.194 | 1122791.9279 | 2573682.6007 | 1122786.558 | 2573694.1815 | 1122784.5051
131 | 2573648.1752 | 1122800.0928 | 2573654.857 | 1122806.2666 | 2573661.6653 | 1122814.9301 | 2573671.1535 | 1122829.8517 | 2573672.1671 | 1122830.6365
132 | 2573648.1752 | 1122800.0928 | 2573641.9185 | 1122786.9309
133 | 2573648.1752 | 1122800.0928 | 2573638.5156 | 1122805.9601 | 2573635.3615 | 1122808.2793
134 | 2573672.1671 | 1122830.6365 | 2573667.4872 | 1122836.1152 | 2573665.5907 | 1122839.7475 | 2573666.1501 | 1122842.4687 | 2573670.5335 | 1122846.8073 | 2573677.8432 | 1122853.7566
135 | 2573641.9185 | 1122786.9309 | 2573638.0342 | 1122778.7598 | 2573636.4567 | 1122776.676
136 | 2573603.4679 | 1122832.3265 | 2573627.0935 | 1122814.3587 | 2573635.3615 | 1122808.2793
137 | 2573526.6419 | 1122811.3305 | 2573529.0459 | 1122814.9466
138 | 2573584.1393 | 1122843.6279 | 2573599.2157 | 1122860.3904
139 | 2573603.4679 | 1122832.3265 | 2573590.4238 | 1122840.0875 | 2573584.1393 | 1122843.6279
140 | 2573623.869 | 1122893.401 | 2573624.3696 | 1122891.4978 | 2573623.7151 | 1122888.188 | 2573621.1478 | 1122884.7753 | 2573599.2157 | 1122860.3904
141 | 2573204.2392 | 1122813.6664 | 2573204.073 | 1122816.1684 | 2573205.1844 | 1122821.6106 | 2573206.3189 | 1122830.4877 | 2573206.5361 | 1122837.7348 | 2573207.2414 | 1122841.5741
142 | 2573278.1961 | 1122754.2309 | 2573276.5322 | 1122758.118 | 2573270.0845 | 1122773.5098 | 2573264.6804 | 1122786.0289 | 2573260.4576 | 1122795.9617
143 | 2573222.4739 | 1122856.5468 | 2573216.426 | 1122852.5649 | 2573210.2124 | 1122847.7012 | 2573207.4686 | 1122842.811 | 2573207.2414 | 1122841.5741
144 | 2573278.1961 | 1122754.2309 | 2573304.7276 | 1122758.7935 | 2573331.4637 | 1122757.2967
145 | 2573225.1807 | 1122858.3289 | 2573222.4739 | 1122856.5468
146 | 2573331.4637 | 1122757.2967 | 2573335.4925 | 1122751.1092 | 2573340.6908 | 1122744.3384
147 | 2573426.4187 | 1122987.1494 | 2573423.9742 | 1122987.3178
148 | 2573426.4187 | 1122987.1494 | 2573438.3408 | 1122986.328 | 2573451.3835 | 1122983.6026 | 2573462.6217 | 1122979.1064 | 2573462.7543 | 1122979.0382
149 | 2573592.1813 | 1122736.4519 | 2573603.477 | 1122753.3872 | 2573614.8866 | 1122759.7293 | 2573630.1075 | 1122768.2892 | 2573636.4567 | 1122776.676
150 | 2573588.7046 | 1122731.2394 | 2573592.1813 | 1122736.4519
151 | 2573470.9846 | 1122974.8009 | 2573470.9846 | 1122974.8009 | 2573462.7543 | 1122979.0382
152 | 2573470.9846 | 1122974.8009 | 2573474.9245 | 1122971.5056
153 | 2573485.5296 | 1122952.951 | 2573484.8284 | 1122956.0862 | 2573481.8211 | 1122963.1141 | 2573477.4919 | 1122969.3584 | 2573474.9245 | 1122971.5056
154 | 2573340.6908 | 1122744.3384 | 2573350.1049 | 1122737.0487 | 2573362.451 | 1122730.1352 | 2573373.0164 | 1122725.1194 | 2573377.971 | 1122720.7731 | 2573383.1677 | 1122711.8568 | 2573388.7269 | 1122699.4928 | 2573397.9799 | 1122687.1125 | 2573409.6613 | 1122672.8206 | 2573414.6064 | 1122666.3066 | 2573415.6793 | 1122656.3001
155 | 2573416.1409 | 1122638.3193 | 2573416.3248 | 1122650.28 | 2573415.6793 | 1122656.3001
156 | 2572955.948 | 1122900.9293 | 2572971.2455 | 1122894.5795
157 | 2572945.8231 | 1122905.132 | 2572955.948 | 1122900.9293
158 | 2572971.2455 | 1122894.5795 | 2572971.2455 | 1122894.5795 | 2572978.8462 | 1122888.8537 | 2572984.3955 | 1122877.9456 | 2572985.7254 | 1122876.4005
159 | 2573678.4989 | 1123041.0136 | 2573673.8371 | 1123038.2436 | 2573625.5935 | 1123024.9589 | 2573603.8528 | 1123020.6185 | 2573580.938 | 1123005.2556 | 2573566.846 | 1122999.0365 | 2573557.1917 | 1122990.2078 | 2573547.3446 | 1122986.6492 | 2573541.3157 | 1122978.1158 | 2573516.0652 | 1122961.2852
160 | 2573643.3133 | 1123056.7306 | 2573645.9167 | 1123061.3548 | 2573645.1155 | 1123066.8277 | 2573647.5044 | 1123070.0078 | 2573651.9544 | 1123070.1995 | 2573663.0687 | 1123056.7443 | 2573671.7325 | 1123052.4821 | 2573680.6338 | 1123054.9223 | 2573680.3977 | 1123048.5312 | 2573678.4989 | 1123041.0136 | 2573678.4989 | 1123041.0136
161 | 2572769.65 | 1122816.8029 | 2572763.7162 | 1122815.9404 | 2572758.4431 | 1122814.5524 | 2572755.9837 | 1122811.2285
162 | 2572769.65 | 1122816.8029 | 2572765.4424 | 1122799.8911
163 | 2572769.65 | 1122816.8029 | 2572774.4739 | 1122841.6936
164 | 2572764.0828 | 1122794.6726 | 2572765.2518 | 1122799.1251 | 2572765.4424 | 1122799.8911
165 | 2572773.2846 | 1122766.1613 | 2572763.9356 | 1122787.7031 | 2572764.0828 | 1122794.6726
166 | 2572774.4739 | 1122841.6936 | 2572760.3806 | 1122845.7036
167 | 2573416.1409 | 1122638.3193 | 2573424.5744 | 1122639.4271 | 2573435.7668 | 1122640.1448 | 2573452.7617 | 1122643.405 | 2573462.1625 | 1122645.2868 | 2573465.2011 | 1122647.0965 | 2573470.5011 | 1122652.8761 | 2573475.0678 | 1122658.481 | 2573479.8145 | 1122661.1837 | 2573487.0989 | 1122664.0531 | 2573499.2952 | 1122665.0889 | 2573504.5776 | 1122666.8777 | 2573507.6865 | 1122670.666 | 2573507.9681 | 1122675.848
168 | 2573512.8625 | 1122688.5966 | 2573510.2979 | 1122684.0723 | 2573508.0809 | 1122677.9234 | 2573507.9681 | 1122675.848
169 | 2573507.9681 | 1122675.848 | 2573583.3384 | 1122500.6718
170 | 2573416.1409 | 1122638.3193 | 2573405.7393 | 1122637.8956
171 | 2573583.3384 | 1122500.6718 | 2573583.8863 | 1122499.0019 | 2573588.0246 | 1122498.3612 | 2573594.0236 | 1122499.9802 | 2573605.0904 | 1122500.143 | 2573611.6007 | 1122498.7694 | 2573621.5268 | 1122497.2919 | 2573632.2874 | 1122497.9563 | 2573640.3694 | 1122501.5339
172 | 2572682.7909 | 1123027.7169 | 2572687.2262 | 1123026.0023
173 | 2572808.2324 | 1123164.6022 | 2572940.1268 | 1123393.1533

## bus_geodata
| x | y | coords
0 | 2573322.4559 | 1122973.469
1 | 2573310.6136 | 1122968.6747
2 | 2573330.8696 | 1122976.8753
3 | 2573301.5913 | 1122964.7544
4 | 2573327.5614 | 1122985.1404
5 | 2573340.328 | 1122980.7089
6 | 2573278.2558 | 1122960.9297
7 | 2573301.297 | 1122954.1601
8 | 2573327.5042 | 1122995.2771
9 | 2573375.1672 | 1122989.5992
10 | 2573242.5698 | 1122964.4379
11 | 2573327.3372 | 1122999.3577
12 | 2573405.9042 | 1122988.5626
13 | 2574668.9619 | 1122321.1369
14 | 2574680.3704 | 1122343.3381
15 | 2574710.2816 | 1122317.4172
16 | 2574131.3707 | 1122712.8133
17 | 2574733.0002 | 1122365.1568
18 | 2574798.5584 | 1122413.2731
19 | 2574823.3577 | 1122572.8577
20 | 2573736.8728 | 1122932.3693
21 | 2573758.2217 | 1122920.5062
22 | 2573723.5829 | 1122869.2907
23 | 2573723.1748 | 1122869.1777
24 | 2573726.2442 | 1122856.8582
25 | 2573685.9008 | 1122841.1364
26 | 2573974.4525 | 1123758.2753
27 | 2573835.5993 | 1123719.2784
28 | 2573834.9339 | 1123739.9671
29 | 2573573.6264 | 1123084.038
30 | 2573345.5167 | 1122889.4505
31 | 2573363.822 | 1122897.1314
32 | 2573320.2004 | 1122879.2113
33 | 2573383.2409 | 1122904.3432
34 | 2573299.8265 | 1122870.971
35 | 2573418.8965 | 1122917.5821
36 | 2573300.5728 | 1122888.0651
37 | 2573285.4632 | 1122864.1241
38 | 2573430.1526 | 1122921.7614
39 | 2573300.5272 | 1122899.7089
40 | 2573239.6512 | 1122831.5292
41 | 2573029.9471 | 1122927.2331
42 | 2573032.3748 | 1122919.4738
43 | 2573018.3234 | 1122948.6353
44 | 2573029.8944 | 1122898.3059
45 | 2573017.3544 | 1122950.3869
46 | 2573027.735 | 1122879.877
47 | 2573010.2983 | 1122963.6653
48 | 2573022.6259 | 1122836.276
49 | 2573043.6716 | 1122990.8162
50 | 2573588.4117 | 1122921.1258
51 | 2573543.2513 | 1122887.5152
52 | 2573590.3119 | 1122921.9176
53 | 2573534.1341 | 1122879.1425
54 | 2573551.7001 | 1122864.3559
55 | 2573525.8615 | 1122886.2845
56 | 2573559.2644 | 1122857.9884
57 | 2573497.398 | 1122917.7108
58 | 2573250.2577 | 1122987.0262
59 | 2573200.7434 | 1122965.7465
60 | 2573092.6307 | 1122984.3779
61 | 2573148.8711 | 1122969.9169
62 | 2573087.5028 | 1122985.4605
63 | 2573149.8735 | 1122969.6169
64 | 2572944.94 | 1123012.334
65 | 2572802.8602 | 1123014.6699
66 | 2573207.758 | 1122984.2912
67 | 2572763.3845 | 1123014.4778
68 | 2572790.2337 | 1123140.3046
69 | 2573055.683 | 1122829.1997
70 | 2573075.6039 | 1122848.3869
71 | 2573040.2216 | 1122815.3091
72 | 2573077.9903 | 1122877.3046
73 | 2573042.4075 | 1122812.6758
74 | 2573065.0846 | 1122778.5634
75 | 2573026.635 | 1122805.4514
76 | 2573017.3207 | 1122841.6942
77 | 2573093.3991 | 1122742.65
78 | 2572959.328 | 1122824.9427
79 | 2572991.6648 | 1122869.4996
80 | 2572988.0452 | 1122697.6663
81 | 2572989.4797 | 1122700.1713
82 | 2572974.5987 | 1122686.1495
83 | 2573010.4332 | 1122722.2738
84 | 2572976.637 | 1122679.8261
85 | 2572943.5885 | 1122743.9618
86 | 2573035.328 | 1122718.6581
87 | 2572973.8478 | 1122671.7457
88 | 2573078.1244 | 1122715.9113
89 | 2574015.3345 | 1122739.172
90 | 2573971.0421 | 1122745.4721
91 | 2573957.8331 | 1122748.3756
92 | 2573929.109 | 1122758.8292
93 | 2573977.0091 | 1122716.9231
94 | 2573918.4373 | 1122764.3336
95 | 2573106.5925 | 1122730.7374
96 | 2573126.3111 | 1122706.6931
97 | 2573151.6011 | 1122796.0361
98 | 2573170.1392 | 1122783.7883
99 | 2573173.1775 | 1122803.2628
100 | 2573125.8165 | 1122696.9644
101 | 2573177.8014 | 1122740.6144
102 | 2572961.9028 | 1122845.408
103 | 2572907.0442 | 1122863.9745
104 | 2572879.9393 | 1122829.6458
105 | 2572840.6242 | 1122893.649
106 | 2572819.5796 | 1122907.3784
107 | 2573489.9951 | 1122926.4828
108 | 2573482.821 | 1122937.9972
109 | 2573449.9879 | 1122929.126
110 | 2573485.8921 | 1122945.4763
111 | 2573570.5518 | 1122851.2815
112 | 2573545.971 | 1122840.5492
113 | 2573822.4734 | 1122777.6527
114 | 2573778.8883 | 1122773.7444
115 | 2573694.1815 | 1122784.5051
116 | 2573862.6329 | 1122871.5174
117 | 2573648.1752 | 1122800.0928
118 | 2573672.1671 | 1122830.6365
119 | 2573641.9185 | 1122786.9309
120 | 2573635.3615 | 1122808.2793
121 | 2573989.5132 | 1122718.9586
122 | 2573529.0459 | 1122814.9466
123 | 2573526.6419 | 1122811.3305
124 | 2573535.1953 | 1122846.8662
125 | 2573584.1393 | 1122843.6279
126 | 2573599.2157 | 1122860.3904
127 | 2573603.4679 | 1122832.3265
128 | 2573440.8733 | 1122925.7418
129 | 2573204.2392 | 1122813.6664
130 | 2573260.4576 | 1122795.9617
131 | 2573207.2414 | 1122841.5741
132 | 2573278.1961 | 1122754.2309
133 | 2573222.4739 | 1122856.5468
134 | 2573331.4637 | 1122757.2967
135 | 2573623.869 | 1122893.401
136 | 2573423.9742 | 1122987.3178
137 | 2573426.4187 | 1122987.1494
138 | 2573677.8432 | 1122853.7566
139 | 2573636.4567 | 1122776.676
140 | 2573592.1813 | 1122736.4519
141 | 2573462.7543 | 1122979.0382
142 | 2573470.9846 | 1122974.8009
143 | 2573474.9245 | 1122971.5056
144 | 2573588.7046 | 1122731.2394
145 | 2573340.6908 | 1122744.3384
146 | 2573415.6793 | 1122656.3001
147 | 2572955.948 | 1122900.9293
148 | 2572971.2455 | 1122894.5795
149 | 2572945.8231 | 1122905.132
150 | 2572985.7254 | 1122876.4005
151 | 2573485.5296 | 1122952.951
152 | 2573516.0652 | 1122961.2852
153 | 2573678.4989 | 1123041.0136
154 | 2573643.3133 | 1123056.7306
155 | 2573174.8808 | 1122785.5162
156 | 2573225.1807 | 1122858.329
157 | 2572755.9837 | 1122811.2285
158 | 2572769.65 | 1122816.8029
159 | 2572764.0828 | 1122794.6726
160 | 2572765.4424 | 1122799.8911
161 | 2572773.2846 | 1122766.1613
162 | 2572774.4739 | 1122841.6936
163 | 2572760.3806 | 1122845.7036
164 | 2574823.2636 | 1122573.1716
165 | 2573507.9681 | 1122675.848
166 | 2573416.1409 | 1122638.3193
167 | 2573512.8625 | 1122688.5966
168 | 2573583.3384 | 1122500.6718
169 | 2573405.7393 | 1122637.8956
170 | 2572687.2262 | 1123026.0023
171 | 2572682.7909 | 1123027.7169
172 | 2572808.2324 | 1123164.6022
173 | 2572940.1268 | 1123393.1533
174 | 2573640.3694 | 1122501.5338
175 | 2573545.971 | 1122840.5492

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1