## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5402-6_1_2_node_131 | 0.4 | n |  | TRUE
1 | bus_LV_5402-6_1_2_node_132 | 0.4 | n |  | TRUE
2 | bus_LV_5402-6_1_2_node_141 | 0.4 | n |  | TRUE
3 | bus_LV_5402-6_1_2_node_123 | 0.4 | n |  | TRUE
4 | bus_LV_5402-6_1_2_node_45 | 0.4 | n |  | TRUE
5 | bus_LV_5402-6_1_2_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_5402-6_1_2_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_5402-6_1_2_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_5402-6_1_2_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_5402-6_1_2_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_5402-6_1_2_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_5402-6_1_2_node_51 | 0.4 | n |  | TRUE
12 | bus_LV_5402-6_1_2_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_5402-6_1_2_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_5402-6_1_2_node_56 | 0.4 | n |  | TRUE
15 | bus_LV_5402-6_1_2_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_5402-6_1_2_node_122 | 0.4 | n |  | TRUE
17 | bus_LV_5402-6_1_2_node_119 | 0.4 | n |  | TRUE
18 | bus_LV_5402-6_1_2_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_5402-6_1_2_node_57 | 0.4 | n |  | TRUE
20 | bus_LV_5402-6_1_2_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_5402-6_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_5402-6_1_2_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_5402-6_1_2_node_92 | 0.4 | n |  | TRUE
24 | bus_LV_5402-6_1_2_node_94 | 0.4 | n |  | TRUE
25 | bus_LV_5402-6_1_2_node_62 | 0.4 | n |  | TRUE
26 | bus_LV_5402-6_1_2_node_63 | 0.4 | n |  | TRUE
27 | bus_LV_5402-6_1_2_node_64 | 0.4 | n |  | TRUE
28 | bus_LV_5402-6_1_2_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_5402-6_1_2_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_5402-6_1_2_node_67 | 0.4 | n |  | TRUE
31 | bus_LV_5402-6_1_2_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_5402-6_1_2_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_5402-6_1_2_node_87 | 0.4 | n |  | TRUE
34 | bus_LV_5402-6_1_2_node_86 | 0.4 | n |  | TRUE
35 | bus_LV_5402-6_1_2_node_127 | 0.4 | n |  | TRUE
36 | bus_LV_5402-6_1_2_node_88 | 0.4 | n |  | TRUE
37 | bus_LV_5402-6_1_2_node_89 | 0.4 | n |  | TRUE
38 | bus_LV_5402-6_1_2_node_90 | 0.4 | n |  | TRUE
39 | bus_LV_5402-6_1_2_node_91 | 0.4 | n |  | TRUE
40 | bus_LV_5402-6_1_2_node_125 | 0.4 | n |  | TRUE
41 | bus_LV_5402-6_1_2_node_124 | 0.4 | n |  | TRUE
42 | bus_LV_5402-6_1_2_node_93 | 0.4 | n |  | TRUE
43 | bus_LV_5402-6_1_2_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_5402-6_1_2_node_95 | 0.4 | n |  | TRUE
45 | bus_LV_5402-6_1_2_node_96 | 0.4 | n |  | TRUE
46 | bus_LV_5402-6_1_2_node_97 | 0.4 | n |  | TRUE
47 | bus_LV_5402-6_1_2_node_98 | 0.4 | n |  | TRUE
48 | bus_LV_5402-6_1_2_node_100 | 0.4 | n |  | TRUE
49 | bus_LV_5402-6_1_2_node_103 | 0.4 | n |  | TRUE
50 | bus_LV_5402-6_1_2_node_101 | 0.4 | n |  | TRUE
51 | bus_LV_5402-6_1_2_node_102 | 0.4 | n |  | TRUE
52 | bus_LV_5402-6_1_2_node_118 | 0.4 | n |  | TRUE
53 | bus_LV_5402-6_1_2_node_104 | 0.4 | n |  | TRUE
54 | bus_LV_5402-6_1_2_node_105 | 0.4 | n |  | TRUE
55 | bus_LV_5402-6_1_2_node_106 | 0.4 | n |  | TRUE
56 | bus_LV_5402-6_1_2_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_5402-6_1_2_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_5402-6_1_2_node_109 | 0.4 | n |  | TRUE
59 | bus_LV_5402-6_1_2_node_114 | 0.4 | n |  | TRUE
60 | bus_LV_5402-6_1_2_node_110 | 0.4 | n |  | TRUE
61 | bus_LV_5402-6_1_2_node_111 | 0.4 | n |  | TRUE
62 | bus_LV_5402-6_1_2_node_112 | 0.4 | n |  | TRUE
63 | bus_LV_5402-6_1_2_node_113 | 0.4 | n |  | TRUE
64 | bus_LV_5402-6_1_2_node_115 | 0.4 | n |  | TRUE
65 | bus_LV_5402-6_1_2_node_116 | 0.4 | n |  | TRUE
66 | bus_LV_5402-6_1_2_node_117 | 0.4 | n |  | TRUE
67 | bus_LV_5402-6_1_2_node_126 | 0.4 | n |  | TRUE
68 | bus_MV_0_node_118 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5402-6_1_2_load_131 | 0 | 0.0063057 | 0.0015803 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5402-6_1_2_load_141 | 2 | 0.00070432 | 0.00017652 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5402-6_1_2_load_123 | 3 | 0.00034918 | 8.7512e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5402-6_1_2_load_45 | 4 | 0.00040281 | 0.00010095 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5402-6_1_2_load_46 | 5 | 0.00037037 | 9.2824e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5402-6_1_2_load_47 | 6 | 0.00034829 | 8.7289e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5402-6_1_2_load_48 | 7 | 0.00050066 | 0.00012548 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5402-6_1_2_load_49 | 8 | 0.00039404 | 9.8755e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5402-6_1_2_load_50 | 9 | 0.00036583 | 9.1685e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5402-6_1_2_load_55 | 10 | 0.00033123 | 8.3014e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5402-6_1_2_load_52 | 12 | 0.0004578 | 0.00011474 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5402-6_1_2_load_56 | 14 | 0.00036967 | 9.2647e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5402-6_1_2_load_119 | 17 | 0.00040237 | 0.00010084 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5402-6_1_2_load_57 | 19 | 0.00054409 | 0.00013636 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5402-6_1_2_load_61 | 20 | 0.00032998 | 8.2701e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5402-6_1_2_load_59 | 21 | 0.00032748 | 8.2075e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5402-6_1_2_load_60 | 22 | 0.00033573 | 8.4141e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5402-6_1_2_load_94 | 24 | 0.00032313 | 8.0984e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5402-6_1_2_load_62 | 25 | 0.00035889 | 8.9946e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5402-6_1_2_load_63 | 26 | 0.00037113 | 9.3013e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5402-6_1_2_load_64 | 27 | 0.00037425 | 9.3796e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5402-6_1_2_load_65 | 28 | 0.00032488 | 8.1423e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5402-6_1_2_load_66 | 29 | 0.00027742 | 6.9529e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5402-6_1_2_load_67 | 30 | 0.00025874 | 6.4847e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5402-6_1_2_load_83 | 31 | 0.00062626 | 0.00015696 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5402-6_1_2_load_86 | 34 | 0.0019995 | 0.00050112 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5402-6_1_2_load_88 | 36 | 0.0015471 | 0.00038774 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5402-6_1_2_load_91 | 39 | 0.0027731 | 0.000695 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5402-6_1_2_load_125 | 40 | 0.00028141 | 7.0527e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5402-6_1_2_load_124 | 41 | 0.00085652 | 0.00021466 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5402-6_1_2_load_93 | 42 | 0.00040414 | 0.00010129 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5402-6_1_2_load_99 | 43 | 0.00032707 | 8.1971e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5402-6_1_2_load_95 | 44 | 0.0003466 | 8.6867e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5402-6_1_2_load_96 | 45 | 0.00027577 | 6.9114e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5402-6_1_2_load_97 | 46 | 0.0003549 | 8.8947e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5402-6_1_2_load_98 | 47 | 0.00033262 | 8.3363e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5402-6_1_2_load_100 | 48 | 0.00037062 | 9.2887e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5402-6_1_2_load_103 | 49 | 0.00033126 | 8.3022e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5402-6_1_2_load_101 | 50 | 0.0002515 | 6.3032e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5402-6_1_2_load_102 | 51 | 0.00047344 | 0.00011865 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5402-6_1_2_load_118 | 52 | 0.00029647 | 7.4302e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5402-6_1_2_load_104 | 53 | 0.00043605 | 0.00010928 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5402-6_1_2_load_105 | 54 | 0.00035368 | 8.864e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5402-6_1_2_load_107 | 56 | 0.00035046 | 8.7835e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5402-6_1_2_load_108 | 57 | 0.00030517 | 7.6482e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5402-6_1_2_load_109 | 58 | 0.00025312 | 6.3438e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5402-6_1_2_load_114 | 59 | 0.00038072 | 9.5417e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5402-6_1_2_load_110 | 60 | 0.00040293 | 0.00010098 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5402-6_1_2_load_111 | 61 | 0.00031819 | 7.9747e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5402-6_1_2_load_112 | 62 | 0.00037053 | 9.2862e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5402-6_1_2_load_113 | 63 | 0.00030636 | 7.678e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5402-6_1_2_load_115 | 64 | 0.00036537 | 9.157e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5402-6_1_2_load_116 | 65 | 0.00041816 | 0.0001048 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5402-6_1_2_load_117 | 66 | 0.00028535 | 7.1515e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5402-6_1_2_load_126 | 67 | 0.00072884 | 0.00018267 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5402-6_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.099189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5402-6_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.15187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5402-6_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.078923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5402-6_1_2_line_3 | NAYY 4x150 SE | 3 | 61 | 0.0058183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5402-6_1_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.0051682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5402-6_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0084936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5402-6_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0099261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5402-6_1_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0072488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5402-6_1_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.01216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5402-6_1_2_line_9 | NAYY 4x150 SE | 9 | 10 | 7.3326e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5402-6_1_2_line_10 | NAYY 4x150 SE | 10 | 18 | 0.025564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5402-6_1_2_line_11 | NAYY 4x150 SE | 11 | 12 | 0.011743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5402-6_1_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.036541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5402-6_1_2_line_13 | NAYY 4x150 SE | 12 | 14 | 0.0064294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5402-6_1_2_line_14 | NAYY 4x150 SE | 13 | 15 | 0.14771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5402-6_1_2_line_15 | NAYY 4x150 SE | 14 | 19 | 0.011014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5402-6_1_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.078006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5402-6_1_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.09341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5402-6_1_2_line_18 | NAYY 4x150 SE | 16 | 67 | 0.1704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5402-6_1_2_line_19 | NAYY 4x150 SE | 18 | 21 | 0.0091222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5402-6_1_2_line_20 | NAYY 4x150 SE | 18 | 22 | 0.0069877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5402-6_1_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.0044889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5402-6_1_2_line_22 | NAYY 4x150 SE | 20 | 25 | 0.010058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5402-6_1_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.012709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5402-6_1_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.0029051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5402-6_1_2_line_25 | NAYY 4x150 SE | 23 | 42 | 0.010718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5402-6_1_2_line_26 | NAYY 4x150 SE | 23 | 30 | 0.0019759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5402-6_1_2_line_27 | NAYY 4x150 SE | 24 | 44 | 0.01424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5402-6_1_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.0051443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5402-6_1_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.011805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5402-6_1_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5402-6_1_2_line_31 | NAYY 4x150 SE | 28 | 29 | 0.01231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5402-6_1_2_line_32 | NAYY 4x150 SE | 29 | 30 | 0.0025772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5402-6_1_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.0043233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5402-6_1_2_line_34 | NAYY 4x150 SE | 32 | 33 | 0.030562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5402-6_1_2_line_35 | NAYY 4x150 SE | 33 | 35 | 0.13006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5402-6_1_2_line_36 | NAYY 4x150 SE | 33 | 34 | 0.015889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5402-6_1_2_line_37 | NAYY 4x150 SE | 35 | 40 | 0.050043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5402-6_1_2_line_38 | NAYY 4x150 SE | 35 | 67 | 0.06744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5402-6_1_2_line_39 | NAYY 4x150 SE | 36 | 37 | 0.045982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5402-6_1_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.025351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5402-6_1_2_line_41 | NAYY 4x150 SE | 37 | 39 | 0.017189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5402-6_1_2_line_42 | NAYY 4x150 SE | 38 | 40 | 0.017689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5402-6_1_2_line_43 | NAYY 4x150 SE | 38 | 41 | 0.018177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5402-6_1_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.01522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5402-6_1_2_line_45 | NAYY 4x150 SE | 43 | 48 | 0.0012336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5402-6_1_2_line_46 | NAYY 4x150 SE | 44 | 45 | 0.0029173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5402-6_1_2_line_47 | NAYY 4x150 SE | 45 | 46 | 0.010788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5402-6_1_2_line_48 | NAYY 4x150 SE | 46 | 47 | 0.0062939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5402-6_1_2_line_49 | NAYY 4x150 SE | 48 | 49 | 0.0059147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5402-6_1_2_line_50 | NAYY 4x150 SE | 49 | 53 | 0.012691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5402-6_1_2_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0090192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5402-6_1_2_line_52 | NAYY 4x150 SE | 51 | 52 | 0.012109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5402-6_1_2_line_53 | NAYY 4x150 SE | 52 | 66 | 0.010218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5402-6_1_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.016185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5402-6_1_2_line_55 | NAYY 4x150 SE | 54 | 55 | 0.0080877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5402-6_1_2_line_56 | NAYY 4x150 SE | 55 | 56 | 0.0048032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5402-6_1_2_line_57 | NAYY 4x150 SE | 55 | 57 | 0.010841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5402-6_1_2_line_58 | NAYY 4x150 SE | 56 | 58 | 0.011206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5402-6_1_2_line_59 | NAYY 4x150 SE | 57 | 59 | 0.004774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5402-6_1_2_line_60 | NAYY 4x150 SE | 58 | 60 | 0.0048698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5402-6_1_2_line_61 | NAYY 4x150 SE | 59 | 62 | 0.0010795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5402-6_1_2_line_62 | NAYY 4x150 SE | 60 | 61 | 0.0066087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5402-6_1_2_line_63 | NAYY 4x150 SE | 62 | 63 | 0.010985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5402-6_1_2_line_64 | NAYY 4x150 SE | 63 | 64 | 0.0046627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5402-6_1_2_line_65 | NAYY 4x150 SE | 64 | 65 | 0.0096088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5402-6_1_2_line_66 | NAYY 4x150 SE | 65 | 66 | 0.013622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5402-6_1_2_trafo_118 | 0.25 MVA 20/0.4 kV | 68 | 52 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2565553.0793 | 1121788.7763 | 2565459.9654 | 1121822.9549
1 | 2565457.8609 | 1121670.4607 | 2565553.0793 | 1121788.7763
2 | 2565505.4014 | 1121607.4633 | 2565457.8609 | 1121670.4607
3 | 2565509.2413 | 1121603.0921 | 2565505.4014 | 1121607.4633
4 | 2565513.1576 | 1121476.2198 | 2565517.2233 | 1121479.4104
5 | 2565513.1576 | 1121476.2198 | 2565506.4757 | 1121470.9763
6 | 2565517.2233 | 1121479.4104 | 2565525.0321 | 1121485.5382
7 | 2565500.7731 | 1121466.5012 | 2565506.4757 | 1121470.9763
8 | 2565525.0321 | 1121485.5382 | 2565532.0508 | 1121491.0461 | 2565533.3445 | 1121494.015
9 | 2565533.3445 | 1121494.015 | 2565533.3737 | 1121494.0822
10 | 2565551.7842 | 1121510.5878 | 2565546.9941 | 1121507.8248 | 2565536.0758 | 1121500.2833 | 2565533.3737 | 1121494.0822
11 | 2565475.4542 | 1121487.2231 | 2565485.3138 | 1121493.6022
12 | 2565444.5291 | 1121481.1859 | 2565448.0839 | 1121476.9856 | 2565454.2007 | 1121482.4423 | 2565458.8831 | 1121486.5954 | 2565475.4542 | 1121487.2231
13 | 2565485.3138 | 1121493.6022 | 2565487.3763 | 1121494.9366 | 2565490.6833 | 1121497.1384
14 | 2565444.5291 | 1121481.1859 | 2565448.0839 | 1121476.9856 | 2565484.4295 | 1121428.7867 | 2565547.9098 | 1121480.4391
15 | 2565490.6833 | 1121497.1384 | 2565496.9615 | 1121501.3184 | 2565499.6115 | 1121503.5609
16 | 2565547.9098 | 1121480.4391 | 2565552.5611 | 1121471.03 | 2565559.4942 | 1121460.0627 | 2565572.3757 | 1121441.2686 | 2565583.9109 | 1121424.4277 | 2565590.3517 | 1121415.0307
17 | 2565547.9098 | 1121480.4391 | 2565573.1482 | 1121500.961 | 2565597.6968 | 1121512.8271 | 2565629.466 | 1121523.8122
18 | 2565590.3517 | 1121415.0307 | 2565596.0278 | 1121418.9559 | 2565616.2104 | 1121432.0586 | 2565665.4955 | 1121458.925 | 2565678.4855 | 1121464.5762 | 2565690.3361 | 1121473.3022 | 2565707.1946 | 1121493.2831 | 2565716.7213 | 1121504.3568 | 2565722.8224 | 1121511.1701 | 2565726.0022 | 1121514.3843
19 | 2565551.7842 | 1121510.5878 | 2565547.6636 | 1121518.7262
20 | 2565551.7842 | 1121510.5878 | 2565557.9028 | 1121513.9629
21 | 2565503.0381 | 1121506.4607 | 2565499.6115 | 1121503.5609
22 | 2565503.0381 | 1121506.4607 | 2565510.7156 | 1121512.9578
23 | 2565541.9226 | 1121530.065 | 2565547.6636 | 1121518.7262
24 | 2565557.9028 | 1121513.9629 | 2565560.4465 | 1121515.3661
25 | 2565541.9226 | 1121530.065 | 2565549.9767 | 1121537.1359
26 | 2565541.9226 | 1121530.065 | 2565540.1582 | 1121529.1755
27 | 2565572.9151 | 1121522.244 | 2565560.4465 | 1121515.3661
28 | 2565514.6425 | 1121516.281 | 2565510.7156 | 1121512.9578
29 | 2565514.6425 | 1121516.281 | 2565514.7333 | 1121516.3578 | 2565525.1685 | 1121521.6186
30 | 2565526.8651 | 1121522.4739 | 2565525.1685 | 1121521.6186
31 | 2565526.8651 | 1121522.4739 | 2565537.8568 | 1121528.0153
32 | 2565537.8568 | 1121528.0153 | 2565540.1582 | 1121529.1755
33 | 2565857.6041 | 1121430.3544 | 2565861.5127 | 1121432.202
34 | 2565829.9095 | 1121417.2601 | 2565857.6041 | 1121430.3544
35 | 2565829.9095 | 1121417.2601 | 2565825.6787 | 1121423.3649 | 2565815.0655 | 1121460.1213 | 2565810.0166 | 1121475.6355 | 2565802.778 | 1121494.0302 | 2565789.4719 | 1121529.1789 | 2565787.4105 | 1121539.707
36 | 2565829.9095 | 1121417.2601 | 2565834.0741 | 1121413.1011 | 2565836.8876 | 1121408.694 | 2565838.9538 | 1121404.3889
37 | 2565787.4105 | 1121539.707 | 2565798.1051 | 1121540.4912 | 2565836.2852 | 1121549.8876
38 | 2565787.4105 | 1121539.707 | 2565778.7067 | 1121539.0671 | 2565743.2467 | 1121526.1839 | 2565731.6538 | 1121519.324 | 2565727.5467 | 1121515.9457 | 2565726.0022 | 1121514.3843
39 | 2565863.9562 | 1121530.6357 | 2565820.7904 | 1121514.7911
40 | 2565863.9562 | 1121530.6357 | 2565853.528 | 1121553.7508
41 | 2565863.9562 | 1121530.6357 | 2565865.1369 | 1121528.0055 | 2565869.9125 | 1121514.5205
42 | 2565853.528 | 1121553.7508 | 2565849.1396 | 1121552.4194 | 2565837.5345 | 1121550.1951 | 2565836.2852 | 1121549.8876
43 | 2565853.528 | 1121553.7508 | 2565870.9189 | 1121559.0403
44 | 2565549.9767 | 1121537.1359 | 2565556.4029 | 1121542.7777 | 2565556.5358 | 1121548.4909 | 2565556.1678 | 1121549.3704
45 | 2565555.6916 | 1121550.5084 | 2565556.1678 | 1121549.3704
46 | 2565572.9151 | 1121522.244 | 2565575.4696 | 1121523.6531
47 | 2565575.4696 | 1121523.6531 | 2565584.9153 | 1121528.8636
48 | 2565584.9153 | 1121528.8636 | 2565584.9153 | 1121528.8636 | 2565588.9542 | 1121533.6906
49 | 2565555.6916 | 1121550.5084 | 2565554.3444 | 1121553.7283 | 2565552.6848 | 1121555.4956
50 | 2565543.9976 | 1121564.7468 | 2565552.6848 | 1121555.4956
51 | 2565600.0883 | 1121548.0868 | 2565594.2082 | 1121554.9256
52 | 2565586.1215 | 1121563.926 | 2565588.1584 | 1121561.9618 | 2565594.2082 | 1121554.9256
53 | 2565586.1215 | 1121563.926 | 2565581.7917 | 1121568.1012 | 2565577.9732 | 1121569.857
54 | 2565543.9976 | 1121564.7468 | 2565532.9184 | 1121576.5453
55 | 2565527.3821 | 1121582.4411 | 2565532.9184 | 1121576.5453
56 | 2565527.3821 | 1121582.4411 | 2565524.2122 | 1121586.0497
57 | 2565527.3821 | 1121582.4411 | 2565536.9291 | 1121587.5781 | 2565536.9291 | 1121587.5781
58 | 2565524.2122 | 1121586.0497 | 2565516.8168 | 1121594.4684
59 | 2565541.4183 | 1121585.9537 | 2565536.9291 | 1121587.5781
60 | 2565516.8168 | 1121594.4684 | 2565513.6028 | 1121598.1271
61 | 2565542.4334 | 1121585.5864 | 2565541.4183 | 1121585.9537
62 | 2565513.6028 | 1121598.1271 | 2565509.2413 | 1121603.0921
63 | 2565542.4334 | 1121585.5864 | 2565547.0429 | 1121583.9185 | 2565552.5807 | 1121581.4023
64 | 2565556.8257 | 1121579.4735 | 2565552.5807 | 1121581.4023
65 | 2565556.8257 | 1121579.4735 | 2565565.5739 | 1121575.4986
66 | 2565577.9732 | 1121569.857 | 2565576.553 | 1121570.5101 | 2565565.5739 | 1121575.4986

## bus_geodata
| x | y | coords
0 | 2565459.9654 | 1121822.9549
1 | 2565553.0793 | 1121788.7763
2 | 2565457.8609 | 1121670.4607
3 | 2565505.4014 | 1121607.4633
4 | 2565513.1576 | 1121476.2198
5 | 2565517.2233 | 1121479.4104
6 | 2565506.4757 | 1121470.9763
7 | 2565525.0321 | 1121485.5382
8 | 2565500.7731 | 1121466.5012
9 | 2565533.3445 | 1121494.015
10 | 2565533.3737 | 1121494.0822
11 | 2565475.4542 | 1121487.2231
12 | 2565485.3138 | 1121493.6022
13 | 2565444.5291 | 1121481.1859
14 | 2565490.6833 | 1121497.1384
15 | 2565547.9098 | 1121480.4391
16 | 2565590.3517 | 1121415.0307
17 | 2565629.466 | 1121523.8122
18 | 2565551.7842 | 1121510.5878
19 | 2565499.6115 | 1121503.5609
20 | 2565503.0381 | 1121506.4607
21 | 2565547.6636 | 1121518.7262
22 | 2565557.9028 | 1121513.9629
23 | 2565541.9226 | 1121530.065
24 | 2565560.4465 | 1121515.3661
25 | 2565510.7156 | 1121512.9578
26 | 2565514.6425 | 1121516.281
27 | 2565525.1685 | 1121521.6186
28 | 2565526.8651 | 1121522.4739
29 | 2565537.8568 | 1121528.0153
30 | 2565540.1582 | 1121529.1755
31 | 2565861.5127 | 1121432.202
32 | 2565857.6041 | 1121430.3544
33 | 2565829.9095 | 1121417.2601
34 | 2565838.9538 | 1121404.3889
35 | 2565787.4105 | 1121539.707
36 | 2565820.7904 | 1121514.7911
37 | 2565863.9562 | 1121530.6357
38 | 2565853.528 | 1121553.7508
39 | 2565869.9125 | 1121514.5205
40 | 2565836.2852 | 1121549.8876
41 | 2565870.9189 | 1121559.0403
42 | 2565549.9767 | 1121537.1359
43 | 2565556.1678 | 1121549.3704
44 | 2565572.9151 | 1121522.244
45 | 2565575.4696 | 1121523.6531
46 | 2565584.9153 | 1121528.8636
47 | 2565588.9542 | 1121533.6906
48 | 2565555.6916 | 1121550.5084
49 | 2565552.6848 | 1121555.4956
50 | 2565600.0883 | 1121548.0868
51 | 2565594.2082 | 1121554.9256
52 | 2565586.1215 | 1121563.926
53 | 2565543.9976 | 1121564.7468
54 | 2565532.9184 | 1121576.5453
55 | 2565527.3821 | 1121582.4411
56 | 2565524.2122 | 1121586.0497
57 | 2565536.9291 | 1121587.5781
58 | 2565516.8168 | 1121594.4684
59 | 2565541.4183 | 1121585.9537
60 | 2565513.6028 | 1121598.1271
61 | 2565509.2413 | 1121603.0921
62 | 2565542.4334 | 1121585.5864
63 | 2565552.5807 | 1121581.4023
64 | 2565556.8257 | 1121579.4735
65 | 2565565.5739 | 1121575.4986
66 | 2565577.9732 | 1121569.857
67 | 2565726.0022 | 1121514.3843
68 | 2565586.1215 | 1121563.926

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1