## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5407-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5407-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5407-6_0_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_5407-6_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_5407-6_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5407-6_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5407-6_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_5407-6_0_4_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_5407-6_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5407-6_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_5407-6_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5407-6_0_4_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_5407-6_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_5407-6_0_4_node_62 | 0.4 | n |  | TRUE
14 | bus_LV_5407-6_0_4_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_5407-6_0_4_node_69 | 0.4 | n |  | TRUE
16 | bus_LV_5407-6_0_4_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_5407-6_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_5407-6_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_5407-6_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_5407-6_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_5407-6_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_5407-6_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_5407-6_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_5407-6_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_5407-6_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_5407-6_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_5407-6_0_4_node_55 | 0.4 | n |  | TRUE
28 | bus_LV_5407-6_0_4_node_74 | 0.4 | n |  | TRUE
29 | bus_LV_5407-6_0_4_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_5407-6_0_4_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_5407-6_0_4_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_5407-6_0_4_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_5407-6_0_4_node_68 | 0.4 | n |  | TRUE
34 | bus_LV_5407-6_0_4_node_73 | 0.4 | n |  | TRUE
35 | bus_LV_5407-6_0_4_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_5407-6_0_4_node_75 | 0.4 | n |  | TRUE
37 | bus_LV_5407-6_0_4_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_5407-6_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_5407-6_0_4_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_5407-6_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_5407-6_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_5407-6_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_5407-6_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_5407-6_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_5407-6_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_5407-6_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_5407-6_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_5407-6_0_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_5407-6_0_4_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_5407-6_0_4_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_5407-6_0_4_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_5407-6_0_4_node_61 | 0.4 | n |  | TRUE
53 | bus_LV_5407-6_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_5407-6_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_5407-6_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_5407-6_0_4_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_5407-6_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_5407-6_0_4_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_5407-6_0_4_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_5407-6_0_4_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_5407-6_0_4_node_79 | 0.4 | n |  | TRUE
62 | bus_LV_5407-6_0_4_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_5407-6_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_5407-6_0_4_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_5407-6_0_4_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_5407-6_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_5407-6_0_4_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_5407-6_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_5407-6_0_4_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_5407-6_0_4_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_5407-6_0_4_node_76 | 0.4 | n |  | TRUE
72 | bus_LV_5407-6_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_5407-6_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_5407-6_0_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_5407-6_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_MV_190_1_node_250 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5407-6_0_4_load_0 | 0 | 0.0060427 | 0.0015144 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5407-6_0_4_load_5 | 2 | 0.002262 | 0.0005669 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5407-6_0_4_load_3 | 4 | 0.00016519 | 4.14e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5407-6_0_4_load_28 | 6 | 0.00204 | 0.00051127 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5407-6_0_4_load_25 | 7 | 0.0038189 | 0.00095711 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5407-6_0_4_load_6 | 8 | 0.00011929 | 2.9897e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5407-6_0_4_load_8 | 10 | 0.00012896 | 3.2322e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5407-6_0_4_load_26 | 11 | 0.013764 | 0.0034496 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5407-6_0_4_load_69 | 15 | 0.0053123 | 0.0013314 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5407-6_0_4_load_14 | 17 | 0.00022396 | 5.6128e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5407-6_0_4_load_10 | 18 | 0.030516 | 0.007648 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5407-6_0_4_load_15 | 20 | 0.010053 | 0.0025196 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5407-6_0_4_load_19 | 22 | 0.0035418 | 0.00088765 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5407-6_0_4_load_21 | 24 | 0.0056689 | 0.0014208 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5407-6_0_4_load_13 | 26 | 0.0002804 | 7.0274e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5407-6_0_4_load_55 | 27 | 0.002235 | 0.00056014 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5407-6_0_4_load_37 | 29 | 0.0032827 | 0.00082273 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5407-6_0_4_load_34 | 30 | 0.015528 | 0.0038916 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5407-6_0_4_load_45 | 31 | 0.0043272 | 0.0010845 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5407-6_0_4_load_67 | 32 | 0.006748 | 0.0016912 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5407-6_0_4_load_68 | 33 | 0.00046533 | 0.00011662 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5407-6_0_4_load_73 | 34 | 0.0099546 | 0.0024949 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5407-6_0_4_load_53 | 35 | 0.0015997 | 0.00040093 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5407-6_0_4_load_75 | 36 | 0.0025833 | 0.00064743 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5407-6_0_4_load_39 | 37 | 0.0040427 | 0.0010132 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5407-6_0_4_load_33 | 38 | 0.00277 | 0.00069424 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5407-6_0_4_load_46 | 39 | 0.0036541 | 0.0009158 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5407-6_0_4_load_22 | 40 | 0.0044572 | 0.0011171 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5407-6_0_4_load_23 | 41 | 0.0016433 | 0.00041185 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5407-6_0_4_load_29 | 42 | 0.0010873 | 0.0002725 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5407-6_0_4_load_30 | 43 | 0.0016069 | 0.00040273 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5407-6_0_4_load_31 | 44 | 0.00039179 | 9.8191e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5407-6_0_4_load_32 | 45 | 0.0010086 | 0.00025278 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5407-6_0_4_load_38 | 47 | 0.0011465 | 0.00028734 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5407-6_0_4_load_70 | 49 | 0.0044629 | 0.0011185 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5407-6_0_4_load_71 | 51 | 0.0046233 | 0.0011587 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5407-6_0_4_load_40 | 53 | 0.0062498 | 0.0015663 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5407-6_0_4_load_41 | 54 | 0.0013827 | 0.00034653 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5407-6_0_4_load_43 | 55 | 0.0055269 | 0.0013852 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5407-6_0_4_load_47 | 56 | 0.0035852 | 0.00089854 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5407-6_0_4_load_44 | 57 | 0.0015461 | 0.00038749 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5407-6_0_4_load_49 | 58 | 0.00262 | 0.00065664 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5407-6_0_4_load_48 | 59 | 0.0037352 | 0.00093613 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5407-6_0_4_load_50 | 60 | 0.0021584 | 0.00054095 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5407-6_0_4_load_79 | 61 | 0.0010039 | 0.00025161 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5407-6_0_4_load_78 | 62 | 0.0017274 | 0.00043292 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5407-6_0_4_load_51 | 63 | 0.0025775 | 0.00064599 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5407-6_0_4_load_52 | 64 | 0.0015385 | 0.00038558 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5407-6_0_4_load_54 | 65 | 0.0049765 | 0.0012472 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5407-6_0_4_load_56 | 66 | 0.001588 | 0.000398 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5407-6_0_4_load_57 | 67 | 0.0019932 | 0.00049954 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5407-6_0_4_load_58 | 68 | 0.0015771 | 0.00039526 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5407-6_0_4_load_59 | 69 | 0.00065009 | 0.00016293 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5407-6_0_4_load_77 | 70 | 0.0013023 | 0.00032638 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5407-6_0_4_load_76 | 71 | 0.0011076 | 0.0002776 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5407-6_0_4_load_63 | 72 | 0.0086907 | 0.0021781 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5407-6_0_4_load_65 | 73 | 0.00036266 | 9.0892e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5407-6_0_4_load_66 | 74 | 0.00044357 | 0.00011117 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5407-6_0_4_load_72 | 75 | 0.0043581 | 0.0010922 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5407-6_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5407-6_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.02298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5407-6_0_4_line_2 | NAYY 4x150 SE | 2 | 6 | 0.10662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5407-6_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.054733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5407-6_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.007823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5407-6_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.011456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5407-6_0_4_line_6 | NAYY 4x150 SE | 5 | 9 | 0.01617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5407-6_0_4_line_7 | NAYY 4x150 SE | 5 | 10 | 0.027437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5407-6_0_4_line_8 | NAYY 4x150 SE | 6 | 7 | 0.10651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5407-6_0_4_line_9 | NAYY 4x150 SE | 7 | 41 | 0.024605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5407-6_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.033957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5407-6_0_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.077932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5407-6_0_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.048562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5407-6_0_4_line_13 | NAYY 4x150 SE | 11 | 14 | 0.030763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5407-6_0_4_line_14 | NAYY 4x150 SE | 12 | 17 | 0.042606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5407-6_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.016323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5407-6_0_4_line_16 | NAYY 4x150 SE | 14 | 40 | 0.027565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5407-6_0_4_line_17 | NAYY 4x150 SE | 15 | 16 | 0.008086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5407-6_0_4_line_18 | NAYY 4x150 SE | 16 | 52 | 0.055353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5407-6_0_4_line_19 | NAYY 4x150 SE | 17 | 25 | 0.032122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5407-6_0_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.029385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5407-6_0_4_line_21 | NAYY 4x150 SE | 19 | 20 | 0.047108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5407-6_0_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.024436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_5407-6_0_4_line_23 | NAYY 4x150 SE | 20 | 22 | 0.054295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5407-6_0_4_line_24 | NAYY 4x150 SE | 21 | 23 | 0.038443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_5407-6_0_4_line_25 | NAYY 4x150 SE | 21 | 24 | 0.013665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5407-6_0_4_line_26 | NAYY 4x150 SE | 22 | 27 | 0.03265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5407-6_0_4_line_27 | NAYY 4x150 SE | 22 | 28 | 0.082707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5407-6_0_4_line_28 | NAYY 4x150 SE | 23 | 29 | 0.052706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_5407-6_0_4_line_29 | NAYY 4x150 SE | 23 | 30 | 0.031071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5407-6_0_4_line_30 | NAYY 4x150 SE | 24 | 31 | 0.010988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5407-6_0_4_line_31 | NAYY 4x150 SE | 25 | 26 | 0.014885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5407-6_0_4_line_32 | NAYY 4x150 SE | 27 | 35 | 0.013595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5407-6_0_4_line_33 | NAYY 4x150 SE | 28 | 36 | 0.015801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5407-6_0_4_line_34 | NAYY 4x150 SE | 28 | 34 | 0.025775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5407-6_0_4_line_35 | NAYY 4x150 SE | 29 | 37 | 0.015269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_5407-6_0_4_line_36 | NAYY 4x150 SE | 30 | 38 | 0.0092457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5407-6_0_4_line_37 | NAYY 4x150 SE | 31 | 39 | 0.034889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5407-6_0_4_line_38 | NAYY 4x150 SE | 32 | 33 | 0.00087228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5407-6_0_4_line_39 | NAYY 4x150 SE | 33 | 34 | 0.021454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5407-6_0_4_line_40 | NAYY 4x150 SE | 35 | 63 | 0.01259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5407-6_0_4_line_41 | NAYY 4x150 SE | 37 | 50 | 0.035516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_5407-6_0_4_line_42 | NAYY 4x150 SE | 38 | 48 | 0.02261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5407-6_0_4_line_43 | NAYY 4x150 SE | 39 | 56 | 9.2031e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5407-6_0_4_line_44 | NAYY 4x150 SE | 40 | 41 | 0.029805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5407-6_0_4_line_45 | NAYY 4x150 SE | 42 | 43 | 0.027245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5407-6_0_4_line_46 | NAYY 4x150 SE | 43 | 44 | 0.030729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5407-6_0_4_line_47 | NAYY 4x150 SE | 44 | 45 | 0.015582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5407-6_0_4_line_48 | NAYY 4x150 SE | 45 | 46 | 0.031524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5407-6_0_4_line_49 | NAYY 4x150 SE | 46 | 47 | 0.018446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5407-6_0_4_line_50 | NAYY 4x150 SE | 46 | 48 | 0.057811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5407-6_0_4_line_51 | NAYY 4x150 SE | 47 | 49 | 0.012999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5407-6_0_4_line_52 | NAYY 4x150 SE | 49 | 51 | 0.022723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5407-6_0_4_line_53 | NAYY 4x150 SE | 50 | 52 | 0.016426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5407-6_0_4_line_54 | NAYY 4x150 SE | 51 | 75 | 0.0074753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5407-6_0_4_line_55 | NAYY 4x150 SE | 52 | 72 | 0.031975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5407-6_0_4_line_56 | NAYY 4x150 SE | 53 | 54 | 0.029859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5407-6_0_4_line_57 | NAYY 4x150 SE | 54 | 55 | 0.0081935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5407-6_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.011176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5407-6_0_4_line_59 | NAYY 4x150 SE | 55 | 58 | 0.06908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5407-6_0_4_line_60 | NAYY 4x150 SE | 56 | 59 | 0.032533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5407-6_0_4_line_61 | NAYY 4x150 SE | 57 | 60 | 0.033351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5407-6_0_4_line_62 | NAYY 4x150 SE | 58 | 59 | 0.0077795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5407-6_0_4_line_63 | NAYY 4x150 SE | 60 | 61 | 0.022462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5407-6_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.025158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5407-6_0_4_line_65 | NAYY 4x150 SE | 63 | 64 | 0.0307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5407-6_0_4_line_66 | NAYY 4x150 SE | 64 | 65 | 0.018213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5407-6_0_4_line_67 | NAYY 4x150 SE | 65 | 66 | 0.0051027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5407-6_0_4_line_68 | NAYY 4x150 SE | 66 | 67 | 0.042025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5407-6_0_4_line_69 | NAYY 4x150 SE | 67 | 68 | 0.0045264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5407-6_0_4_line_70 | NAYY 4x150 SE | 68 | 69 | 0.01873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_5407-6_0_4_line_71 | NAYY 4x150 SE | 69 | 70 | 0.010085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_5407-6_0_4_line_72 | NAYY 4x150 SE | 70 | 71 | 0.015348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5407-6_0_4_line_73 | NAYY 4x150 SE | 72 | 73 | 0.040162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5407-6_0_4_line_74 | NAYY 4x150 SE | 73 | 74 | 0.015694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5407-6_0_4_trafo_11 | 0.25 MVA 20/0.4 kV | 76 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2567728.2631 | 1132321.8579 | 2567715.8156 | 1132313.5982 | 2567705.6637 | 1132307.2092
1 | 2567728.2631 | 1132321.8579 | 2567732.0307 | 1132323.7942 | 2567737.5393 | 1132325.9213 | 2567747.3491 | 1132327.5696 | 2567750.2165 | 1132327.9467
2 | 2567734.8192 | 1132433.4475 | 2567750.2165 | 1132327.9467
3 | 2567612.312 | 1132255.6135 | 2567589.1928 | 1132305.224
4 | 2567604.7554 | 1132253.5086 | 2567612.312 | 1132255.6135
5 | 2567584.3538 | 1132315.608 | 2567589.1928 | 1132305.224
6 | 2567604.7554 | 1132253.5086 | 2567610.6505 | 1132241.5932 | 2567610.0118 | 1132238.7841
7 | 2567604.7554 | 1132253.5086 | 2567580.7005 | 1132240.3116
8 | 2567635.1996 | 1132395.7718 | 2567734.8192 | 1132433.4475
9 | 2567612.2212 | 1132386.9749 | 2567635.1996 | 1132395.7718
10 | 2567584.3538 | 1132315.608 | 2567570.0106 | 1132346.3865
11 | 2567633.7121 | 1132168.9551 | 2567637.3372 | 1132171.5814 | 2567608.9554 | 1132234.1875 | 2567610.0118 | 1132238.7841
12 | 2567536.4503 | 1132221.1156 | 2567543.7734 | 1132222.7436 | 2567550.273 | 1132224.4317 | 2567558.0216 | 1132227.8694 | 2567580.7005 | 1132240.3116
13 | 2567557.0163 | 1132374.2704 | 2567570.0106 | 1132346.3865
14 | 2567633.7121 | 1132168.9551 | 2567614.0955 | 1132154.8757 | 2567598.4045 | 1132145.1522
15 | 2567536.4503 | 1132221.1156 | 2567541.6641 | 1132205.6464
16 | 2567557.0163 | 1132374.2704 | 2567563.2047 | 1132373.9702 | 2567569.2658 | 1132374.3267 | 2567576.975 | 1132374.7743 | 2567584.3974 | 1132376.2907
17 | 2567541.6641 | 1132205.6464 | 2567543.074 | 1132205.8167 | 2567549.6564 | 1132206.8677
18 | 2567486.5697 | 1132198.84 | 2567541.6641 | 1132205.6464
19 | 2567568.6524 | 1132133.1537 | 2567596.2041 | 1132143.7886 | 2567598.4045 | 1132145.1522
20 | 2567424.1858 | 1132173.8756 | 2567432.2412 | 1132172.7982 | 2567446.3183 | 1132164.7514 | 2567450.0641 | 1132161.3739
21 | 2567424.1858 | 1132173.8756 | 2567432.9919 | 1132142.1899 | 2567438.7977 | 1132129.2073
22 | 2567424.1858 | 1132173.8756 | 2567409.5291 | 1132177.2454 | 2567401.689 | 1132182.5349
23 | 2567410.0232 | 1132090.1935 | 2567437.3821 | 1132109.7166 | 2567441.1063 | 1132117.8338 | 2567440.4472 | 1132125.519 | 2567438.7977 | 1132129.2073
24 | 2567377.5673 | 1132212.4249 | 2567381.1226 | 1132207.8366 | 2567394.0167 | 1132190.3581 | 2567401.689 | 1132182.5349
25 | 2567401.689 | 1132182.5349 | 2567394.2001 | 1132171.1048
26 | 2567383.4457 | 1132071.2281 | 2567410.0232 | 1132090.1935
27 | 2567410.0232 | 1132090.1935 | 2567466.2065 | 1132029.4985
28 | 2567377.5673 | 1132212.4249 | 2567384.5407 | 1132214.8772 | 2567429.8449 | 1132213.9351
29 | 2567377.5673 | 1132212.4249 | 2567373.9289 | 1132218.7366 | 2567363.3162 | 1132240.0235
30 | 2567388.1781 | 1132161.9136 | 2567394.2001 | 1132171.1048
31 | 2567568.6524 | 1132133.1537 | 2567578.1776 | 1132127.633 | 2567580.0323 | 1132124.2301
32 | 2567383.4457 | 1132071.2281 | 2567372.3797 | 1132063.3315
33 | 2567466.2065 | 1132029.4985 | 2567454.1377 | 1132019.2989
34 | 2567466.2065 | 1132029.4985 | 2567483.3063 | 1132040.7563 | 2567487.8011 | 1132043.5679
35 | 2567445.1107 | 1132213.6176 | 2567429.8449 | 1132213.9351
36 | 2567359.191 | 1132248.2979 | 2567363.3162 | 1132240.0235
37 | 2567388.1781 | 1132161.9136 | 2567371.2716 | 1132136.1096 | 2567369.5944 | 1132132.4345
38 | 2567506.7292 | 1132055.4079 | 2567505.9897 | 1132054.9453
39 | 2567487.8011 | 1132043.5679 | 2567505.9897 | 1132054.9453
40 | 2567362.1311 | 1132056.0182 | 2567372.3797 | 1132063.3315
41 | 2567480.5467 | 1132214.1246 | 2567472.6799 | 1132213.0443 | 2567445.1107 | 1132213.6176
42 | 2567343.5268 | 1132264.602 | 2567359.191 | 1132248.2979 | 2567359.191 | 1132248.2979
43 | 2567369.5562 | 1132132.3508 | 2567369.5944 | 1132132.4345
44 | 2567584.3974 | 1132376.2907 | 2567609.8569 | 1132386.0698 | 2567612.2212 | 1132386.9749
45 | 2567453.118 | 1132344.6106 | 2567475.5109 | 1132360.1305
46 | 2567427.8618 | 1132327.1062 | 2567453.118 | 1132344.6106
47 | 2567415.0547 | 1132318.2299 | 2567427.8618 | 1132327.1062
48 | 2567389.1453 | 1132300.2728 | 2567415.0547 | 1132318.2299
49 | 2567389.1453 | 1132300.2728 | 2567403.855 | 1132289.143
50 | 2567389.1453 | 1132300.2728 | 2567343.5268 | 1132264.602
51 | 2567414.221 | 1132281.2997 | 2567403.855 | 1132289.143
52 | 2567414.221 | 1132281.2997 | 2567415.1161 | 1132280.6225 | 2567427.8925 | 1132272.7161 | 2567434.1586 | 1132270.7209
53 | 2567480.5467 | 1132214.1246 | 2567486.5697 | 1132198.84
54 | 2567441.2815 | 1132268.4527 | 2567434.1586 | 1132270.7209
55 | 2567486.5697 | 1132198.84 | 2567497.1195 | 1132172.0697 | 2567500.1294 | 1132170.9801
56 | 2567296.746 | 1132176.6339 | 2567296.7438 | 1132163.4718 | 2567292.2596 | 1132147.3883
57 | 2567292.2596 | 1132147.3883 | 2567291.4828 | 1132144.602 | 2567288.0521 | 1132140.561
58 | 2567280.819 | 1132132.0409 | 2567288.0521 | 1132140.561
59 | 2567345.0292 | 1132101.5011 | 2567288.0521 | 1132140.561
60 | 2567369.5562 | 1132132.3508 | 2567362.3342 | 1132116.526 | 2567350.9035 | 1132106.6014
61 | 2567257.5726 | 1132108.1619 | 2567275.4657 | 1132125.7351 | 2567280.819 | 1132132.0409
62 | 2567345.0292 | 1132101.5011 | 2567350.9035 | 1132106.6014
63 | 2567241.5473 | 1132092.423 | 2567257.5726 | 1132108.1619
64 | 2567223.5985 | 1132074.795 | 2567241.5473 | 1132092.423
65 | 2567362.1311 | 1132056.0182 | 2567343.9191 | 1132043.0223 | 2567336.6363 | 1132038.9868
66 | 2567336.6363 | 1132038.9868 | 2567320.7054 | 1132030.1594
67 | 2567316.2422 | 1132027.6863 | 2567320.7054 | 1132030.1594
68 | 2567316.2422 | 1132027.6863 | 2567313.4221 | 1132026.1236 | 2567278.2574 | 1132009.7228
69 | 2567274.1552 | 1132007.8096 | 2567278.2574 | 1132009.7228
70 | 2567257.1809 | 1131999.8927 | 2567274.1552 | 1132007.8096
71 | 2567257.1809 | 1131999.8927 | 2567248.0413 | 1131995.63
72 | 2567235.0764 | 1131987.4165 | 2567248.0413 | 1131995.63 | 2567248.0413 | 1131995.63
73 | 2567537.8927 | 1132157.3092 | 2567537.8927 | 1132157.3092 | 2567500.1294 | 1132170.9801
74 | 2567537.8927 | 1132157.3092 | 2567551.8851 | 1132164.4168

## bus_geodata
| x | y | coords
0 | 2567705.6637 | 1132307.2092
1 | 2567728.2631 | 1132321.8579
2 | 2567750.2165 | 1132327.9467
3 | 2567612.312 | 1132255.6135
4 | 2567589.1928 | 1132305.224
5 | 2567604.7554 | 1132253.5086
6 | 2567734.8192 | 1132433.4475
7 | 2567635.1996 | 1132395.7718
8 | 2567584.3538 | 1132315.608
9 | 2567610.0118 | 1132238.7841
10 | 2567580.7005 | 1132240.3116
11 | 2567570.0106 | 1132346.3865
12 | 2567633.7121 | 1132168.9551
13 | 2567536.4503 | 1132221.1156
14 | 2567557.0163 | 1132374.2704
15 | 2567549.6564 | 1132206.8677
16 | 2567541.6641 | 1132205.6464
17 | 2567598.4045 | 1132145.1522
18 | 2567450.0641 | 1132161.3739
19 | 2567424.1858 | 1132173.8756
20 | 2567438.7977 | 1132129.2073
21 | 2567401.689 | 1132182.5349
22 | 2567410.0232 | 1132090.1935
23 | 2567377.5673 | 1132212.4249
24 | 2567394.2001 | 1132171.1048
25 | 2567568.6524 | 1132133.1537
26 | 2567580.0323 | 1132124.2301
27 | 2567383.4457 | 1132071.2281
28 | 2567466.2065 | 1132029.4985
29 | 2567429.8449 | 1132213.9351
30 | 2567363.3162 | 1132240.0235
31 | 2567388.1781 | 1132161.9136
32 | 2567506.7292 | 1132055.4079
33 | 2567505.9897 | 1132054.9453
34 | 2567487.8011 | 1132043.5679
35 | 2567372.3797 | 1132063.3315
36 | 2567454.1377 | 1132019.2989
37 | 2567445.1107 | 1132213.6176
38 | 2567359.191 | 1132248.2979
39 | 2567369.5944 | 1132132.4345
40 | 2567584.3974 | 1132376.2907
41 | 2567612.2212 | 1132386.9749
42 | 2567475.5109 | 1132360.1305
43 | 2567453.118 | 1132344.6106
44 | 2567427.8618 | 1132327.1062
45 | 2567415.0547 | 1132318.2299
46 | 2567389.1453 | 1132300.2728
47 | 2567403.855 | 1132289.143
48 | 2567343.5268 | 1132264.602
49 | 2567414.221 | 1132281.2997
50 | 2567480.5467 | 1132214.1246
51 | 2567434.1586 | 1132270.7209
52 | 2567486.5697 | 1132198.84
53 | 2567296.746 | 1132176.6339
54 | 2567292.2596 | 1132147.3883
55 | 2567288.0521 | 1132140.561
56 | 2567369.5562 | 1132132.3508
57 | 2567280.819 | 1132132.0409
58 | 2567345.0292 | 1132101.5011
59 | 2567350.9035 | 1132106.6014
60 | 2567257.5726 | 1132108.1619
61 | 2567241.5473 | 1132092.423
62 | 2567223.5985 | 1132074.795
63 | 2567362.1311 | 1132056.0182
64 | 2567336.6363 | 1132038.9868
65 | 2567320.7054 | 1132030.1594
66 | 2567316.2422 | 1132027.6863
67 | 2567278.2574 | 1132009.7228
68 | 2567274.1552 | 1132007.8096
69 | 2567257.1809 | 1131999.8927
70 | 2567248.0413 | 1131995.63
71 | 2567235.0764 | 1131987.4165
72 | 2567500.1294 | 1132170.9801
73 | 2567537.8927 | 1132157.3092
74 | 2567551.8851 | 1132164.4168
75 | 2567441.2815 | 1132268.4527
76 | 2567401.689 | 1132182.5349

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1