## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5410-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5410-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5410-5_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5410-5_0_4_node_178 | 0.4 | n |  | TRUE
4 | bus_LV_5410-5_0_4_node_177 | 0.4 | n |  | TRUE
5 | bus_LV_5410-5_0_4_node_52 | 0.4 | n |  | TRUE
6 | bus_LV_5410-5_0_4_node_181 | 0.4 | n |  | TRUE
7 | bus_LV_5410-5_0_4_node_182 | 0.4 | n |  | TRUE
8 | bus_LV_5410-5_0_4_node_183 | 0.4 | n |  | TRUE
9 | bus_LV_5410-5_0_4_node_184 | 0.4 | n |  | TRUE
10 | bus_LV_5410-5_0_4_node_189 | 0.4 | n |  | TRUE
11 | bus_LV_5410-5_0_4_node_53 | 0.4 | n |  | TRUE
12 | bus_LV_5410-5_0_4_node_187 | 0.4 | n |  | TRUE
13 | bus_LV_5410-5_0_4_node_191 | 0.4 | n |  | TRUE
14 | bus_LV_5410-5_0_4_node_153 | 0.4 | n |  | TRUE
15 | bus_LV_5410-5_0_4_node_71 | 0.4 | n |  | TRUE
16 | bus_LV_5410-5_0_4_node_154 | 0.4 | n |  | TRUE
17 | bus_LV_5410-5_0_4_node_155 | 0.4 | n |  | TRUE
18 | bus_LV_5410-5_0_4_node_156 | 0.4 | n |  | TRUE
19 | bus_LV_5410-5_0_4_node_157 | 0.4 | n |  | TRUE
20 | bus_LV_5410-5_0_4_node_158 | 0.4 | n |  | TRUE
21 | bus_LV_5410-5_0_4_node_159 | 0.4 | n |  | TRUE
22 | bus_LV_5410-5_0_4_node_160 | 0.4 | n |  | TRUE
23 | bus_LV_5410-5_0_4_node_161 | 0.4 | n |  | TRUE
24 | bus_LV_5410-5_0_4_node_162 | 0.4 | n |  | TRUE
25 | bus_LV_5410-5_0_4_node_163 | 0.4 | n |  | TRUE
26 | bus_LV_5410-5_0_4_node_165 | 0.4 | n |  | TRUE
27 | bus_LV_5410-5_0_4_node_166 | 0.4 | n |  | TRUE
28 | bus_LV_5410-5_0_4_node_167 | 0.4 | n |  | TRUE
29 | bus_LV_5410-5_0_4_node_174 | 0.4 | n |  | TRUE
30 | bus_LV_5410-5_0_4_node_168 | 0.4 | n |  | TRUE
31 | bus_LV_5410-5_0_4_node_169 | 0.4 | n |  | TRUE
32 | bus_LV_5410-5_0_4_node_170 | 0.4 | n |  | TRUE
33 | bus_LV_5410-5_0_4_node_171 | 0.4 | n |  | TRUE
34 | bus_LV_5410-5_0_4_node_172 | 0.4 | n |  | TRUE
35 | bus_LV_5410-5_0_4_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_5410-5_0_4_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_5410-5_0_4_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_5410-5_0_4_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_5410-5_0_4_node_49 | 0.4 | n |  | TRUE
40 | bus_LV_5410-5_0_4_node_50 | 0.4 | n |  | TRUE
41 | bus_LV_5410-5_0_4_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_5410-5_0_4_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_5410-5_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_5410-5_0_4_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_5410-5_0_4_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_5410-5_0_4_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_5410-5_0_4_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_5410-5_0_4_node_60 | 0.4 | n |  | TRUE
49 | bus_LV_5410-5_0_4_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_5410-5_0_4_node_62 | 0.4 | n |  | TRUE
51 | bus_LV_5410-5_0_4_node_77 | 0.4 | n |  | TRUE
52 | bus_LV_5410-5_0_4_node_173 | 0.4 | n |  | TRUE
53 | bus_LV_5410-5_0_4_node_65 | 0.4 | n |  | TRUE
54 | bus_LV_5410-5_0_4_node_73 | 0.4 | n |  | TRUE
55 | bus_LV_5410-5_0_4_node_63 | 0.4 | n |  | TRUE
56 | bus_LV_5410-5_0_4_node_64 | 0.4 | n |  | TRUE
57 | bus_LV_5410-5_0_4_node_66 | 0.4 | n |  | TRUE
58 | bus_LV_5410-5_0_4_node_67 | 0.4 | n |  | TRUE
59 | bus_LV_5410-5_0_4_node_70 | 0.4 | n |  | TRUE
60 | bus_LV_5410-5_0_4_node_72 | 0.4 | n |  | TRUE
61 | bus_LV_5410-5_0_4_node_186 | 0.4 | n |  | TRUE
62 | bus_LV_5410-5_0_4_node_188 | 0.4 | n |  | TRUE
63 | bus_LV_5410-5_0_4_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_5410-5_0_4_node_76 | 0.4 | n |  | TRUE
65 | bus_LV_5410-5_0_4_node_78 | 0.4 | n |  | TRUE
66 | bus_LV_5410-5_0_4_node_185 | 0.4 | n |  | TRUE
67 | bus_LV_5410-5_0_4_node_190 | 0.4 | n |  | TRUE
68 | bus_LV_5410-5_0_4_node_175 | 0.4 | n |  | TRUE
69 | bus_LV_5410-5_0_4_node_176 | 0.4 | n |  | TRUE
70 | bus_MV_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5410-5_0_4_load_0 | 0 | 0.0010543 | 0.00026422 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5410-5_0_4_load_1 | 1 | 0.00059021 | 0.00014792 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5410-5_0_4_load_3 | 2 | 0.00061133 | 0.00015321 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5410-5_0_4_load_178 | 3 | 0.00063475 | 0.00015908 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5410-5_0_4_load_177 | 4 | 0.00038725 | 9.7054e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5410-5_0_4_load_52 | 5 | 0.00081792 | 0.00020499 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5410-5_0_4_load_181 | 6 | 0.0043109 | 0.0010804 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5410-5_0_4_load_184 | 9 | 0.00072452 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5410-5_0_4_load_189 | 10 | 0.00072524 | 0.00018176 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5410-5_0_4_load_187 | 12 | 0.00072525 | 0.00018176 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5410-5_0_4_load_153 | 14 | 0.00021923 | 5.4944e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5410-5_0_4_load_154 | 16 | 0.00012947 | 3.2448e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5410-5_0_4_load_155 | 17 | 0.00027929 | 6.9998e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5410-5_0_4_load_156 | 18 | 0.00082736 | 0.00020736 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5410-5_0_4_load_157 | 19 | 0.00025404 | 6.3668e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5410-5_0_4_load_159 | 21 | 0.0006161 | 0.00015441 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5410-5_0_4_load_160 | 22 | 0.00058518 | 0.00014666 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5410-5_0_4_load_161 | 23 | 0.00069998 | 0.00017543 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5410-5_0_4_load_163 | 25 | 0.00087349 | 0.00021892 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5410-5_0_4_load_174 | 29 | 0.00063616 | 0.00015944 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5410-5_0_4_load_168 | 30 | 0.00053522 | 0.00013414 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5410-5_0_4_load_170 | 32 | 0.00075125 | 0.00018828 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5410-5_0_4_load_171 | 33 | 0.00064462 | 0.00016156 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5410-5_0_4_load_172 | 34 | 0.0010117 | 0.00025356 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5410-5_0_4_load_46 | 36 | 0.00039666 | 9.9411e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5410-5_0_4_load_47 | 37 | 0.00039634 | 9.9332e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5410-5_0_4_load_48 | 38 | 0.00030817 | 7.7236e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5410-5_0_4_load_50 | 40 | 0.0003948 | 9.8947e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5410-5_0_4_load_54 | 42 | 0.00047953 | 0.00012018 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5410-5_0_4_load_55 | 43 | 0.00060906 | 0.00015264 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5410-5_0_4_load_56 | 44 | 0.00032528 | 8.1523e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5410-5_0_4_load_57 | 45 | 0.00028869 | 7.2352e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5410-5_0_4_load_59 | 47 | 0.00011857 | 2.9715e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5410-5_0_4_load_62 | 50 | 0.00053463 | 0.00013399 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5410-5_0_4_load_173 | 52 | 0.00056306 | 0.00014112 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5410-5_0_4_load_73 | 54 | 0.00028681 | 7.1881e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5410-5_0_4_load_63 | 55 | 0.00019734 | 4.9458e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5410-5_0_4_load_64 | 56 | 0.00046131 | 0.00011561 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5410-5_0_4_load_66 | 57 | 0.00031307 | 7.8462e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5410-5_0_4_load_70 | 59 | 0.00019715 | 4.941e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5410-5_0_4_load_72 | 60 | 0.00020968 | 5.255e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5410-5_0_4_load_186 | 61 | 0.00072525 | 0.00018176 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5410-5_0_4_load_188 | 62 | 0.00072478 | 0.00018165 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5410-5_0_4_load_75 | 63 | 0.00093315 | 0.00023387 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5410-5_0_4_load_78 | 65 | 0.00062238 | 0.00015598 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5410-5_0_4_load_185 | 66 | 0.00072452 | 0.00018158 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5410-5_0_4_load_190 | 67 | 0.00072525 | 0.00018176 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5410-5_0_4_load_175 | 68 | 0.00039118 | 9.804e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5410-5_0_4_load_176 | 69 | 0.00084408 | 0.00021155 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5410-5_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.028035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5410-5_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.012608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5410-5_0_4_line_2 | NAYY 4x150 SE | 2 | 5 | 0.44192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_5410-5_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.04106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5410-5_0_4_line_4 | NAYY 4x150 SE | 4 | 69 | 0.083401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5410-5_0_4_line_5 | NAYY 4x150 SE | 5 | 41 | 0.17381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_5410-5_0_4_line_6 | NAYY 4x150 SE | 6 | 7 | 0.012904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_5410-5_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.0057385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_5410-5_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.022309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_5410-5_0_4_line_9 | NAYY 4x150 SE | 8 | 65 | 0.34273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_5410-5_0_4_line_10 | NAYY 4x150 SE | 9 | 13 | 0.015757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_5410-5_0_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.2858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5410-5_0_4_line_12 | NAYY 4x150 SE | 10 | 12 | 0.015802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5410-5_0_4_line_13 | NAYY 4x150 SE | 11 | 13 | 0.06975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_5410-5_0_4_line_14 | NAYY 4x150 SE | 11 | 41 | 0.58808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_5410-5_0_4_line_15 | NAYY 4x150 SE | 12 | 61 | 0.02076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5410-5_0_4_line_16 | NAYY 4x150 SE | 13 | 66 | 0.015903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5410-5_0_4_line_17 | NAYY 4x150 SE | 14 | 15 | 0.23302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5410-5_0_4_line_18 | NAYY 4x150 SE | 14 | 16 | 0.11107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5410-5_0_4_line_19 | NAYY 4x150 SE | 15 | 35 | 0.027699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5410-5_0_4_line_20 | NAYY 4x150 SE | 16 | 17 | 0.05121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5410-5_0_4_line_21 | NAYY 4x150 SE | 18 | 19 | 0.030091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5410-5_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.048955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5410-5_0_4_line_23 | NAYY 4x150 SE | 20 | 21 | 0.24768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5410-5_0_4_line_24 | NAYY 4x150 SE | 20 | 22 | 0.08241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5410-5_0_4_line_25 | NAYY 4x150 SE | 22 | 23 | 0.02042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5410-5_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.054433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5410-5_0_4_line_27 | NAYY 4x150 SE | 24 | 25 | 0.0077225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5410-5_0_4_line_28 | NAYY 4x150 SE | 25 | 26 | 0.1075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5410-5_0_4_line_29 | NAYY 4x150 SE | 26 | 27 | 0.041056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5410-5_0_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.29998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5410-5_0_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.25612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5410-5_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.30807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5410-5_0_4_line_33 | NAYY 4x150 SE | 29 | 68 | 0.083826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5410-5_0_4_line_34 | NAYY 4x150 SE | 30 | 31 | 0.29707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5410-5_0_4_line_35 | NAYY 4x150 SE | 31 | 32 | 0.016025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5410-5_0_4_line_36 | NAYY 4x150 SE | 31 | 33 | 0.098851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5410-5_0_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.20391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_5410-5_0_4_line_38 | NAYY 4x150 SE | 34 | 35 | 0.43083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_5410-5_0_4_line_39 | NAYY 4x150 SE | 35 | 58 | 0.20147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_5410-5_0_4_line_40 | NAYY 4x150 SE | 36 | 37 | 0.029818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5410-5_0_4_line_41 | NAYY 4x150 SE | 37 | 38 | 0.08722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5410-5_0_4_line_42 | NAYY 4x150 SE | 38 | 39 | 0.031091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5410-5_0_4_line_43 | NAYY 4x150 SE | 39 | 40 | 0.041099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5410-5_0_4_line_44 | NAYY 4x150 SE | 39 | 41 | 0.29441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5410-5_0_4_line_45 | NAYY 4x150 SE | 42 | 43 | 0.011882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5410-5_0_4_line_46 | NAYY 4x150 SE | 43 | 44 | 0.031054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5410-5_0_4_line_47 | NAYY 4x150 SE | 44 | 45 | 0.0054175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5410-5_0_4_line_48 | NAYY 4x150 SE | 45 | 46 | 0.16879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5410-5_0_4_line_49 | NAYY 4x150 SE | 46 | 47 | 0.0085626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5410-5_0_4_line_50 | NAYY 4x150 SE | 46 | 48 | 0.62849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_5410-5_0_4_line_51 | NAYY 4x150 SE | 46 | 49 | 0.18496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_5410-5_0_4_line_52 | NAYY 4x150 SE | 47 | 50 | 0.015484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5410-5_0_4_line_53 | NAYY 4x150 SE | 48 | 51 | 0.66614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_5410-5_0_4_line_54 | NAYY 4x150 SE | 48 | 52 | 0.16169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5410-5_0_4_line_55 | NAYY 4x150 SE | 49 | 53 | 0.008894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5410-5_0_4_line_56 | NAYY 4x150 SE | 49 | 54 | 0.05142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_5410-5_0_4_line_57 | NAYY 4x150 SE | 51 | 63 | 0.029153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_5410-5_0_4_line_58 | NAYY 4x150 SE | 53 | 56 | 0.024728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5410-5_0_4_line_59 | NAYY 4x150 SE | 54 | 60 | 0.0065417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_5410-5_0_4_line_60 | NAYY 4x150 SE | 55 | 56 | 0.13488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5410-5_0_4_line_61 | NAYY 4x150 SE | 57 | 58 | 0.030369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5410-5_0_4_line_62 | NAYY 4x150 SE | 58 | 59 | 0.035193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_5410-5_0_4_line_63 | NAYY 4x150 SE | 59 | 60 | 0.011187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_5410-5_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.0069065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5410-5_0_4_line_65 | NAYY 4x150 SE | 62 | 67 | 0.027349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5410-5_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.025937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_5410-5_0_4_line_67 | NAYY 4x150 SE | 64 | 65 | 0.47124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_5410-5_0_4_line_68 | NAYY 4x150 SE | 68 | 69 | 0.060425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5410-5_0_4_trafo_171 | 0.25 MVA 20/0.4 kV | 70 | 33 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50
0 | 2569485.8253 | 1133874.8748 | 2569484.9272 | 1133846.8545 | 2569484.9272 | 1133846.8545
1 | 2569484.9272 | 1133846.8545 | 2569484.1049 | 1133834.2738
2 | 2569684.4684 | 1133440.3869 | 2569484.1049 | 1133834.2738
3 | 2570623.1049 | 1133041.6288 | 2570627.8096 | 1133043.7282 | 2570645.9482 | 1133048.809 | 2570660.7188 | 1133057.3676
4 | 2570549.3851 | 1133003.849 | 2570562.025 | 1133014.6571 | 2570587.0281 | 1133025.5293 | 2570623.1049 | 1133041.6288
5 | 2569726.3113 | 1133398.5018 | 2569716.5546 | 1133397.7838 | 2569702.9456 | 1133390.2485 | 2569664.4218 | 1133363.4401 | 2569655.6302 | 1133361.7724 | 2569650.1854 | 1133362.8115 | 2569648.3031 | 1133366.5895 | 2569649.143 | 1133372.8662 | 2569664.2182 | 1133394.8457 | 2569684.4684 | 1133440.3869
6 | 2569646.6817 | 1133066.3368 | 2569646.2258 | 1133056.8455 | 2569645.2954 | 1133053.5734
7 | 2569643.7258 | 1133048.0537 | 2569645.2954 | 1133053.5734
8 | 2569646.6817 | 1133066.3368 | 2569626.5844 | 1133076.0208
9 | 2569643.7258 | 1133048.0537 | 2569642.0471 | 1133037.2679 | 2569643.7555 | 1133029.5221 | 2569650.1053 | 1133010.9475 | 2569624.4198 | 1132967.3997 | 2569597.0161 | 1132940.3912 | 2569576.0037 | 1132922.8996 | 2569554.3848 | 1132902.7321 | 2569549.6772 | 1132894.3517 | 2569547.959 | 1132886.4565 | 2569547.3948 | 1132879.9339 | 2569547.727 | 1132869.5048 | 2569550.1042 | 1132846.359 | 2569555.357 | 1132804.2114 | 2569557.8656 | 1132787.2347 | 2569560.964 | 1132768.1429 | 2569557.9573 | 1132756.6523 | 2569555.5574 | 1132747.4405
10 | 2569612.8005 | 1133069.0868 | 2569619.6012 | 1133074.2884 | 2569626.5844 | 1133076.0208
11 | 2569545.3177 | 1133052.197 | 2569539.6658 | 1133047.3453 | 2569536.1378 | 1133040.8266 | 2569532.0354 | 1133022.7161 | 2569527.5806 | 1133003.4401 | 2569518.1457 | 1132981.2546 | 2569505.0923 | 1132962.0555 | 2569492.319 | 1132937.3856 | 2569489.9547 | 1132926.57 | 2569506.9506 | 1132874.4802 | 2569506.1178 | 1132860.5219 | 2569493.4677 | 1132832.8721 | 2569485.8564 | 1132815.1352 | 2569482.5285 | 1132794.9642 | 2569479.941 | 1132787.9467
12 | 2569479.941 | 1132787.9467 | 2569476.1746 | 1132777.7322 | 2569473.747 | 1132773.4579
13 | 2569612.8005 | 1133069.0868 | 2569598.2634 | 1133062.4013 | 2569576.112 | 1133058.6112 | 2569557.9041 | 1133055.2126 | 2569545.3177 | 1133052.197
14 | 2569726.3113 | 1133398.5018 | 2569723.4217 | 1133396.393 | 2569720.2441 | 1133393.6409 | 2569717.1363 | 1133389.4656 | 2569714.9294 | 1133385.3413 | 2569708.1986 | 1133372.5243 | 2569702.6153 | 1133361.3357 | 2569699.3514 | 1133356.7276 | 2569695.2491 | 1133352.2682 | 2569690.3903 | 1133347.3791 | 2569685.3646 | 1133342.9911 | 2569680.1891 | 1133339.4265 | 2569674.1149 | 1133336.2444 | 2569657.4736 | 1133330.4142 | 2569640.2011 | 1133324.5983 | 2569633.4795 | 1133322.798 | 2569626.7913 | 1133319.9747 | 2569616.6716 | 1133312.9445 | 2569601.8019 | 1133301.247 | 2569590.2514 | 1133294.413 | 2569578.304 | 1133288.2591 | 2569564.6681 | 1133283.1143 | 2569550.1843 | 1133279.2745 | 2569525.0831 | 1133273.4986 | 2569515.0603 | 1133270.4366 | 2569506.3075 | 1133267.3461 | 2569498.3612 | 1133263.8957 | 2569494.5468 | 1133261.6028 | 2569490.763 | 1133259.2652 | 2569487.4304 | 1133256.3473 | 2569484.553 | 1133253.6383 | 2569482.1444 | 1133250.7713 | 2569480.059 | 1133247.8693 | 2569477.839 | 1133244.2454 | 2569476.1577 | 1133240.5965 | 2569473.1235 | 1133232.7636 | 2569466.6975 | 1133214.8983 | 2569464.5985 | 1133206.2936 | 2569472.1296 | 1133206.7779 | 2569478.4861 | 1133212.4596 | 2569489.4171 | 1133220.0302 | 2569498.4998 | 1133218.3167 | 2569514.7947 | 1133205.8169 | 2569525.3584 | 1133195.5916 | 2569525.9022 | 1133184.3833 | 2569502.7697 | 1133166.1691 | 2569502.9074 | 1133159.9097 | 2569503.076 | 1133152.1605 | 2569537.2278 | 1133117.8039 | 2569546.0305 | 1133091.1572 | 2569545.3177 | 1133052.197
15 | 2569462.8977 | 1132755.7842 | 2569467.1405 | 1132761.8256 | 2569473.747 | 1132773.4579
16 | 2569612.8005 | 1133069.0868 | 2569617.0317 | 1133059.3829 | 2569621.3022 | 1133056.2164
17 | 2570565.7246 | 1133514.6658 | 2570572.0831 | 1133508.4205 | 2570594.3987 | 1133510.0679 | 2570616.2677 | 1133522.7008 | 2570651.6385 | 1133527.5307 | 2570684.073 | 1133523.7487 | 2570696.368 | 1133527.324 | 2570708.0118 | 1133533.1147 | 2570712.829 | 1133531.2236 | 2570715.5664 | 1133527.464 | 2570709.399 | 1133519.2121 | 2570698.3979 | 1133501.5568 | 2570689.4098 | 1133484.7255 | 2570676.5685 | 1133466.4961
18 | 2570676.5685 | 1133466.4961 | 2570675.6902 | 1133465.2493 | 2570654.0367 | 1133428.9255 | 2570644.9085 | 1133419.7099 | 2570633.3257 | 1133415.442 | 2570616.9946 | 1133411.4085 | 2570606.0212 | 1133404.2585 | 2570595.6474 | 1133398.19
19 | 2570565.7246 | 1133514.6658 | 2570544.0755 | 1133509.2356 | 2570538.7751 | 1133508.3166
20 | 2570548.535 | 1133387.0418 | 2570560.7102 | 1133384.9257 | 2570574.1261 | 1133384.6489 | 2570588.2116 | 1133393.8402 | 2570595.6474 | 1133398.19
21 | 2570277.4901 | 1132997.3013 | 2570292.3834 | 1133002.9862 | 2570305.9498 | 1133007.0073
22 | 2570350.5161 | 1133025.5444 | 2570347.4226 | 1133025.7708 | 2570339.5519 | 1133020.4625 | 2570323.8151 | 1133012.3026 | 2570305.9498 | 1133007.0073
23 | 2570350.5161 | 1133025.5444 | 2570356.565 | 1133037.6651 | 2570365.5512 | 1133060.0543 | 2570384.6825 | 1133086.918 | 2570401.6661 | 1133138.9049 | 2570407.162 | 1133165.4355 | 2570414.0353 | 1133177.7523 | 2570431.652 | 1133191.0391 | 2570458.9585 | 1133200.7878 | 2570466.2214 | 1133209.3898 | 2570474.158 | 1133226.6483
24 | 2570350.5161 | 1133025.5444 | 2570351.3166 | 1133020.8159 | 2570346.7311 | 1133011.9785 | 2570309.7858 | 1132972.652 | 2570303.2039 | 1132960.6375
25 | 2570296.0624 | 1132941.7015 | 2570298.5374 | 1132952.1194 | 2570303.2039 | 1132960.6375
26 | 2570295.3607 | 1132890.2487 | 2570288.7779 | 1132899.4747 | 2570288.6239 | 1132910.392 | 2570296.0624 | 1132941.7015
27 | 2570295.3607 | 1132890.2487 | 2570292.1946 | 1132883.2051
28 | 2570248.1199 | 1132785.1517 | 2570292.1946 | 1132883.2051
29 | 2570259.2045 | 1132745.9441 | 2570256.4521 | 1132760.6984 | 2570253.7605 | 1132773.7515 | 2570248.1199 | 1132785.1517
30 | 2570129.0214 | 1132550.3463 | 2570133.4989 | 1132554.3595 | 2570135.24 | 1132557.6858 | 2570135.2454 | 1132563.4331 | 2570133.8654 | 1132569.254 | 2570126.9023 | 1132580.9943 | 2570115.944 | 1132599.0132 | 2570111.1591 | 1132610.6205 | 2570110.916 | 1132617.4696 | 2570112.8594 | 1132624.3523 | 2570126.5233 | 1132638.0469 | 2570139.3066 | 1132652.713 | 2570155.3324 | 1132661.4602 | 2570166.4685 | 1132671.5545 | 2570178.6144 | 1132680.3543 | 2570183.9427 | 1132686.7422 | 2570187.9287 | 1132694.1373 | 2570198.8245 | 1132719.4738 | 2570202.4449 | 1132723.0021 | 2570210.1252 | 1132727.0772 | 2570222.6942 | 1132732.729 | 2570248.1199 | 1132785.1517
31 | 2570259.2045 | 1132745.9441 | 2570271.5125 | 1132754.8878 | 2570282.8953 | 1132766.682 | 2570293.1743 | 1132781.0273 | 2570308.6376 | 1132799.1268 | 2570313.8516 | 1132808.9393 | 2570320.8781 | 1132817.8647 | 2570330.065 | 1132829.314 | 2570349.1183 | 1132844.8835 | 2570357.2138 | 1132853.6035 | 2570370.0856 | 1132861.4219 | 2570376.0454 | 1132867.9292 | 2570380.1427 | 1132874.5456 | 2570386.0122 | 1132887.7345 | 2570403.5843 | 1132907.4246 | 2570410.5876 | 1132913.2486 | 2570420.0261 | 1132918.0046 | 2570435.7446 | 1132923.9638 | 2570436.1057 | 1132924.1903
32 | 2570129.0214 | 1132550.3463 | 2570120.781 | 1132566.8621 | 2570078.2016 | 1132623.1793 | 2570078.3781 | 1132658.685 | 2570107.1329 | 1132730.0778 | 2570105.9714 | 1132807.8001 | 2570093.788 | 1132833.9087
33 | 2570436.1057 | 1132924.1903 | 2570450.0768 | 1132932.9535 | 2570461.9714 | 1132945.6459 | 2570468.9621 | 1132956.7616 | 2570471.3837 | 1132963.9311 | 2570474.191 | 1132969.6757 | 2570479.8782 | 1132974.0167 | 2570493.8457 | 1132979.3064 | 2570494.5698 | 1132979.5253
34 | 2570076.6226 | 1133093.9106 | 2570095.4196 | 1133095.1067 | 2570109.9295 | 1133085.5744 | 2570116.7579 | 1133067.0091 | 2570112.5189 | 1133025.6651 | 2570108.3195 | 1132970.614 | 2570098.9171 | 1132934.4093 | 2570082.6732 | 1132898.6833 | 2570080.9407 | 1132861.44 | 2570093.788 | 1132833.9087
35 | 2570076.6226 | 1133093.9106 | 2570071.4542 | 1133078.7423
36 | 2570076.6226 | 1133093.9106 | 2570064.0167 | 1133093.1062 | 2570041.0291 | 1133099.0901 | 2570032.6756 | 1133123.6217 | 2570044.2427 | 1133144.6635 | 2570055.4333 | 1133150.3219
37 | 2570055.4333 | 1133150.3219 | 2570067.8427 | 1133156.5966 | 2570110.9566 | 1133168.4217 | 2570143.5182 | 1133196.1518 | 2570174.1798 | 1133236.6535 | 2570194.8684 | 1133271.7018 | 2570201.5223 | 1133280.4966
38 | 2570538.7751 | 1133508.3166 | 2570509.7976 | 1133499.6986 | 2570480.0912 | 1133483.7139 | 2570450.6915 | 1133472.2302 | 2570426.454 | 1133472.7271 | 2570403.1875 | 1133462.4585 | 2570380.4935 | 1133448.1185 | 2570360.7834 | 1133425.393 | 2570332.9086 | 1133364.1775 | 2570319.17 | 1133347.4035 | 2570300.6737 | 1133338.3458 | 2570270.2332 | 1133332.9821 | 2570237.2525 | 1133316.7592 | 2570219.3693 | 1133304.0857 | 2570201.5223 | 1133280.4966
39 | 2570569.1287 | 1133686.6459 | 2570569.3187 | 1133676.7067 | 2570570.522 | 1133659.8925 | 2570572.5683 | 1133653.3459 | 2570586.3779 | 1133643.996 | 2570590.6734 | 1133639.3394 | 2570589.5905 | 1133627.2164 | 2570589.5728 | 1133617.3004 | 2570579.6604 | 1133590.9246 | 2570576.2015 | 1133579.3357 | 2570572.1741 | 1133564.8259 | 2570555.5064 | 1133546.9985 | 2570548.0047 | 1133535.0959 | 2570542.823 | 1133528.5514 | 2570538.7751 | 1133508.3166
40 | 2569995.8696 | 1133739.7251 | 2569994.1135 | 1133733.2175 | 2569989.5885 | 1133722.6125 | 2569983.9574 | 1133712.5309
41 | 2569983.9574 | 1133712.5309 | 2569980.121 | 1133705.6623 | 2569972.8619 | 1133691.6805 | 2569961.5956 | 1133665.9794 | 2569959.7932 | 1133661.1082 | 2569957.4442 | 1133656.2286 | 2569953.9544 | 1133651.0323 | 2569950.539 | 1133646.8583 | 2569944.6888 | 1133639.117 | 2569942.2793 | 1133636.4805
42 | 2569920.6865 | 1133614.1244 | 2569927.2646 | 1133621.1839 | 2569937.2045 | 1133630.928 | 2569942.2793 | 1133636.4805
43 | 2569885.0835 | 1133593.6698 | 2569900.3391 | 1133604.2766 | 2569920.6865 | 1133614.1244
44 | 2569920.6865 | 1133614.1244 | 2569896.532 | 1133584.8971 | 2569883.9518 | 1133569.0188 | 2569870.4339 | 1133551.8778 | 2569862.6694 | 1133543.1123 | 2569854.5065 | 1133534.7379 | 2569843.5099 | 1133524.6212 | 2569839.6191 | 1133519.3047 | 2569836.484 | 1133514.2734 | 2569833.9597 | 1133509.7616 | 2569829.382 | 1133501.0135 | 2569817.4247 | 1133485.0766 | 2569793.1244 | 1133454.6277 | 2569783.5932 | 1133438.9788 | 2569772.1706 | 1133423.8174 | 2569767.345 | 1133419.3839 | 2569761.6003 | 1133415.8776 | 2569755.7481 | 1133412.4275 | 2569749.49 | 1133409.3907 | 2569736.8997 | 1133403.9068 | 2569726.3113 | 1133398.5018
45 | 2570311.2751 | 1133464.0998 | 2570306.6647 | 1133455.8192 | 2570305.8243 | 1133453.566
46 | 2570311.2751 | 1133464.0998 | 2570312.3186 | 1133465.9742 | 2570315.4108 | 1133473.3181 | 2570317.3081 | 1133477.1774 | 2570319.2232 | 1133479.9693 | 2570328.0246 | 1133489.879
47 | 2570328.0246 | 1133489.879 | 2570330.2922 | 1133492.4321 | 2570331.5747 | 1133493.9703
48 | 2570429.3887 | 1133598.4642 | 2570436.3069 | 1133573.0287 | 2570436.8821 | 1133569.4463 | 2570436.8672 | 1133566.4116 | 2570436.1186 | 1133562.8913 | 2570433.9294 | 1133559.1335 | 2570431.0038 | 1133555.8907 | 2570427.1548 | 1133552.708 | 2570422.852 | 1133549.5831 | 2570418.243 | 1133546.8266 | 2570414.0476 | 1133545.2242 | 2570409.2456 | 1133543.9027 | 2570402.5518 | 1133542.9573 | 2570394.9741 | 1133542.2831 | 2570381.1086 | 1133541.8399 | 2570377.8272 | 1133541.3892 | 2570375.7529 | 1133540.6435 | 2570373.3757 | 1133539.3434 | 2570371.1806 | 1133537.52 | 2570368.9048 | 1133534.9299 | 2570362.0418 | 1133526.2148 | 2570358.4907 | 1133522.5749 | 2570344.2767 | 1133509.2049 | 2570331.5747 | 1133493.9703
49 | 2570429.3887 | 1133598.4642 | 2570434.0825 | 1133593.4276 | 2570435.431 | 1133592.4293
50 | 2570011.2944 | 1133295.9918 | 2570110.4981 | 1133387.7333 | 2570164.6202 | 1133449.6958 | 2570172.1147 | 1133459.9638 | 2570181.0536 | 1133466.5673 | 2570191.9274 | 1133472.1941 | 2570202.449 | 1133489.0838 | 2570206.4544 | 1133494.2776 | 2570211.5658 | 1133498.9769 | 2570215.7621 | 1133502.3134 | 2570224.4263 | 1133507.8733 | 2570280.7073 | 1133541.4121 | 2570359.5965 | 1133611.1581 | 2570371.7463 | 1133616.4898 | 2570379.8018 | 1133620.4188 | 2570386.1582 | 1133624.7786 | 2570393.7865 | 1133631.0554 | 2570404.2443 | 1133641.4091 | 2570411.2676 | 1133646.7773 | 2570433.241 | 1133660.3206 | 2570426.9941 | 1133651.6025 | 2570424.4773 | 1133643.8221 | 2570421.527 | 1133632.4198 | 2570421.1571 | 1133627.6192 | 2570421.2184 | 1133624.4284 | 2570421.9522 | 1133620.2561 | 2570423.3263 | 1133614.8022 | 2570429.3887 | 1133598.4642
51 | 2570497.3774 | 1133758.0436 | 2570494.0162 | 1133752.2795 | 2570478.0658 | 1133720.5529 | 2570468.0906 | 1133695.556 | 2570465.0543 | 1133690.1238 | 2570460.0471 | 1133684.6234 | 2570446.8542 | 1133673.716 | 2570438.4873 | 1133665.9087 | 2570433.241 | 1133660.3206 | 2570426.9941 | 1133651.6025 | 2570424.4773 | 1133643.8221 | 2570421.527 | 1133632.4198 | 2570421.1571 | 1133627.6192 | 2570421.2184 | 1133624.4284 | 2570421.9522 | 1133620.2561 | 2570423.3263 | 1133614.8022 | 2570429.3887 | 1133598.4642
52 | 2570449.9648 | 1133589.2253 | 2570439.2978 | 1133589.5667 | 2570435.431 | 1133592.4293
53 | 2570011.2944 | 1133295.9918 | 2569986.5268 | 1133276.7389 | 2569969.6585 | 1133274.7553 | 2569928.7289 | 1133251.6591 | 2569907.5963 | 1133228.2085 | 2569881.1987 | 1133209.4755 | 2569866.6588 | 1133188.271 | 2569863.0819 | 1133179.5623 | 2569824.9161 | 1133109.1072 | 2569812.827 | 1133042.4789 | 2569815.4814 | 1133005.336 | 2569820.116 | 1132991.5504 | 2569822.1858 | 1132980.5901 | 2569820.92 | 1132963.0544 | 2569814.2063 | 1132949.0699 | 2569804.7958 | 1132925.4275 | 2569806.808 | 1132906.0522 | 2569803.3216 | 1132893.9637 | 2569797.5435 | 1132883.8876 | 2569789.4737 | 1132878.9145 | 2569785.3624 | 1132852.7665 | 2569781.0245 | 1132841.2825 | 2569779.8113 | 1132817.3878 | 2569782.9034 | 1132796.8954 | 2569778.0604 | 1132769.1614 | 2569757.772 | 1132754.8339 | 2569745.011 | 1132758.522
54 | 2570011.2944 | 1133295.9918 | 2570036.5179 | 1133324.9029 | 2570042.1248 | 1133334.7466 | 2570045.9573 | 1133348.4788 | 2570047.3312 | 1133360.0444 | 2570049.8699 | 1133370.5592 | 2570053.7354 | 1133381.6344 | 2570061.7958 | 1133397.291 | 2570070.3436 | 1133411.8892 | 2570085.5528 | 1133434.8362 | 2570086.1748 | 1133436.1916
55 | 2570505.4702 | 1133761.7836 | 2570497.3774 | 1133758.0436
56 | 2570497.3774 | 1133758.0436 | 2570499.2812 | 1133752.2759 | 2570501.5727 | 1133747.0954 | 2570504.6077 | 1133741.2776 | 2570508.0658 | 1133735.4133 | 2570511.1539 | 1133730.996 | 2570514.9173 | 1133726.1641 | 2570518.7515 | 1133721.6319 | 2570524.3435 | 1133716.1241 | 2570525.0931 | 1133715.4447
57 | 2569745.011 | 1132758.522 | 2569739.6078 | 1132760.2945 | 2569716.3603 | 1132757.0986
58 | 2570505.4702 | 1133761.7836 | 2570510.636 | 1133758.8347 | 2570522.1002 | 1133743.9607
59 | 2570529.9403 | 1133711.0517 | 2570525.0931 | 1133715.4447
60 | 2570637.1815 | 1133741.864 | 2570618.6357 | 1133731.8712 | 2570600.9129 | 1133723.2645 | 2570586.2424 | 1133717.0775 | 2570577.3373 | 1133714.075 | 2570569.6766 | 1133712.1115 | 2570564.4007 | 1133711.4592 | 2570559.7285 | 1133711.482 | 2570555.6684 | 1133712.3134 | 2570551.144 | 1133714.2253 | 2570544.9913 | 1133718.4242 | 2570538.0555 | 1133724.6056 | 2570530.6756 | 1133732.8347 | 2570522.1002 | 1133743.9607
61 | 2570569.1287 | 1133686.6459 | 2570578.8904 | 1133683.7968 | 2570589.4106 | 1133681.7889 | 2570598.8336 | 1133680.6615
62 | 2570569.1287 | 1133686.6459 | 2570561.5625 | 1133689.8623 | 2570555.6656 | 1133692.8593 | 2570548.0761 | 1133697.5987 | 2570539.7681 | 1133703.3645 | 2570538.7352 | 1133704.1481
63 | 2570538.7352 | 1133704.1481 | 2570531.5087 | 1133709.6302 | 2570529.9403 | 1133711.0517
64 | 2569462.8977 | 1132755.7842 | 2569458.9284 | 1132750.1322
65 | 2569458.9284 | 1132750.1322 | 2569447.6377 | 1132734.0551 | 2569442.859 | 1132728.0135
66 | 2569705.4744 | 1132734.6755 | 2569714.2543 | 1132756.8091 | 2569716.3603 | 1132757.0986
67 | 2569705.4744 | 1132734.6755 | 2569682.7126 | 1132723.0398 | 2569643.433 | 1132695.2904 | 2569627.8344 | 1132682.8517 | 2569598.4692 | 1132661 | 2569586.9094 | 1132647.9963 | 2569570.0539 | 1132627.5935 | 2569554.0514 | 1132609.9433 | 2569537.9067 | 1132596.1514 | 2569520.091 | 1132583.8353 | 2569502.5292 | 1132576.0648 | 2569495.0759 | 1132575.9024 | 2569479.6954 | 1132585.3406 | 2569475.83 | 1132595.8654 | 2569476.8206 | 1132605.9766 | 2569481.8906 | 1132617.4455 | 2569501.5084 | 1132651.1741 | 2569507.7357 | 1132670.7412 | 2569525.564 | 1132687.1259 | 2569544.0728 | 1132714.7683 | 2569550.4832 | 1132727.9647 | 2569555.5574 | 1132747.4405
68 | 2570494.5698 | 1132979.5253 | 2570496.8139 | 1132980.2035 | 2570509.0184 | 1132983.89 | 2570543.2552 | 1132998.6076 | 2570549.3851 | 1133003.849

## bus_geodata
| x | y | coords
0 | 2569485.8253 | 1133874.8748
1 | 2569484.9272 | 1133846.8545
2 | 2569484.1049 | 1133834.2738
3 | 2570660.7188 | 1133057.3676
4 | 2570623.1049 | 1133041.6288
5 | 2569684.4684 | 1133440.3869
6 | 2569645.2954 | 1133053.5734
7 | 2569646.6817 | 1133066.3368
8 | 2569643.7258 | 1133048.0537
9 | 2569626.5844 | 1133076.0208
10 | 2569479.941 | 1132787.9467
11 | 2569545.3177 | 1133052.197
12 | 2569473.747 | 1132773.4579
13 | 2569612.8005 | 1133069.0868
14 | 2570676.5685 | 1133466.4961
15 | 2570565.7246 | 1133514.6658
16 | 2570595.6474 | 1133398.19
17 | 2570548.535 | 1133387.0418
18 | 2570305.9498 | 1133007.0073
19 | 2570277.4901 | 1132997.3013
20 | 2570350.5161 | 1133025.5444
21 | 2570474.158 | 1133226.6483
22 | 2570303.2039 | 1132960.6375
23 | 2570296.0624 | 1132941.7015
24 | 2570295.3607 | 1132890.2487
25 | 2570292.1946 | 1132883.2051
26 | 2570248.1199 | 1132785.1517
27 | 2570259.2045 | 1132745.9441
28 | 2570129.0214 | 1132550.3463
29 | 2570436.1057 | 1132924.1903
30 | 2570093.788 | 1132833.9087
31 | 2570076.6226 | 1133093.9106
32 | 2570071.4542 | 1133078.7423
33 | 2570055.4333 | 1133150.3219
34 | 2570201.5223 | 1133280.4966
35 | 2570538.7751 | 1133508.3166
36 | 2569995.8696 | 1133739.7251
37 | 2569983.9574 | 1133712.5309
38 | 2569942.2793 | 1133636.4805
39 | 2569920.6865 | 1133614.1244
40 | 2569885.0835 | 1133593.6698
41 | 2569726.3113 | 1133398.5018
42 | 2570305.8243 | 1133453.566
43 | 2570311.2751 | 1133464.0998
44 | 2570328.0246 | 1133489.879
45 | 2570331.5747 | 1133493.9703
46 | 2570429.3887 | 1133598.4642
47 | 2570435.431 | 1133592.4293
48 | 2570011.2944 | 1133295.9918
49 | 2570497.3774 | 1133758.0436
50 | 2570449.9648 | 1133589.2253
51 | 2569745.011 | 1132758.522
52 | 2570086.1748 | 1133436.1916
53 | 2570505.4702 | 1133761.7836
54 | 2570525.0931 | 1133715.4447
55 | 2570637.1815 | 1133741.864
56 | 2570522.1002 | 1133743.9607
57 | 2570598.8336 | 1133680.6615
58 | 2570569.1287 | 1133686.6459
59 | 2570538.7352 | 1133704.1481
60 | 2570529.9403 | 1133711.0517
61 | 2569462.8977 | 1132755.7842
62 | 2569458.9284 | 1132750.1322
63 | 2569716.3603 | 1132757.0986
64 | 2569705.4744 | 1132734.6755
65 | 2569555.5574 | 1132747.4405
66 | 2569621.3022 | 1133056.2164
67 | 2569442.859 | 1132728.0135
68 | 2570494.5698 | 1132979.5253
69 | 2570549.3851 | 1133003.849
70 | 2570055.4333 | 1133150.3219

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1