## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5411-6_1_3_node_9 | 0.4 | n |  | TRUE
1 | bus_LV_5411-6_1_3_node_10 | 0.4 | n |  | TRUE
2 | bus_LV_5411-6_1_3_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_5411-6_1_3_node_12 | 0.4 | n |  | TRUE
4 | bus_LV_5411-6_1_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_5411-6_1_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_5411-6_1_3_node_155 | 0.4 | n |  | TRUE
7 | bus_LV_5411-6_1_3_node_118 | 0.4 | n |  | TRUE
8 | bus_LV_5411-6_1_3_node_120 | 0.4 | n |  | TRUE
9 | bus_LV_5411-6_1_3_node_121 | 0.4 | n |  | TRUE
10 | bus_LV_5411-6_1_3_node_116 | 0.4 | n |  | TRUE
11 | bus_LV_5411-6_1_3_node_153 | 0.4 | n |  | TRUE
12 | bus_LV_5411-6_1_3_node_154 | 0.4 | n |  | TRUE
13 | bus_LV_5411-6_1_3_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_5411-6_1_3_node_126 | 0.4 | n |  | TRUE
15 | bus_LV_5411-6_1_3_node_70 | 0.4 | n |  | TRUE
16 | bus_LV_5411-6_1_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_5411-6_1_3_node_220 | 0.4 | n |  | TRUE
18 | bus_LV_5411-6_1_3_node_168 | 0.4 | n |  | TRUE
19 | bus_LV_5411-6_1_3_node_68 | 0.4 | n |  | TRUE
20 | bus_LV_5411-6_1_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_5411-6_1_3_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_5411-6_1_3_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_5411-6_1_3_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_5411-6_1_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_5411-6_1_3_node_145 | 0.4 | n |  | TRUE
26 | bus_LV_5411-6_1_3_node_60 | 0.4 | n |  | TRUE
27 | bus_LV_5411-6_1_3_node_149 | 0.4 | n |  | TRUE
28 | bus_LV_5411-6_1_3_node_138 | 0.4 | n |  | TRUE
29 | bus_LV_5411-6_1_3_node_159 | 0.4 | n |  | TRUE
30 | bus_LV_5411-6_1_3_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_5411-6_1_3_node_139 | 0.4 | n |  | TRUE
32 | bus_LV_5411-6_1_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_5411-6_1_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_5411-6_1_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_5411-6_1_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_5411-6_1_3_node_221 | 0.4 | n |  | TRUE
37 | bus_LV_5411-6_1_3_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_5411-6_1_3_node_117 | 0.4 | n |  | TRUE
39 | bus_LV_5411-6_1_3_node_119 | 0.4 | n |  | TRUE
40 | bus_LV_5411-6_1_3_node_164 | 0.4 | n |  | TRUE
41 | bus_LV_5411-6_1_3_node_224 | 0.4 | n |  | TRUE
42 | bus_LV_5411-6_1_3_node_163 | 0.4 | n |  | TRUE
43 | bus_LV_5411-6_1_3_node_172 | 0.4 | n |  | TRUE
44 | bus_LV_5411-6_1_3_node_173 | 0.4 | n |  | TRUE
45 | bus_LV_5411-6_1_3_node_143 | 0.4 | n |  | TRUE
46 | bus_LV_5411-6_1_3_node_208 | 0.4 | n |  | TRUE
47 | bus_LV_5411-6_1_3_node_157 | 0.4 | n |  | TRUE
48 | bus_LV_5411-6_1_3_node_171 | 0.4 | n |  | TRUE
49 | bus_LV_5411-6_1_3_node_24 | 0.4 | n |  | TRUE
50 | bus_LV_5411-6_1_3_node_142 | 0.4 | n |  | TRUE
51 | bus_LV_5411-6_1_3_node_141 | 0.4 | n |  | TRUE
52 | bus_LV_5411-6_1_3_node_166 | 0.4 | n |  | TRUE
53 | bus_LV_5411-6_1_3_node_167 | 0.4 | n |  | TRUE
54 | bus_LV_5411-6_1_3_node_140 | 0.4 | n |  | TRUE
55 | bus_LV_5411-6_1_3_node_25 | 0.4 | n |  | TRUE
56 | bus_LV_5411-6_1_3_node_26 | 0.4 | n |  | TRUE
57 | bus_LV_5411-6_1_3_node_27 | 0.4 | n |  | TRUE
58 | bus_LV_5411-6_1_3_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_5411-6_1_3_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_5411-6_1_3_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_5411-6_1_3_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_5411-6_1_3_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_5411-6_1_3_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_5411-6_1_3_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_5411-6_1_3_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_5411-6_1_3_node_144 | 0.4 | n |  | TRUE
67 | bus_LV_5411-6_1_3_node_156 | 0.4 | n |  | TRUE
68 | bus_LV_5411-6_1_3_node_150 | 0.4 | n |  | TRUE
69 | bus_LV_5411-6_1_3_node_39 | 0.4 | n |  | TRUE
70 | bus_LV_5411-6_1_3_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_5411-6_1_3_node_41 | 0.4 | n |  | TRUE
72 | bus_LV_5411-6_1_3_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_5411-6_1_3_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_5411-6_1_3_node_184 | 0.4 | n |  | TRUE
75 | bus_LV_5411-6_1_3_node_183 | 0.4 | n |  | TRUE
76 | bus_LV_5411-6_1_3_node_45 | 0.4 | n |  | TRUE
77 | bus_LV_5411-6_1_3_node_46 | 0.4 | n |  | TRUE
78 | bus_LV_5411-6_1_3_node_182 | 0.4 | n |  | TRUE
79 | bus_LV_5411-6_1_3_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_5411-6_1_3_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_5411-6_1_3_node_61 | 0.4 | n |  | TRUE
82 | bus_LV_5411-6_1_3_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_5411-6_1_3_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_5411-6_1_3_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_5411-6_1_3_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_5411-6_1_3_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_5411-6_1_3_node_165 | 0.4 | n |  | TRUE
88 | bus_LV_5411-6_1_3_node_169 | 0.4 | n |  | TRUE
89 | bus_LV_5411-6_1_3_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_5411-6_1_3_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_5411-6_1_3_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_5411-6_1_3_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_5411-6_1_3_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_5411-6_1_3_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_5411-6_1_3_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_5411-6_1_3_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_5411-6_1_3_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_5411-6_1_3_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_5411-6_1_3_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_5411-6_1_3_node_76 | 0.4 | n |  | TRUE
101 | bus_LV_5411-6_1_3_node_67 | 0.4 | n |  | TRUE
102 | bus_LV_5411-6_1_3_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_5411-6_1_3_node_71 | 0.4 | n |  | TRUE
104 | bus_LV_5411-6_1_3_node_72 | 0.4 | n |  | TRUE
105 | bus_LV_5411-6_1_3_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_5411-6_1_3_node_80 | 0.4 | n |  | TRUE
107 | bus_LV_5411-6_1_3_node_148 | 0.4 | n |  | TRUE
108 | bus_LV_5411-6_1_3_node_146 | 0.4 | n |  | TRUE
109 | bus_LV_5411-6_1_3_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_5411-6_1_3_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_5411-6_1_3_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_5411-6_1_3_node_75 | 0.4 | n |  | TRUE
113 | bus_LV_5411-6_1_3_node_77 | 0.4 | n |  | TRUE
114 | bus_LV_5411-6_1_3_node_225 | 0.4 | n |  | TRUE
115 | bus_LV_5411-6_1_3_node_79 | 0.4 | n |  | TRUE
116 | bus_LV_5411-6_1_3_node_160 | 0.4 | n |  | TRUE
117 | bus_LV_5411-6_1_3_node_209 | 0.4 | n |  | TRUE
118 | bus_LV_5411-6_1_3_node_134 | 0.4 | n |  | TRUE
119 | bus_LV_5411-6_1_3_node_147 | 0.4 | n |  | TRUE
120 | bus_LV_5411-6_1_3_node_84 | 0.4 | n |  | TRUE
121 | bus_LV_5411-6_1_3_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_5411-6_1_3_node_86 | 0.4 | n |  | TRUE
123 | bus_LV_5411-6_1_3_node_88 | 0.4 | n |  | TRUE
124 | bus_LV_5411-6_1_3_node_87 | 0.4 | n |  | TRUE
125 | bus_LV_5411-6_1_3_node_158 | 0.4 | n |  | TRUE
126 | bus_LV_5411-6_1_3_node_192 | 0.4 | n |  | TRUE
127 | bus_LV_5411-6_1_3_node_201 | 0.4 | n |  | TRUE
128 | bus_LV_5411-6_1_3_node_125 | 0.4 | n |  | TRUE
129 | bus_LV_5411-6_1_3_node_193 | 0.4 | n |  | TRUE
130 | bus_LV_5411-6_1_3_node_200 | 0.4 | n |  | TRUE
131 | bus_LV_5411-6_1_3_node_110 | 0.4 | n |  | TRUE
132 | bus_LV_5411-6_1_3_node_111 | 0.4 | n |  | TRUE
133 | bus_LV_5411-6_1_3_node_112 | 0.4 | n |  | TRUE
134 | bus_LV_5411-6_1_3_node_113 | 0.4 | n |  | TRUE
135 | bus_LV_5411-6_1_3_node_114 | 0.4 | n |  | TRUE
136 | bus_LV_5411-6_1_3_node_115 | 0.4 | n |  | TRUE
137 | bus_LV_5411-6_1_3_node_135 | 0.4 | n |  | TRUE
138 | bus_LV_5411-6_1_3_node_123 | 0.4 | n |  | TRUE
139 | bus_LV_5411-6_1_3_node_133 | 0.4 | n |  | TRUE
140 | bus_LV_5411-6_1_3_node_222 | 0.4 | n |  | TRUE
141 | bus_LV_5411-6_1_3_node_223 | 0.4 | n |  | TRUE
142 | bus_LV_5411-6_1_3_node_122 | 0.4 | n |  | TRUE
143 | bus_LV_5411-6_1_3_node_136 | 0.4 | n |  | TRUE
144 | bus_LV_5411-6_1_3_node_137 | 0.4 | n |  | TRUE
145 | bus_LV_5411-6_1_3_node_124 | 0.4 | n |  | TRUE
146 | bus_LV_5411-6_1_3_node_127 | 0.4 | n |  | TRUE
147 | bus_LV_5411-6_1_3_node_128 | 0.4 | n |  | TRUE
148 | bus_LV_5411-6_1_3_node_129 | 0.4 | n |  | TRUE
149 | bus_LV_5411-6_1_3_node_130 | 0.4 | n |  | TRUE
150 | bus_LV_5411-6_1_3_node_132 | 0.4 | n |  | TRUE
151 | bus_LV_5411-6_1_3_node_131 | 0.4 | n |  | TRUE
152 | bus_LV_5411-6_1_3_node_152 | 0.4 | n |  | TRUE
153 | bus_LV_5411-6_1_3_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_5411-6_1_3_node_161 | 0.4 | n |  | TRUE
155 | bus_LV_5411-6_1_3_node_162 | 0.4 | n |  | TRUE
156 | bus_LV_5411-6_1_3_node_170 | 0.4 | n |  | TRUE
157 | bus_MV_193_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5411-6_1_3_load_9 | 0 | 0.0023635 | 0.00059234 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5411-6_1_3_load_10 | 1 | 0.0029545 | 0.00074047 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5411-6_1_3_load_12 | 3 | 0.0022898 | 0.00057387 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5411-6_1_3_load_13 | 4 | 0.0010174 | 0.00025499 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5411-6_1_3_load_155 | 6 | 0.001778 | 0.00044562 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5411-6_1_3_load_120 | 8 | 0.0014395 | 0.00036077 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5411-6_1_3_load_121 | 9 | 0.0010224 | 0.00025623 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5411-6_1_3_load_116 | 10 | 0.0019467 | 0.00048788 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5411-6_1_3_load_153 | 11 | 0.00082631 | 0.00020709 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5411-6_1_3_load_154 | 12 | 0.001325 | 0.00033208 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5411-6_1_3_load_31 | 13 | 0.00038382 | 9.6195e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5411-6_1_3_load_70 | 15 | 0.0015342 | 0.00038452 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5411-6_1_3_load_32 | 16 | 0.00093107 | 0.00023335 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5411-6_1_3_load_220 | 17 | 0.00098113 | 0.00024589 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5411-6_1_3_load_68 | 19 | 0.0018066 | 0.00045278 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5411-6_1_3_load_15 | 20 | 0.0024712 | 0.00061935 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5411-6_1_3_load_16 | 21 | 0.0027501 | 0.00068925 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5411-6_1_3_load_17 | 22 | 0.0019698 | 0.00049367 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5411-6_1_3_load_145 | 25 | 0.001362 | 0.00034135 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5411-6_1_3_load_149 | 27 | 0.0016418 | 0.00041147 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5411-6_1_3_load_159 | 29 | 0.0024947 | 0.00062523 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5411-6_1_3_load_42 | 30 | 0.0014582 | 0.00036547 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5411-6_1_3_load_139 | 31 | 0.0016227 | 0.0004067 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5411-6_1_3_load_30 | 32 | 0.0025224 | 0.00063218 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5411-6_1_3_load_20 | 33 | 0.0023432 | 0.00058727 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5411-6_1_3_load_21 | 34 | 0.0017524 | 0.0004392 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5411-6_1_3_load_221 | 36 | 0.0018839 | 0.00047214 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5411-6_1_3_load_23 | 37 | 0.0010496 | 0.00026305 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5411-6_1_3_load_119 | 39 | 0.0041681 | 0.0010446 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5411-6_1_3_load_224 | 41 | 0.0012337 | 0.00030919 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5411-6_1_3_load_172 | 43 | 0.0011634 | 0.00029157 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5411-6_1_3_load_173 | 44 | 0.0014431 | 0.00036168 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5411-6_1_3_load_143 | 45 | 0.029201 | 0.0073186 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5411-6_1_3_load_208 | 46 | 0.0015874 | 0.00039783 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5411-6_1_3_load_171 | 48 | 0.0015792 | 0.00039578 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5411-6_1_3_load_24 | 49 | 0.0033736 | 0.0008455 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5411-6_1_3_load_142 | 50 | 0.0018674 | 0.000468 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5411-6_1_3_load_166 | 52 | 0.0013758 | 0.00034481 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5411-6_1_3_load_167 | 53 | 0.0016442 | 0.00041207 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5411-6_1_3_load_140 | 54 | 0.0057486 | 0.0014407 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5411-6_1_3_load_25 | 55 | 0.0012313 | 0.00030858 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5411-6_1_3_load_26 | 56 | 0.0019796 | 0.00049615 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5411-6_1_3_load_28 | 58 | 0.0019957 | 0.00050016 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5411-6_1_3_load_29 | 59 | 0.0026157 | 0.00065555 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5411-6_1_3_load_33 | 60 | 0.0039547 | 0.00099115 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5411-6_1_3_load_34 | 61 | 0.0012689 | 0.00031802 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5411-6_1_3_load_35 | 62 | 0.00076025 | 0.00019054 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5411-6_1_3_load_36 | 63 | 0.00090133 | 0.00022589 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5411-6_1_3_load_37 | 64 | 0.0012443 | 0.00031185 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5411-6_1_3_load_144 | 66 | 0.0021367 | 0.00053552 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5411-6_1_3_load_156 | 67 | 0.0023486 | 0.00058861 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5411-6_1_3_load_150 | 68 | 0.0012268 | 0.00030747 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5411-6_1_3_load_39 | 69 | 0.0016923 | 0.00042414 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5411-6_1_3_load_43 | 72 | 0.00061531 | 0.00015421 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5411-6_1_3_load_44 | 73 | 0.0019118 | 0.00047914 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5411-6_1_3_load_183 | 75 | 0.00080583 | 0.00020196 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5411-6_1_3_load_46 | 77 | 0.00033096 | 8.2945e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5411-6_1_3_load_182 | 78 | 0.00072968 | 0.00018288 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5411-6_1_3_load_58 | 79 | 0.0006339 | 0.00015887 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5411-6_1_3_load_61 | 81 | 0.00034306 | 8.5978e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5411-6_1_3_load_53 | 82 | 0.000984 | 0.00024661 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5411-6_1_3_load_54 | 83 | 0.00086619 | 0.00021709 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5411-6_1_3_load_55 | 84 | 0.00075039 | 0.00018806 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5411-6_1_3_load_57 | 86 | 0.0015843 | 0.00039706 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5411-6_1_3_load_165 | 87 | 0.0007022 | 0.00017599 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5411-6_1_3_load_169 | 88 | 0.00077414 | 0.00019402 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5411-6_1_3_load_62 | 89 | 0.00097572 | 0.00024454 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5411-6_1_3_load_63 | 90 | 0.00065253 | 0.00016354 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5411-6_1_3_load_64 | 91 | 0.00070609 | 0.00017696 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5411-6_1_3_load_66 | 93 | 0.0003345 | 8.3835e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5411-6_1_3_load_73 | 94 | 0.00039719 | 9.9544e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5411-6_1_3_load_74 | 95 | 0.0012993 | 0.00032562 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5411-6_1_3_load_82 | 97 | 0.00053174 | 0.00013327 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5411-6_1_3_load_92 | 99 | 0.0011074 | 0.00027753 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5411-6_1_3_load_76 | 100 | 0.0012252 | 0.00030707 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5411-6_1_3_load_67 | 101 | 0.00090885 | 0.00022778 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5411-6_1_3_load_72 | 104 | 0.001229 | 0.00030801 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5411-6_1_3_load_80 | 106 | 0.0014292 | 0.0003582 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5411-6_1_3_load_148 | 107 | 0.0019997 | 0.00050118 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5411-6_1_3_load_146 | 108 | 0.0016849 | 0.00042227 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5411-6_1_3_load_83 | 109 | 0.0010186 | 0.00025528 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5411-6_1_3_load_90 | 110 | 0.00060122 | 0.00015068 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5411-6_1_3_load_91 | 111 | 0.00092158 | 0.00023097 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5411-6_1_3_load_75 | 112 | 0.0012849 | 0.00032203 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5411-6_1_3_load_77 | 113 | 0.00040661 | 0.00010191 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5411-6_1_3_load_225 | 114 | 0.0013446 | 0.00033698 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5411-6_1_3_load_79 | 115 | 0.0013105 | 0.00032845 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5411-6_1_3_load_160 | 116 | 0.0012113 | 0.00030359 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5411-6_1_3_load_209 | 117 | 0.0021262 | 0.00053287 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5411-6_1_3_load_147 | 119 | 0.0010934 | 0.00027404 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5411-6_1_3_load_84 | 120 | 0.00095518 | 0.00023939 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5411-6_1_3_load_85 | 121 | 0.00089293 | 0.00022379 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5411-6_1_3_load_158 | 125 | 0.00090793 | 0.00022755 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5411-6_1_3_load_201 | 127 | 0.00060935 | 0.00015272 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5411-6_1_3_load_125 | 128 | 0.00044125 | 0.00011059 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5411-6_1_3_load_193 | 129 | 0.00071339 | 0.00017879 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5411-6_1_3_load_200 | 130 | 0.00043722 | 0.00010958 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5411-6_1_3_load_110 | 131 | 0.001777 | 0.00044537 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5411-6_1_3_load_111 | 132 | 0.0014267 | 0.00035757 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5411-6_1_3_load_113 | 134 | 0.0021187 | 0.00053099 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5411-6_1_3_load_115 | 136 | 0.001744 | 0.0004371 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5411-6_1_3_load_123 | 138 | 0.00079368 | 0.00019892 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5411-6_1_3_load_133 | 139 | 0.0018911 | 0.00047394 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5411-6_1_3_load_222 | 140 | 0.0027799 | 0.00069672 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5411-6_1_3_load_223 | 141 | 0.0020553 | 0.00051511 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5411-6_1_3_load_122 | 142 | 0.00071362 | 0.00017885 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5411-6_1_3_load_136 | 143 | 0.0014785 | 0.00037054 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5411-6_1_3_load_137 | 144 | 0.00048286 | 0.00012102 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5411-6_1_3_load_124 | 145 | 0.0011319 | 0.00028369 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5411-6_1_3_load_127 | 146 | 0.0010763 | 0.00026973 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5411-6_1_3_load_130 | 149 | 0.0017483 | 0.00043817 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5411-6_1_3_load_132 | 150 | 0.00053041 | 0.00013293 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5411-6_1_3_load_152 | 152 | 0.0018168 | 0.00045532 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5411-6_1_3_load_151 | 153 | 0.0028198 | 0.00070672 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5411-6_1_3_load_161 | 154 | 0.0013658 | 0.0003423 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5411-6_1_3_load_162 | 155 | 0.002083 | 0.00052205 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_5411-6_1_3_load_170 | 156 | 0.00074028 | 0.00018553 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5411-6_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5411-6_1_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.031888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5411-6_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.014746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5411-6_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_5411-6_1_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.027386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_5411-6_1_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.00014847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5411-6_1_3_line_6 | NAYY 4x150 SE | 4 | 13 | 0.023197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5411-6_1_3_line_7 | NAYY 4x150 SE | 5 | 14 | 0.036103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_5411-6_1_3_line_8 | NAYY 4x150 SE | 5 | 15 | 0.076778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5411-6_1_3_line_9 | NAYY 4x150 SE | 7 | 8 | 0.032513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5411-6_1_3_line_10 | NAYY 4x150 SE | 7 | 9 | 0.017336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5411-6_1_3_line_11 | NAYY 4x150 SE | 7 | 10 | 0.035239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_5411-6_1_3_line_12 | NAYY 4x150 SE | 8 | 143 | 0.0044408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5411-6_1_3_line_13 | NAYY 4x150 SE | 9 | 11 | 0.0028827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5411-6_1_3_line_14 | NAYY 4x150 SE | 10 | 38 | 0.030764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_5411-6_1_3_line_15 | NAYY 4x150 SE | 11 | 12 | 0.03008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5411-6_1_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5411-6_1_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.031796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5411-6_1_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.044091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_5411-6_1_3_line_19 | NAYY 4x150 SE | 15 | 19 | 0.028174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5411-6_1_3_line_20 | NAYY 4x150 SE | 16 | 59 | 0.072994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5411-6_1_3_line_21 | NAYY 4x150 SE | 18 | 53 | 0.050144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5411-6_1_3_line_22 | NAYY 4x150 SE | 18 | 49 | 0.02911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_5411-6_1_3_line_23 | NAYY 4x150 SE | 19 | 101 | 0.024465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5411-6_1_3_line_24 | NAYY 4x150 SE | 20 | 21 | 0.022421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5411-6_1_3_line_25 | NAYY 4x150 SE | 20 | 22 | 0.0013853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5411-6_1_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.021739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5411-6_1_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.019965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5411-6_1_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.023922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5411-6_1_3_line_29 | NAYY 4x150 SE | 23 | 26 | 0.06417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5411-6_1_3_line_30 | NAYY 4x150 SE | 24 | 27 | 0.027898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5411-6_1_3_line_31 | NAYY 4x150 SE | 24 | 28 | 0.005909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5411-6_1_3_line_32 | NAYY 4x150 SE | 25 | 29 | 0.021439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5411-6_1_3_line_33 | NAYY 4x150 SE | 26 | 30 | 0.052658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5411-6_1_3_line_34 | NAYY 4x150 SE | 28 | 31 | 0.018978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5411-6_1_3_line_35 | NAYY 4x150 SE | 28 | 32 | 0.011884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5411-6_1_3_line_36 | NAYY 4x150 SE | 30 | 70 | 0.14008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5411-6_1_3_line_37 | NAYY 4x150 SE | 32 | 57 | 0.029613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5411-6_1_3_line_38 | NAYY 4x150 SE | 33 | 34 | 0.028932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5411-6_1_3_line_39 | NAYY 4x150 SE | 33 | 35 | 0.0074447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5411-6_1_3_line_40 | NAYY 4x150 SE | 34 | 36 | 0.053852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5411-6_1_3_line_41 | NAYY 4x150 SE | 35 | 37 | 0.070336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5411-6_1_3_line_42 | NAYY 4x150 SE | 36 | 44 | 0.038754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5411-6_1_3_line_43 | NAYY 4x150 SE | 37 | 48 | 0.027722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5411-6_1_3_line_44 | NAYY 4x150 SE | 38 | 39 | 0.064199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_5411-6_1_3_line_45 | NAYY 4x150 SE | 39 | 54 | 0.031738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_5411-6_1_3_line_46 | NAYY 4x150 SE | 40 | 41 | 0.026327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5411-6_1_3_line_47 | NAYY 4x150 SE | 40 | 42 | 0.025366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5411-6_1_3_line_48 | NAYY 4x150 SE | 42 | 47 | 0.019904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5411-6_1_3_line_49 | NAYY 4x150 SE | 42 | 154 | 0.01474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5411-6_1_3_line_50 | NAYY 4x150 SE | 43 | 44 | 0.0055221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5411-6_1_3_line_51 | NAYY 4x150 SE | 43 | 45 | 0.051909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5411-6_1_3_line_52 | NAYY 4x150 SE | 45 | 51 | 0.051252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5411-6_1_3_line_53 | NAYY 4x150 SE | 46 | 47 | 0.02257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5411-6_1_3_line_54 | NAYY 4x150 SE | 47 | 65 | 0.017145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5411-6_1_3_line_55 | NAYY 4x150 SE | 48 | 52 | 0.016095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5411-6_1_3_line_56 | NAYY 4x150 SE | 49 | 50 | 0.073948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
57 | LV_5411-6_1_3_line_57 | NAYY 4x150 SE | 50 | 51 | 0.0029216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
58 | LV_5411-6_1_3_line_58 | NAYY 4x150 SE | 51 | 54 | 0.0035541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_5411-6_1_3_line_59 | NAYY 4x150 SE | 52 | 85 | 0.057578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5411-6_1_3_line_60 | NAYY 4x150 SE | 55 | 56 | 0.018658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5411-6_1_3_line_61 | NAYY 4x150 SE | 55 | 57 | 0.0039416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5411-6_1_3_line_62 | NAYY 4x150 SE | 56 | 58 | 0.018417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5411-6_1_3_line_63 | NAYY 4x150 SE | 57 | 59 | 0.0083056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5411-6_1_3_line_64 | NAYY 4x150 SE | 58 | 60 | 0.026994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5411-6_1_3_line_65 | NAYY 4x150 SE | 61 | 62 | 0.010864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5411-6_1_3_line_66 | NAYY 4x150 SE | 61 | 63 | 0.019406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5411-6_1_3_line_67 | NAYY 4x150 SE | 62 | 64 | 0.021533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_5411-6_1_3_line_68 | NAYY 4x150 SE | 63 | 65 | 0.0079756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_5411-6_1_3_line_69 | NAYY 4x150 SE | 64 | 66 | 0.023912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_5411-6_1_3_line_70 | NAYY 4x150 SE | 65 | 67 | 0.03124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_5411-6_1_3_line_71 | NAYY 4x150 SE | 66 | 68 | 0.017268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_5411-6_1_3_line_72 | NAYY 4x150 SE | 68 | 151 | 0.027985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_5411-6_1_3_line_73 | NAYY 4x150 SE | 69 | 70 | 0.20898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_5411-6_1_3_line_74 | NAYY 4x150 SE | 69 | 71 | 0.026803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_5411-6_1_3_line_75 | NAYY 4x150 SE | 71 | 72 | 0.123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_5411-6_1_3_line_76 | NAYY 4x150 SE | 71 | 73 | 0.097388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_5411-6_1_3_line_77 | NAYY 4x150 SE | 73 | 74 | 0.11997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_5411-6_1_3_line_78 | NAYY 4x150 SE | 74 | 75 | 0.10491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_5411-6_1_3_line_79 | NAYY 4x150 SE | 75 | 78 | 0.10579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_5411-6_1_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.029478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_5411-6_1_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.1306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_5411-6_1_3_line_82 | NAYY 4x150 SE | 77 | 79 | 0.0633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_5411-6_1_3_line_83 | NAYY 4x150 SE | 79 | 80 | 0.052999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_5411-6_1_3_line_84 | NAYY 4x150 SE | 80 | 81 | 0.0054489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_5411-6_1_3_line_85 | NAYY 4x150 SE | 82 | 83 | 0.0019351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_5411-6_1_3_line_86 | NAYY 4x150 SE | 82 | 84 | 0.01659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_5411-6_1_3_line_87 | NAYY 4x150 SE | 83 | 85 | 0.031916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_5411-6_1_3_line_88 | NAYY 4x150 SE | 84 | 86 | 0.015137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_5411-6_1_3_line_89 | NAYY 4x150 SE | 85 | 87 | 0.015278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_5411-6_1_3_line_90 | NAYY 4x150 SE | 87 | 88 | 0.02346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_5411-6_1_3_line_91 | NAYY 4x150 SE | 88 | 156 | 0.093708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_5411-6_1_3_line_92 | NAYY 4x150 SE | 89 | 90 | 0.027213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_5411-6_1_3_line_93 | NAYY 4x150 SE | 89 | 91 | 0.0013841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_5411-6_1_3_line_94 | NAYY 4x150 SE | 90 | 92 | 0.019917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_5411-6_1_3_line_95 | NAYY 4x150 SE | 91 | 93 | 0.012396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_5411-6_1_3_line_96 | NAYY 4x150 SE | 92 | 94 | 0.010644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_5411-6_1_3_line_97 | NAYY 4x150 SE | 92 | 95 | 0.021536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_5411-6_1_3_line_98 | NAYY 4x150 SE | 93 | 96 | 0.003596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_5411-6_1_3_line_99 | NAYY 4x150 SE | 94 | 97 | 0.0048621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_5411-6_1_3_line_100 | NAYY 4x150 SE | 95 | 98 | 0.010929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_5411-6_1_3_line_101 | NAYY 4x150 SE | 96 | 99 | 0.033136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_5411-6_1_3_line_102 | NAYY 4x150 SE | 96 | 100 | 0.044341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_5411-6_1_3_line_103 | NAYY 4x150 SE | 97 | 109 | 0.017141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_5411-6_1_3_line_104 | NAYY 4x150 SE | 98 | 110 | 0.034909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_5411-6_1_3_line_105 | NAYY 4x150 SE | 98 | 111 | 0.028927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_5411-6_1_3_line_106 | NAYY 4x150 SE | 99 | 117 | 0.006115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_5411-6_1_3_line_107 | NAYY 4x150 SE | 100 | 112 | 0.035531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_5411-6_1_3_line_108 | NAYY 4x150 SE | 101 | 102 | 0.012567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_5411-6_1_3_line_109 | NAYY 4x150 SE | 102 | 103 | 0.008266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_5411-6_1_3_line_110 | NAYY 4x150 SE | 102 | 104 | 0.038214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_5411-6_1_3_line_111 | NAYY 4x150 SE | 103 | 105 | 0.021449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_5411-6_1_3_line_112 | NAYY 4x150 SE | 103 | 106 | 0.012851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_5411-6_1_3_line_113 | NAYY 4x150 SE | 105 | 107 | 0.042214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_5411-6_1_3_line_114 | NAYY 4x150 SE | 105 | 108 | 0.019402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_5411-6_1_3_line_115 | NAYY 4x150 SE | 108 | 119 | 0.021214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_5411-6_1_3_line_116 | NAYY 4x150 SE | 109 | 120 | 0.013483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_5411-6_1_3_line_117 | NAYY 4x150 SE | 112 | 113 | 0.040891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_5411-6_1_3_line_118 | NAYY 4x150 SE | 112 | 114 | 0.16113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_5411-6_1_3_line_119 | NAYY 4x150 SE | 113 | 115 | 0.0026255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_5411-6_1_3_line_120 | NAYY 4x150 SE | 115 | 116 | 0.05284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_5411-6_1_3_line_121 | NAYY 4x150 SE | 116 | 118 | 0.024249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_5411-6_1_3_line_122 | NAYY 4x150 SE | 118 | 119 | 0.0094059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_5411-6_1_3_line_123 | NAYY 4x150 SE | 118 | 139 | 0.025099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_5411-6_1_3_line_124 | NAYY 4x150 SE | 120 | 121 | 0.01948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_5411-6_1_3_line_125 | NAYY 4x150 SE | 121 | 122 | 0.061269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_5411-6_1_3_line_126 | NAYY 4x150 SE | 122 | 123 | 0.032108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_5411-6_1_3_line_127 | NAYY 4x150 SE | 123 | 127 | 0.28193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_5411-6_1_3_line_128 | NAYY 4x150 SE | 124 | 125 | 0.021532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_5411-6_1_3_line_129 | NAYY 4x150 SE | 124 | 126 | 0.10576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_5411-6_1_3_line_130 | NAYY 4x150 SE | 125 | 128 | 0.017524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_5411-6_1_3_line_131 | NAYY 4x150 SE | 126 | 129 | 0.039373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_5411-6_1_3_line_132 | NAYY 4x150 SE | 127 | 130 | 0.1366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_5411-6_1_3_line_133 | NAYY 4x150 SE | 128 | 145 | 0.022759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_5411-6_1_3_line_134 | NAYY 4x150 SE | 131 | 132 | 0.010527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_5411-6_1_3_line_135 | NAYY 4x150 SE | 131 | 133 | 0.019384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_5411-6_1_3_line_136 | NAYY 4x150 SE | 132 | 134 | 0.018894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_5411-6_1_3_line_137 | NAYY 4x150 SE | 133 | 135 | 0.017265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_5411-6_1_3_line_138 | NAYY 4x150 SE | 133 | 136 | 0.023477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_5411-6_1_3_line_139 | NAYY 4x150 SE | 135 | 137 | 0.003054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_5411-6_1_3_line_140 | NAYY 4x150 SE | 135 | 138 | 0.057466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_5411-6_1_3_line_141 | NAYY 4x150 SE | 136 | 139 | 0.0089377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_5411-6_1_3_line_142 | NAYY 4x150 SE | 137 | 140 | 0.017868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_5411-6_1_3_line_143 | NAYY 4x150 SE | 137 | 141 | 0.032771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_5411-6_1_3_line_144 | NAYY 4x150 SE | 138 | 142 | 0.030161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_5411-6_1_3_line_145 | NAYY 4x150 SE | 142 | 145 | 0.0016315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_5411-6_1_3_line_146 | NAYY 4x150 SE | 143 | 144 | 0.0070356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_5411-6_1_3_line_147 | NAYY 4x150 SE | 144 | 150 | 0.018427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_5411-6_1_3_line_148 | NAYY 4x150 SE | 146 | 147 | 0.021262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_5411-6_1_3_line_149 | NAYY 4x150 SE | 146 | 148 | 0.0025617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_5411-6_1_3_line_150 | NAYY 4x150 SE | 147 | 149 | 0.0043705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_5411-6_1_3_line_151 | NAYY 4x150 SE | 148 | 150 | 0.020234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_5411-6_1_3_line_152 | NAYY 4x150 SE | 148 | 151 | 0.020758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_5411-6_1_3_line_153 | NAYY 4x150 SE | 149 | 152 | 0.0074282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_5411-6_1_3_line_154 | NAYY 4x150 SE | 152 | 153 | 0.02034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_5411-6_1_3_line_155 | NAYY 4x150 SE | 154 | 155 | 0.035168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5411-6_1_3_trafo_13 | 0.25 MVA 20/0.4 kV | 157 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2579491.0836 | 1133229.0274 | 2579488.1206 | 1133228.4029 | 2579480.9671 | 1133225.5037 | 2579476.4834 | 1133222.2062 | 2579474.4261 | 1133217.1218 | 2579474.7936 | 1133212.0292 | 2579475.5897 | 1133209.4099
1 | 2579522.5325 | 1133233.655 | 2579518.6411 | 1133232.4898 | 2579508.8094 | 1133232.0231 | 2579496.4249 | 1133230.1533 | 2579491.0836 | 1133229.0274
2 | 2579480.0481 | 1133195.3552 | 2579477.1915 | 1133204.1394 | 2579475.5897 | 1133209.4099
3 | 2579522.5325 | 1133233.655 | 2579526.0132 | 1133227.2511 | 2579529.9605 | 1133222.2129 | 2579534.0952 | 1133217.9746 | 2579538.4024 | 1133215.035
4 | 2579522.5325 | 1133233.655 | 2579521.2308 | 1133235.6937 | 2579517.5793 | 1133246.1891 | 2579511.2398 | 1133258.5167
5 | 2579480.094 | 1133195.214 | 2579480.0481 | 1133195.3552
6 | 2579559.5853 | 1133205.6786 | 2579547.3563 | 1133210.5036 | 2579539.6939 | 1133214.1536 | 2579538.4024 | 1133215.035
7 | 2579482.9612 | 1133279.7458 | 2579487.0722 | 1133277.6196 | 2579496.1032 | 1133273.5201 | 2579502.4328 | 1133269.5966 | 2579506.4819 | 1133265.0917 | 2579511.2398 | 1133258.5167
8 | 2579511.2398 | 1133258.5167 | 2579525.4282 | 1133263.4375 | 2579536.1393 | 1133266.6916 | 2579546.9634 | 1133269.256 | 2579553.8247 | 1133269.9997 | 2579559.4173 | 1133268.9247 | 2579567.611 | 1133265.3395 | 2579583.2721 | 1133256.6661
9 | 2579323.7916 | 1133160.3875 | 2579327.584 | 1133155.1274 | 2579335.8003 | 1133144.6718 | 2579344.3706 | 1133135.2577
10 | 2579323.7916 | 1133160.3875 | 2579315.4524 | 1133155.2247 | 2579308.3097 | 1133152.8467
11 | 2579323.7916 | 1133160.3875 | 2579311.1426 | 1133177.9173 | 2579304.0965 | 1133189.5754
12 | 2579347.3217 | 1133131.9393 | 2579344.9878 | 1133134.5797 | 2579344.3706 | 1133135.2577
13 | 2579305.5746 | 1133151.9361 | 2579308.3097 | 1133152.8467
14 | 2579285.7231 | 1133213.3889 | 2579292.7357 | 1133208.8737 | 2579297.9051 | 1133201.1298 | 2579302.9219 | 1133191.519 | 2579304.0965 | 1133189.5754
15 | 2579287.7161 | 1133134.9435 | 2579285.4708 | 1133142.3659 | 2579289.6053 | 1133144.8196 | 2579300.7787 | 1133150.3394 | 2579305.5746 | 1133151.9361
16 | 2579576.5298 | 1133198.9251 | 2579561.1401 | 1133205.0652 | 2579559.5853 | 1133205.6786
17 | 2579482.9612 | 1133279.7458 | 2579487.2266 | 1133284.5002 | 2579498.2647 | 1133291.1214 | 2579509.8284 | 1133296.1289
18 | 2579482.9612 | 1133279.7458 | 2579473.3252 | 1133284.7366 | 2579455.562 | 1133290.2111 | 2579442.2047 | 1133296.4931
19 | 2579608.6958 | 1133244.5285 | 2579599.8082 | 1133248.6665 | 2579583.7076 | 1133256.4249 | 2579583.2721 | 1133256.6661
20 | 2579576.5298 | 1133198.9251 | 2579589.9451 | 1133193.5729 | 2579616.9741 | 1133180.4414 | 2579643.635 | 1133170.3688
21 | 2579442.2047 | 1133296.4931 | 2579443.856 | 1133299.9003 | 2579441.8857 | 1133302.2415 | 2579432.343 | 1133309.7444 | 2579425.5069 | 1133316.3377 | 2579417.1337 | 1133323.6477 | 2579407.4709 | 1133327.8734
22 | 2579442.2047 | 1133296.4931 | 2579427.9022 | 1133303.2231 | 2579416.1428 | 1133309.4439
23 | 2579608.6958 | 1133244.5285 | 2579610.2223 | 1133243.8177 | 2579621.808 | 1133241.6663 | 2579632.7237 | 1133240.3328
24 | 2579719.0546 | 1133157.0151 | 2579730.9151 | 1133156.5781 | 2579741.4274 | 1133155.6534
25 | 2579719.0546 | 1133157.0151 | 2579717.6702 | 1133157.0661
26 | 2579756.3889 | 1133140.9402 | 2579751.3738 | 1133148.9944 | 2579748.3674 | 1133152.3061 | 2579745.3951 | 1133154.3282 | 2579741.4274 | 1133155.6534 | 2579741.4274 | 1133155.6534
27 | 2579697.7179 | 1133157.7684 | 2579710.6567 | 1133157.3245 | 2579717.6702 | 1133157.0661
28 | 2579756.3889 | 1133140.9402 | 2579764.694 | 1133145.2366 | 2579771.3469 | 1133148.0823 | 2579777.1425 | 1133150.0638 | 2579778.3245 | 1133150.3234
29 | 2579756.3889 | 1133140.9402 | 2579740.4577 | 1133130.5999 | 2579722.6819 | 1133116.5306 | 2579714.0865 | 1133110.6678 | 2579703.1676 | 1133105.1686
30 | 2579701.9905 | 1133130.4628 | 2579699.9178 | 1133136.7395 | 2579698.1252 | 1133143.8713 | 2579697.4862 | 1133150.7102 | 2579697.7179 | 1133157.7684
31 | 2579691.8074 | 1133158.1997 | 2579697.7179 | 1133157.7684
32 | 2579799.2645 | 1133154.9227 | 2579778.3245 | 1133150.3234
33 | 2579703.1676 | 1133105.1686 | 2579713.6805 | 1133104.3994 | 2579740.7358 | 1133103.4634 | 2579755.7725 | 1133102.9434
34 | 2579691.8074 | 1133158.1997 | 2579689.5751 | 1133149.125 | 2579687.7408 | 1133143.9064 | 2579685.6424 | 1133142.5795 | 2579684.0265 | 1133142.7739
35 | 2579691.8074 | 1133158.1997 | 2579683.2674 | 1133159.607 | 2579680.098 | 1133160.2224
36 | 2579894.5293 | 1133120.3558 | 2579849.692 | 1133114.5029 | 2579771.3626 | 1133102.4042 | 2579755.7725 | 1133102.9434
37 | 2579651.4401 | 1133167.5295 | 2579662.7977 | 1133163.8893 | 2579672.6051 | 1133161.6773 | 2579680.098 | 1133160.2224
38 | 2579322.6081 | 1133338.0272 | 2579312.3699 | 1133340.004 | 2579294.4938 | 1133343.9007 | 2579294.2969 | 1133343.9692
39 | 2579329.9246 | 1133336.6531 | 2579328.4321 | 1133336.9028 | 2579322.6081 | 1133338.0272
40 | 2579294.2969 | 1133343.9692 | 2579266.0316 | 1133298.1318
41 | 2579329.9246 | 1133336.6531 | 2579329.674 | 1133339.8889 | 2579326.8184 | 1133342.2221 | 2579321.0264 | 1133347.9448 | 2579314.6138 | 1133354.559 | 2579309.3621 | 1133360.7245 | 2579308.9273 | 1133364.1054 | 2579309.3004 | 1133367.4058 | 2579311.8141 | 1133370.8655 | 2579314.3198 | 1133372.0241 | 2579320.1312 | 1133371.9152 | 2579338.4915 | 1133371.3363
42 | 2579278.3985 | 1133261.4044 | 2579266.0316 | 1133298.1318
43 | 2579365.8412 | 1133366.9743 | 2579354.1693 | 1133369.386 | 2579339.5195 | 1133371.3039 | 2579338.4915 | 1133371.3363
44 | 2579285.7231 | 1133213.3889 | 2579290.4559 | 1133217.4524 | 2579299.9226 | 1133221.444 | 2579311.9527 | 1133225.4268 | 2579323.9883 | 1133228.776 | 2579337.5871 | 1133232.2977 | 2579345.8916 | 1133233.9895
45 | 2579376.8029 | 1133241.1588 | 2579376.707 | 1133241.1234 | 2579366.4224 | 1133238.7797 | 2579353.4711 | 1133235.5336 | 2579345.8916 | 1133233.9895
46 | 2579223.8075 | 1133027.9556 | 2579217.7489 | 1133041.2831 | 2579215.0584 | 1133049.074 | 2579212.4412 | 1133051.3286
47 | 2579212.4412 | 1133051.3286 | 2579221.3652 | 1133060.8135 | 2579229.0275 | 1133070.5252
48 | 2579229.0275 | 1133070.5252 | 2579235.9436 | 1133078.1384 | 2579241.6747 | 1133081.4758 | 2579244.4196 | 1133082.7336
49 | 2579229.0275 | 1133070.5252 | 2579236.3386 | 1133065.4641 | 2579241.2923 | 1133062.3561
50 | 2579278.3985 | 1133261.4044 | 2579283.7902 | 1133260.2114
51 | 2579330.3231 | 1133239.5285 | 2579328.6138 | 1133239.7321 | 2579321.5514 | 1133240.9459 | 2579315.4177 | 1133243.6239 | 2579308.4631 | 1133249.3172 | 2579303.8811 | 1133253.2683 | 2579298.7546 | 1133255.5759 | 2579292.7948 | 1133257.3306 | 2579284.2675 | 1133260.1058 | 2579283.7902 | 1133260.2114
52 | 2579380.1369 | 1133242.39 | 2579377.5493 | 1133244.322 | 2579372.9624 | 1133244.6157 | 2579366.9939 | 1133243.8135 | 2579358.4464 | 1133240.7302 | 2579349.1736 | 1133239.3947 | 2579338.8939 | 1133238.5073 | 2579330.3231 | 1133239.5285
53 | 2579244.4196 | 1133082.7336 | 2579242.5908 | 1133090.3881 | 2579239.2291 | 1133104.6987
54 | 2579261.3758 | 1133081.9748 | 2579255.2297 | 1133083.3411 | 2579248.2329 | 1133083.5431 | 2579244.4196 | 1133082.7336
55 | 2579365.8412 | 1133366.9743 | 2579367.2999 | 1133366.6729 | 2579376.7698 | 1133364.9396 | 2579381.6903 | 1133364.1835
56 | 2579416.1428 | 1133309.4439 | 2579382.8784 | 1133243.4
57 | 2579380.1369 | 1133242.39 | 2579382.8784 | 1133243.4
58 | 2579380.1369 | 1133242.39 | 2579376.8029 | 1133241.1588
59 | 2579438.1956 | 1133353.1791 | 2579426.9652 | 1133355.5965 | 2579402.4039 | 1133360.6719 | 2579386.2407 | 1133363.4842 | 2579381.6903 | 1133364.1835
60 | 2579630.4865 | 1133167.7815 | 2579636.3958 | 1133166.7578 | 2579644.202 | 1133164.6415 | 2579648.7745 | 1133164.626
61 | 2579651.4401 | 1133167.5295 | 2579648.7745 | 1133164.626 | 2579648.7745 | 1133164.626
62 | 2579616.3078 | 1133161.2909 | 2579616.7585 | 1133162.2666 | 2579618.8668 | 1133166.5282 | 2579621.2608 | 1133168.799 | 2579628.0176 | 1133168.2091 | 2579630.4865 | 1133167.7815
63 | 2579651.4401 | 1133167.5295 | 2579644.0515 | 1133170.2114 | 2579643.635 | 1133170.3688
64 | 2579607.2391 | 1133135.897 | 2579610.1218 | 1133143.7688 | 2579614.2615 | 1133156.8613 | 2579616.3078 | 1133161.2909
65 | 2579288.257 | 1133076.7631 | 2579298.9221 | 1133074.6953
66 | 2579288.257 | 1133076.7631 | 2579269.2056 | 1133080.4568
67 | 2579298.9221 | 1133074.6953 | 2579303.756 | 1133073.7582 | 2579320.1635 | 1133071.1801
68 | 2579261.3758 | 1133081.9748 | 2579269.2056 | 1133080.4568
69 | 2579343.6841 | 1133067.311 | 2579342.9165 | 1133067.1759 | 2579333.7366 | 1133068.3191 | 2579325.0219 | 1133070.4167 | 2579320.1635 | 1133071.1801
70 | 2579261.3758 | 1133081.9748 | 2579264.6058 | 1133087.7665 | 2579266.2317 | 1133094.9422 | 2579266.7307 | 1133101.2436 | 2579266.1146 | 1133107.8601 | 2579265.0741 | 1133112.016
71 | 2579359.6867 | 1133073.4225 | 2579354.0669 | 1133070.4837 | 2579348.6165 | 1133068.1791 | 2579343.6841 | 1133067.311
72 | 2579384.8496 | 1133085.6634 | 2579363.7608 | 1133075.553 | 2579359.6867 | 1133073.4225
73 | 2579894.5293 | 1133120.3558 | 2579900.5731 | 1133116.0112 | 2579915.7547 | 1133097.9405 | 2579922.3743 | 1133090.8038 | 2579927.1297 | 1133087.9199 | 2579932.6809 | 1133085.8781 | 2579943.7385 | 1133084.5406 | 2579956.7768 | 1133083.8968 | 2579963.7492 | 1133083.2733 | 2579968.4955 | 1133082.2681 | 2579972.5903 | 1133079.7755 | 2579977.1982 | 1133062.6184 | 2579978.4737 | 1133045.7281 | 2579977.3436 | 1133039.2508 | 2579973.8594 | 1133030.9028 | 2579970.4324 | 1133028.1906 | 2579952.9171 | 1133018.3441 | 2579940.2893 | 1133005.9246 | 2579934.3287 | 1132998.3407 | 2579930.5539 | 1132990.5939 | 2579929.721 | 1132985.5387
74 | 2579944.9851 | 1132964.3551 | 2579937.8397 | 1132970.8377 | 2579933.0804 | 1132977.2123 | 2579930.3001 | 1132981.4347 | 2579929.721 | 1132985.5387
75 | 2579944.9851 | 1132964.3551 | 2579960.9882 | 1132959.3216 | 2579978.4454 | 1132953.9942 | 2580011.1122 | 1132945.7259 | 2580026.6737 | 1132944.4514 | 2580044.3908 | 1132945.4931 | 2580065.2946 | 1132945.9665
76 | 2579944.9851 | 1132964.3551 | 2579994.0728 | 1132914.6562 | 2580006.1365 | 1132907.9016 | 2580019.7096 | 1132905.9809
77 | 2580137.5107 | 1132892.6257 | 2580093.8595 | 1132889.6796 | 2580087.388 | 1132890.5125 | 2580055.6901 | 1132900.8893 | 2580019.7096 | 1132905.9809
78 | 2580137.5107 | 1132892.6257 | 2580157.7749 | 1132891.0024 | 2580166.1274 | 1132888.6293 | 2580178.2553 | 1132882.553 | 2580190.1791 | 1132877.6113 | 2580199.1154 | 1132874.8583 | 2580208.2407 | 1132875.7065 | 2580216.3003 | 1132877.9033 | 2580225.3412 | 1132881.164 | 2580232.7349 | 1132884.5303 | 2580236.8235 | 1132887.082
79 | 2580328.0689 | 1132929.3692 | 2580323.0774 | 1132925.4654 | 2580318.2068 | 1132921.5127 | 2580313.728 | 1132917.2697 | 2580308.569 | 1132914.5741 | 2580300.7028 | 1132912.6656 | 2580291.7675 | 1132913.373 | 2580284.0045 | 1132914.7547 | 2580277.2032 | 1132913.6209 | 2580267.3824 | 1132909.5844 | 2580258.7295 | 1132904.866 | 2580251.4359 | 1132901.4994 | 2580247.2462 | 1132898.6118 | 2580242.759 | 1132891.8565 | 2580239.0605 | 1132888.4781 | 2580236.8235 | 1132887.082
80 | 2580354.8934 | 1133057.1817 | 2580327.8577 | 1133068.9313
81 | 2580328.0689 | 1132929.3692 | 2580354.8934 | 1133057.1817
82 | 2580327.8577 | 1133068.9313 | 2580352.6378 | 1133087.793 | 2580343.8147 | 1133118.7173
83 | 2580331.2218 | 1133170.1367 | 2580333.9516 | 1133162.1684 | 2580341.0693 | 1133128.3396 | 2580343.8147 | 1133118.7173
84 | 2580331.2218 | 1133170.1367 | 2580326.9064 | 1133173.4636
85 | 2579419.6909 | 1133378.1823 | 2579421.4334 | 1133377.3408
86 | 2579404.3137 | 1133384.3328 | 2579413.5356 | 1133381.155 | 2579419.6909 | 1133378.1823
87 | 2579438.1956 | 1133353.1791 | 2579439.1007 | 1133356.7445 | 2579438.312 | 1133360.2267 | 2579435.4668 | 1133365.5835 | 2579431.7275 | 1133370.5876 | 2579424.6864 | 1133375.7698 | 2579421.4334 | 1133377.3408
88 | 2579389.5038 | 1133386.9617 | 2579399.427 | 1133386.0168 | 2579404.3137 | 1133384.3328
89 | 2579438.1956 | 1133353.1791 | 2579448.849 | 1133350.8861 | 2579453.1376 | 1133349.9954
90 | 2579453.1376 | 1133349.9954 | 2579466.2643 | 1133347.2693 | 2579476.189 | 1133345.6678
91 | 2579510.2513 | 1133352.4663 | 2579520.4362 | 1133350.464 | 2579529.9851 | 1133347.052 | 2579533.5599 | 1133345.6948 | 2579535.9557 | 1133341.6846 | 2579536.1316 | 1133339.0939 | 2579533.8825 | 1133336.4336 | 2579528.7929 | 1133336.0062 | 2579521.4604 | 1133337.0094 | 2579512.5298 | 1133338.9074 | 2579501.4611 | 1133341.3575 | 2579487.1674 | 1133343.8963 | 2579476.189 | 1133345.6678
92 | 2579812.2095 | 1133318.9346 | 2579823.6851 | 1133322.3923 | 2579837.9212 | 1133327.7968
93 | 2579812.2095 | 1133318.9346 | 2579810.8843 | 1133318.5353
94 | 2579856.9448 | 1133333.2306 | 2579855.3363 | 1133333.3138 | 2579850.4141 | 1133332.3076 | 2579839.6783 | 1133328.4639 | 2579837.9212 | 1133327.7968
95 | 2579799.0149 | 1133314.959 | 2579810.8843 | 1133318.5353
96 | 2579856.9448 | 1133333.2306 | 2579858.4712 | 1133331.6025 | 2579859.8955 | 1133329.3522 | 2579861.8318 | 1133323.9393
97 | 2579856.9448 | 1133333.2306 | 2579857.3918 | 1133335.6859 | 2579857.3243 | 1133340.8108 | 2579856.6598 | 1133346.9605 | 2579854.6121 | 1133354.414
98 | 2579795.5449 | 1133314.0159 | 2579798.8733 | 1133314.9163 | 2579799.0149 | 1133314.959
99 | 2579863.3002 | 1133319.3073 | 2579862.6028 | 1133321.7838 | 2579861.8318 | 1133323.9393
100 | 2579850.3371 | 1133364.4681 | 2579854.4924 | 1133354.8494 | 2579854.6121 | 1133354.414
101 | 2579795.5449 | 1133314.0159 | 2579794.4187 | 1133317.9105 | 2579791.738 | 1133324.2115 | 2579787.0739 | 1133333.5873 | 2579784.2096 | 1133340.2558 | 2579781.888 | 1133344.1161
102 | 2579795.5449 | 1133314.0159 | 2579784.45 | 1133311.0184 | 2579774.2721 | 1133310.5746 | 2579767.9264 | 1133312.03 | 2579760.0218 | 1133316.8923 | 2579755.7311 | 1133320.5752 | 2579754.7167 | 1133321.2442
103 | 2579863.3002 | 1133319.3073 | 2579864.5579 | 1133314.8405 | 2579866.7967 | 1133309.8639 | 2579870.6653 | 1133306.5827 | 2579872.4256 | 1133305.6962
104 | 2579850.3371 | 1133364.4681 | 2579844.835 | 1133362.6856 | 2579837.8238 | 1133360.7971 | 2579832.8793 | 1133360.0466 | 2579829.6706 | 1133360.3909 | 2579827.95 | 1133361.4972 | 2579827.1016 | 1133363.3009 | 2579827.4447 | 1133366.9238 | 2579828.8038 | 1133372.7888
105 | 2579850.3371 | 1133364.4681 | 2579855.6763 | 1133368.1743 | 2579861.659 | 1133370.9445 | 2579867.7844 | 1133374.9704 | 2579869.7949 | 1133377.6872 | 2579870.2559 | 1133379.72 | 2579869.4653 | 1133382.7019
106 | 2579778.7364 | 1133349.3564 | 2579781.888 | 1133344.1161
107 | 2579720.3377 | 1133327.6423 | 2579728.374 | 1133327.6152 | 2579741.0715 | 1133326.483 | 2579747.2168 | 1133324.9616 | 2579751.7833 | 1133323.1787 | 2579754.7167 | 1133321.2442
108 | 2579645.2237 | 1133239.0524 | 2579637.2512 | 1133239.7797 | 2579632.7237 | 1133240.3328
109 | 2579653.4826 | 1133238.8132 | 2579650.3796 | 1133238.5792 | 2579645.2237 | 1133239.0524
110 | 2579645.2237 | 1133239.0524 | 2579645.2388 | 1133243.5323 | 2579644.2686 | 1133250.2834 | 2579640.5184 | 1133263.5248 | 2579639.1783 | 1133267.8537 | 2579633.0029 | 1133273.867
111 | 2579653.4826 | 1133238.8132 | 2579659.165 | 1133239.2276 | 2579666.6118 | 1133242.3817 | 2579673.9787 | 1133244.6913
112 | 2579653.4826 | 1133238.8132 | 2579653.8756 | 1133236.6664 | 2579655.8553 | 1133234.7699 | 2579661.3537 | 1133233.1394 | 2579663.4934 | 1133232.6633
113 | 2579673.9787 | 1133244.6913 | 2579673.2708 | 1133249.3182 | 2579671.9054 | 1133273.5236 | 2579671.0252 | 1133279.5518 | 2579669.4968 | 1133282.8808 | 2579667.3432 | 1133285.6783
114 | 2579673.9787 | 1133244.6913 | 2579679.3729 | 1133246.3739 | 2579691.1643 | 1133248.1683 | 2579692.9727 | 1133248.4117
115 | 2579692.9727 | 1133248.4117 | 2579707.1985 | 1133250.3264 | 2579713.8766 | 1133251.894
116 | 2579885.5569 | 1133305.5101 | 2579885.5569 | 1133305.5101 | 2579881.3194 | 1133304.4015 | 2579877.2242 | 1133304.3819 | 2579873.5318 | 1133305.1391 | 2579872.4256 | 1133305.6962
117 | 2579685.8746 | 1133319.0817 | 2579685.8769 | 1133319.1099 | 2579686.8464 | 1133323.5311 | 2579687.5375 | 1133325.3074 | 2579688.905 | 1133326.7924 | 2579691.5749 | 1133328.6954 | 2579694.3109 | 1133329.6978 | 2579697.7296 | 1133329.9642 | 2579704.1372 | 1133328.5863 | 2579716.358 | 1133327.6557 | 2579720.3377 | 1133327.6423
118 | 2579720.3377 | 1133327.6423 | 2579669.3952 | 1133480.5116
119 | 2579685.6602 | 1133316.4649 | 2579685.8746 | 1133319.0817
120 | 2579685.6602 | 1133316.4649 | 2579685.6602 | 1133316.4649 | 2579686.3393 | 1133314.684 | 2579688.7817 | 1133310.796 | 2579691.7119 | 1133307.7291 | 2579695.7292 | 1133305.1921 | 2579701.7322 | 1133302.526 | 2579706.7708 | 1133299.2408 | 2579709.6315 | 1133296.0962 | 2579713.0177 | 1133289.0036 | 2579717.3977 | 1133277.1306
121 | 2579723.1058 | 1133253.6744 | 2579722.0807 | 1133262.4266 | 2579718.7006 | 1133273.599 | 2579717.3977 | 1133277.1306
122 | 2579723.1058 | 1133253.6744 | 2579718.1227 | 1133252.8908 | 2579713.8766 | 1133251.894
123 | 2579723.1058 | 1133253.6744 | 2579743.8334 | 1133257.4731 | 2579747.8135 | 1133258.0809
124 | 2579885.5569 | 1133305.5101 | 2579889.866 | 1133307.33 | 2579894.1797 | 1133310.5171 | 2579900.1349 | 1133316.5557 | 2579900.7874 | 1133317.2572
125 | 2579949.2745 | 1133352.6651 | 2579943.7384 | 1133352.2389 | 2579939.9898 | 1133349.9836 | 2579934.5088 | 1133345.2996 | 2579925.0658 | 1133339.0058 | 2579916.4482 | 1133333.2428 | 2579911.8552 | 1133329.3784 | 2579906.5779 | 1133323.4821 | 2579900.7874 | 1133317.2572
126 | 2579955.776 | 1133384.0922 | 2579953.0997 | 1133368.6824 | 2579949.2745 | 1133352.6651
127 | 2579955.776 | 1133384.0922 | 2579994.9663 | 1133663.2855
128 | 2579910.8148 | 1133255.3011 | 2579907.7338 | 1133257.0233 | 2579903.9882 | 1133258.003 | 2579901.2474 | 1133257.8787 | 2579898.7274 | 1133257.0534 | 2579891.5689 | 1133252.048
129 | 2579910.8148 | 1133255.3011 | 2580008.9541 | 1133215.877
130 | 2579878.4674 | 1133240.4754 | 2579880.6129 | 1133242.7736 | 2579888.1104 | 1133249.6297 | 2579891.5689 | 1133252.048
131 | 2580008.9541 | 1133215.877 | 2580011.4159 | 1133217.7364 | 2580017.0488 | 1133217.1507 | 2580024.0699 | 1133217.3497 | 2580028.5646 | 1133219.4025 | 2580031.1078 | 1133222.6067 | 2580032.0471 | 1133227.3059 | 2580031.2556 | 1133232.3555 | 2580028.9677 | 1133236.4873
132 | 2580105.8512 | 1133705.7077 | 2580105.8512 | 1133705.7077 | 2580089.8225 | 1133707.0947 | 2580081.405 | 1133715.0598 | 2580074.7063 | 1133714.4373 | 2580070.4713 | 1133709.3155 | 2580064.343 | 1133699.6421 | 2580017.7854 | 1133668.1255 | 2579997.194 | 1133670.1172 | 2579994.9663 | 1133663.2855
133 | 2579878.4674 | 1133240.4754 | 2579875.8849 | 1133237.7091 | 2579872.6889 | 1133235.0074 | 2579868.3921 | 1133232.2982 | 2579865.3552 | 1133231.1078 | 2579861.6116 | 1133230.3866 | 2579858.9795 | 1133230.2553
134 | 2579790.7827 | 1133251.9117 | 2579800.2551 | 1133256.5052
135 | 2579773.7589 | 1133242.654 | 2579781.7939 | 1133246.7957 | 2579790.1468 | 1133251.6034 | 2579790.7827 | 1133251.9117
136 | 2579818.1878 | 1133262.4257 | 2579806.5523 | 1133258.8852 | 2579800.2551 | 1133256.5052
137 | 2579773.7589 | 1133242.654 | 2579775.9139 | 1133237.9667 | 2579780.4409 | 1133226.7349
138 | 2579773.7589 | 1133242.654 | 2579767.4989 | 1133251.3238 | 2579763.8913 | 1133254.393 | 2579760.1271 | 1133256.7068 | 2579756.6375 | 1133257.7015
139 | 2579780.4409 | 1133226.7349 | 2579777.7878 | 1133225.2097
140 | 2579780.4409 | 1133226.7349 | 2579781.2731 | 1133224.6644 | 2579785.1924 | 1133218.148 | 2579787.9676 | 1133214.737 | 2579791.0341 | 1133213.2482 | 2579794.6503 | 1133212.7136 | 2579798.2633 | 1133213.5352 | 2579802.8975 | 1133215.843 | 2579813.6588 | 1133222.6324 | 2579819.0478 | 1133225.0822 | 2579825.5361 | 1133227.0614 | 2579827.3689 | 1133227.3751
141 | 2579756.6375 | 1133257.7015 | 2579755.036 | 1133258.158 | 2579750.7419 | 1133258.5282 | 2579747.8135 | 1133258.0809
142 | 2579777.7878 | 1133225.2097 | 2579781.3392 | 1133207.7003
143 | 2579745.2353 | 1133221.1505 | 2579774.8209 | 1133224.2525 | 2579777.7878 | 1133225.2097
144 | 2579857.35 | 1133230.1739 | 2579850.3401 | 1133229.8241 | 2579838.0214 | 1133229.1984 | 2579827.3689 | 1133227.3751
145 | 2579857.35 | 1133230.1739 | 2579858.9795 | 1133230.2553
146 | 2579352.062 | 1133126.7483 | 2579351.3447 | 1133127.3877 | 2579347.3217 | 1133131.9393
147 | 2579366.3942 | 1133115.1972 | 2579358.3669 | 1133121.1272 | 2579352.062 | 1133126.7483
148 | 2579407.2046 | 1133099.1268 | 2579395.1614 | 1133102.592 | 2579386.8621 | 1133105.302
149 | 2579384.427 | 1133106.0971 | 2579386.8621 | 1133105.302
150 | 2579407.2046 | 1133099.1268 | 2579411.5025 | 1133098.3332
151 | 2579384.427 | 1133106.0971 | 2579379.4149 | 1133108.1487 | 2579374.9266 | 1133110.2873 | 2579366.6367 | 1133115.0181 | 2579366.3942 | 1133115.1972
152 | 2579384.427 | 1133106.0971 | 2579384.5132 | 1133102.0726 | 2579385.7829 | 1133097.4438 | 2579386.249 | 1133094.1739 | 2579385.6731 | 1133090.1072 | 2579384.8496 | 1133085.6634
153 | 2579411.5025 | 1133098.3332 | 2579418.8072 | 1133096.9845
154 | 2579438.8087 | 1133093.2913 | 2579418.8072 | 1133096.9845
155 | 2579263.0445 | 1133039.059 | 2579263.4591 | 1133043.2041 | 2579263.3087 | 1133046.4729 | 2579262.4397 | 1133048.9438 | 2579261.0821 | 1133050.3825 | 2579250.7874 | 1133056.3987 | 2579241.2923 | 1133062.3561

## bus_geodata
| x | y | coords
0 | 2579491.0836 | 1133229.0274
1 | 2579475.5897 | 1133209.4099
2 | 2579522.5325 | 1133233.655
3 | 2579480.0481 | 1133195.3552
4 | 2579538.4024 | 1133215.035
5 | 2579511.2398 | 1133258.5167
6 | 2579480.094 | 1133195.214
7 | 2579323.7916 | 1133160.3875
8 | 2579344.3706 | 1133135.2577
9 | 2579308.3097 | 1133152.8467
10 | 2579304.0965 | 1133189.5754
11 | 2579305.5746 | 1133151.9361
12 | 2579287.7161 | 1133134.9435
13 | 2579559.5853 | 1133205.6786
14 | 2579482.9612 | 1133279.7458
15 | 2579583.2721 | 1133256.6661
16 | 2579576.5298 | 1133198.9251
17 | 2579509.8284 | 1133296.1289
18 | 2579442.2047 | 1133296.4931
19 | 2579608.6958 | 1133244.5285
20 | 2579719.0546 | 1133157.0151
21 | 2579741.4274 | 1133155.6534
22 | 2579717.6702 | 1133157.0661
23 | 2579756.3889 | 1133140.9402
24 | 2579697.7179 | 1133157.7684
25 | 2579778.3245 | 1133150.3234
26 | 2579703.1676 | 1133105.1686
27 | 2579701.9905 | 1133130.4628
28 | 2579691.8074 | 1133158.1997
29 | 2579799.2645 | 1133154.9227
30 | 2579755.7725 | 1133102.9434
31 | 2579684.0265 | 1133142.7739
32 | 2579680.098 | 1133160.2224
33 | 2579322.6081 | 1133338.0272
34 | 2579294.2969 | 1133343.9692
35 | 2579329.9246 | 1133336.6531
36 | 2579266.0316 | 1133298.1318
37 | 2579338.4915 | 1133371.3363
38 | 2579285.7231 | 1133213.3889
39 | 2579345.8916 | 1133233.9895
40 | 2579212.4412 | 1133051.3286
41 | 2579223.8075 | 1133027.9556
42 | 2579229.0275 | 1133070.5252
43 | 2579283.7902 | 1133260.2114
44 | 2579278.3985 | 1133261.4044
45 | 2579330.3231 | 1133239.5285
46 | 2579239.2291 | 1133104.6987
47 | 2579244.4196 | 1133082.7336
48 | 2579365.8412 | 1133366.9743
49 | 2579416.1427 | 1133309.4439
50 | 2579382.8784 | 1133243.4
51 | 2579380.1369 | 1133242.39
52 | 2579381.6903 | 1133364.1835
53 | 2579407.4709 | 1133327.8734
54 | 2579376.8029 | 1133241.1588
55 | 2579648.7745 | 1133164.626
56 | 2579630.4865 | 1133167.7815
57 | 2579651.4401 | 1133167.5295
58 | 2579616.3078 | 1133161.2909
59 | 2579643.635 | 1133170.3688
60 | 2579607.2391 | 1133135.897
61 | 2579288.257 | 1133076.7631
62 | 2579298.9221 | 1133074.6953
63 | 2579269.2056 | 1133080.4568
64 | 2579320.1635 | 1133071.1801
65 | 2579261.3758 | 1133081.9748
66 | 2579343.6841 | 1133067.311
67 | 2579265.0741 | 1133112.016
68 | 2579359.6867 | 1133073.4225
69 | 2579929.721 | 1132985.5387
70 | 2579894.5293 | 1133120.3558
71 | 2579944.9851 | 1132964.3551
72 | 2580065.2946 | 1132945.9665
73 | 2580019.7096 | 1132905.9809
74 | 2580137.5107 | 1132892.6257
75 | 2580236.8235 | 1132887.082
76 | 2580354.8934 | 1133057.1817
77 | 2580327.8577 | 1133068.9313
78 | 2580328.0689 | 1132929.3692
79 | 2580343.8147 | 1133118.7173
80 | 2580331.2218 | 1133170.1367
81 | 2580326.9064 | 1133173.4636
82 | 2579419.6909 | 1133378.1823
83 | 2579421.4334 | 1133377.3408
84 | 2579404.3137 | 1133384.3328
85 | 2579438.1956 | 1133353.1791
86 | 2579389.5038 | 1133386.9617
87 | 2579453.1376 | 1133349.9954
88 | 2579476.189 | 1133345.6678
89 | 2579812.2095 | 1133318.9346
90 | 2579837.9212 | 1133327.7968
91 | 2579810.8843 | 1133318.5353
92 | 2579856.9448 | 1133333.2306
93 | 2579799.0149 | 1133314.959
94 | 2579861.8318 | 1133323.9393
95 | 2579854.6121 | 1133354.414
96 | 2579795.5449 | 1133314.0159
97 | 2579863.3002 | 1133319.3073
98 | 2579850.3371 | 1133364.4681
99 | 2579781.888 | 1133344.1161
100 | 2579754.7167 | 1133321.2442
101 | 2579632.7237 | 1133240.3328
102 | 2579645.2237 | 1133239.0524
103 | 2579653.4826 | 1133238.8132
104 | 2579633.0029 | 1133273.867
105 | 2579673.9787 | 1133244.6913
106 | 2579663.4934 | 1133232.6633
107 | 2579667.3432 | 1133285.6783
108 | 2579692.9727 | 1133248.4117
109 | 2579872.4256 | 1133305.6962
110 | 2579828.8038 | 1133372.7888
111 | 2579869.4653 | 1133382.7019
112 | 2579720.3377 | 1133327.6423
113 | 2579685.8746 | 1133319.0817
114 | 2579669.3952 | 1133480.5116
115 | 2579685.6602 | 1133316.4649
116 | 2579717.3977 | 1133277.1306
117 | 2579778.7364 | 1133349.3564
118 | 2579723.1058 | 1133253.6744
119 | 2579713.8766 | 1133251.894
120 | 2579885.5569 | 1133305.5101
121 | 2579900.7874 | 1133317.2572
122 | 2579949.2745 | 1133352.6651
123 | 2579955.776 | 1133384.0922
124 | 2579910.8148 | 1133255.3011
125 | 2579891.5689 | 1133252.048
126 | 2580008.9541 | 1133215.877
127 | 2579994.9663 | 1133663.2855
128 | 2579878.4674 | 1133240.4754
129 | 2580028.9677 | 1133236.4873
130 | 2580105.8512 | 1133705.7077
131 | 2579790.7827 | 1133251.9117
132 | 2579800.2551 | 1133256.5052
133 | 2579773.7589 | 1133242.654
134 | 2579818.1878 | 1133262.4257
135 | 2579780.4409 | 1133226.7349
136 | 2579756.6375 | 1133257.7015
137 | 2579777.7878 | 1133225.2097
138 | 2579827.3689 | 1133227.3751
139 | 2579747.8135 | 1133258.0809
140 | 2579781.3392 | 1133207.7003
141 | 2579745.2353 | 1133221.1505
142 | 2579857.35 | 1133230.1739
143 | 2579347.3217 | 1133131.9393
144 | 2579352.062 | 1133126.7483
145 | 2579858.9795 | 1133230.2553
146 | 2579386.8621 | 1133105.302
147 | 2579407.2046 | 1133099.1268
148 | 2579384.427 | 1133106.0971
149 | 2579411.5025 | 1133098.3332
150 | 2579366.3942 | 1133115.1972
151 | 2579384.8496 | 1133085.6634
152 | 2579418.8072 | 1133096.9845
153 | 2579438.8087 | 1133093.2913
154 | 2579241.2923 | 1133062.3561
155 | 2579263.0445 | 1133039.059
156 | 2579510.2513 | 1133352.4663
157 | 2579522.5325 | 1133233.655

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1