## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_563-11_1_4_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_563-11_1_4_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_563-11_1_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_563-11_1_4_node_227 | 0.4 | n |  | TRUE
4 | bus_LV_563-11_1_4_node_40 | 0.4 | n |  | TRUE
5 | bus_LV_563-11_1_4_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_563-11_1_4_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_563-11_1_4_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_563-11_1_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_563-11_1_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_563-11_1_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_563-11_1_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_563-11_1_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_563-11_1_4_node_55 | 0.4 | n |  | TRUE
14 | bus_LV_563-11_1_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_563-11_1_4_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_563-11_1_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_563-11_1_4_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_563-11_1_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_563-11_1_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_563-11_1_4_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_563-11_1_4_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_563-11_1_4_node_54 | 0.4 | n |  | TRUE
23 | bus_LV_563-11_1_4_node_70 | 0.4 | n |  | TRUE
24 | bus_LV_563-11_1_4_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_563-11_1_4_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_563-11_1_4_node_48 | 0.4 | n |  | TRUE
27 | bus_LV_563-11_1_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_563-11_1_4_node_71 | 0.4 | n |  | TRUE
29 | bus_LV_563-11_1_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_563-11_1_4_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_563-11_1_4_node_51 | 0.4 | n |  | TRUE
32 | bus_LV_563-11_1_4_node_112 | 0.4 | n |  | TRUE
33 | bus_LV_563-11_1_4_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_563-11_1_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_563-11_1_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_563-11_1_4_node_172 | 0.4 | n |  | TRUE
37 | bus_LV_563-11_1_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_563-11_1_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_563-11_1_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_563-11_1_4_node_73 | 0.4 | n |  | TRUE
41 | bus_LV_563-11_1_4_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_563-11_1_4_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_563-11_1_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_563-11_1_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_563-11_1_4_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_563-11_1_4_node_47 | 0.4 | n |  | TRUE
47 | bus_LV_563-11_1_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_563-11_1_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_563-11_1_4_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_563-11_1_4_node_171 | 0.4 | n |  | TRUE
51 | bus_LV_563-11_1_4_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_563-11_1_4_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_563-11_1_4_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_563-11_1_4_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_563-11_1_4_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_563-11_1_4_node_170 | 0.4 | n |  | TRUE
57 | bus_LV_563-11_1_4_node_204 | 0.4 | n |  | TRUE
58 | bus_LV_563-11_1_4_node_168 | 0.4 | n |  | TRUE
59 | bus_LV_563-11_1_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_563-11_1_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_563-11_1_4_node_111 | 0.4 | n |  | TRUE
62 | bus_LV_563-11_1_4_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_563-11_1_4_node_113 | 0.4 | n |  | TRUE
64 | bus_LV_563-11_1_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_563-11_1_4_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_563-11_1_4_node_106 | 0.4 | n |  | TRUE
67 | bus_LV_563-11_1_4_node_110 | 0.4 | n |  | TRUE
68 | bus_LV_563-11_1_4_node_119 | 0.4 | n |  | TRUE
69 | bus_LV_563-11_1_4_node_104 | 0.4 | n |  | TRUE
70 | bus_LV_563-11_1_4_node_98 | 0.4 | n |  | TRUE
71 | bus_LV_563-11_1_4_node_99 | 0.4 | n |  | TRUE
72 | bus_LV_563-11_1_4_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_563-11_1_4_node_101 | 0.4 | n |  | TRUE
74 | bus_LV_563-11_1_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_563-11_1_4_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_563-11_1_4_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_563-11_1_4_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_563-11_1_4_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_563-11_1_4_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_563-11_1_4_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_563-11_1_4_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_563-11_1_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_563-11_1_4_node_82 | 0.4 | n |  | TRUE
84 | bus_LV_563-11_1_4_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_563-11_1_4_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_563-11_1_4_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_563-11_1_4_node_88 | 0.4 | n |  | TRUE
88 | bus_LV_563-11_1_4_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_563-11_1_4_node_96 | 0.4 | n |  | TRUE
90 | bus_LV_563-11_1_4_node_97 | 0.4 | n |  | TRUE
91 | bus_LV_563-11_1_4_node_228 | 0.4 | n |  | TRUE
92 | bus_LV_563-11_1_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_563-11_1_4_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_563-11_1_4_node_95 | 0.4 | n |  | TRUE
95 | bus_LV_563-11_1_4_node_103 | 0.4 | n |  | TRUE
96 | bus_LV_563-11_1_4_node_105 | 0.4 | n |  | TRUE
97 | bus_LV_563-11_1_4_node_107 | 0.4 | n |  | TRUE
98 | bus_LV_563-11_1_4_node_108 | 0.4 | n |  | TRUE
99 | bus_LV_563-11_1_4_node_192 | 0.4 | n |  | TRUE
100 | bus_LV_563-11_1_4_node_194 | 0.4 | n |  | TRUE
101 | bus_LV_563-11_1_4_node_191 | 0.4 | n |  | TRUE
102 | bus_LV_563-11_1_4_node_114 | 0.4 | n |  | TRUE
103 | bus_LV_563-11_1_4_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_563-11_1_4_node_116 | 0.4 | n |  | TRUE
105 | bus_LV_563-11_1_4_node_117 | 0.4 | n |  | TRUE
106 | bus_LV_563-11_1_4_node_118 | 0.4 | n |  | TRUE
107 | bus_LV_563-11_1_4_node_120 | 0.4 | n |  | TRUE
108 | bus_LV_563-11_1_4_node_121 | 0.4 | n |  | TRUE
109 | bus_LV_563-11_1_4_node_124 | 0.4 | n |  | TRUE
110 | bus_LV_563-11_1_4_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_563-11_1_4_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_563-11_1_4_node_126 | 0.4 | n |  | TRUE
113 | bus_LV_563-11_1_4_node_127 | 0.4 | n |  | TRUE
114 | bus_LV_563-11_1_4_node_130 | 0.4 | n |  | TRUE
115 | bus_LV_563-11_1_4_node_131 | 0.4 | n |  | TRUE
116 | bus_LV_563-11_1_4_node_236 | 0.4 | n |  | TRUE
117 | bus_LV_563-11_1_4_node_235 | 0.4 | n |  | TRUE
118 | bus_LV_563-11_1_4_node_133 | 0.4 | n |  | TRUE
119 | bus_LV_563-11_1_4_node_129 | 0.4 | n |  | TRUE
120 | bus_LV_563-11_1_4_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_563-11_1_4_node_128 | 0.4 | n |  | TRUE
122 | bus_LV_563-11_1_4_node_222 | 0.4 | n |  | TRUE
123 | bus_LV_563-11_1_4_node_223 | 0.4 | n |  | TRUE
124 | bus_LV_563-11_1_4_node_224 | 0.4 | n |  | TRUE
125 | bus_LV_563-11_1_4_node_141 | 0.4 | n |  | TRUE
126 | bus_LV_563-11_1_4_node_134 | 0.4 | n |  | TRUE
127 | bus_LV_563-11_1_4_node_135 | 0.4 | n |  | TRUE
128 | bus_LV_563-11_1_4_node_136 | 0.4 | n |  | TRUE
129 | bus_LV_563-11_1_4_node_205 | 0.4 | n |  | TRUE
130 | bus_LV_563-11_1_4_node_140 | 0.4 | n |  | TRUE
131 | bus_LV_563-11_1_4_node_206 | 0.4 | n |  | TRUE
132 | bus_LV_563-11_1_4_node_138 | 0.4 | n |  | TRUE
133 | bus_LV_563-11_1_4_node_137 | 0.4 | n |  | TRUE
134 | bus_LV_563-11_1_4_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_563-11_1_4_node_147 | 0.4 | n |  | TRUE
136 | bus_LV_563-11_1_4_node_225 | 0.4 | n |  | TRUE
137 | bus_LV_563-11_1_4_node_226 | 0.4 | n |  | TRUE
138 | bus_LV_563-11_1_4_node_144 | 0.4 | n |  | TRUE
139 | bus_LV_563-11_1_4_node_142 | 0.4 | n |  | TRUE
140 | bus_LV_563-11_1_4_node_143 | 0.4 | n |  | TRUE
141 | bus_LV_563-11_1_4_node_145 | 0.4 | n |  | TRUE
142 | bus_LV_563-11_1_4_node_146 | 0.4 | n |  | TRUE
143 | bus_LV_563-11_1_4_node_148 | 0.4 | n |  | TRUE
144 | bus_LV_563-11_1_4_node_149 | 0.4 | n |  | TRUE
145 | bus_LV_563-11_1_4_node_150 | 0.4 | n |  | TRUE
146 | bus_LV_563-11_1_4_node_151 | 0.4 | n |  | TRUE
147 | bus_LV_563-11_1_4_node_152 | 0.4 | n |  | TRUE
148 | bus_LV_563-11_1_4_node_154 | 0.4 | n |  | TRUE
149 | bus_LV_563-11_1_4_node_153 | 0.4 | n |  | TRUE
150 | bus_LV_563-11_1_4_node_157 | 0.4 | n |  | TRUE
151 | bus_LV_563-11_1_4_node_155 | 0.4 | n |  | TRUE
152 | bus_LV_563-11_1_4_node_158 | 0.4 | n |  | TRUE
153 | bus_LV_563-11_1_4_node_165 | 0.4 | n |  | TRUE
154 | bus_LV_563-11_1_4_node_156 | 0.4 | n |  | TRUE
155 | bus_LV_563-11_1_4_node_159 | 0.4 | n |  | TRUE
156 | bus_LV_563-11_1_4_node_160 | 0.4 | n |  | TRUE
157 | bus_LV_563-11_1_4_node_161 | 0.4 | n |  | TRUE
158 | bus_LV_563-11_1_4_node_163 | 0.4 | n |  | TRUE
159 | bus_LV_563-11_1_4_node_166 | 0.4 | n |  | TRUE
160 | bus_LV_563-11_1_4_node_162 | 0.4 | n |  | TRUE
161 | bus_LV_563-11_1_4_node_164 | 0.4 | n |  | TRUE
162 | bus_LV_563-11_1_4_node_167 | 0.4 | n |  | TRUE
163 | bus_LV_563-11_1_4_node_169 | 0.4 | n |  | TRUE
164 | bus_LV_563-11_1_4_node_173 | 0.4 | n |  | TRUE
165 | bus_LV_563-11_1_4_node_193 | 0.4 | n |  | TRUE
166 | bus_LV_563-11_1_4_node_195 | 0.4 | n |  | TRUE
167 | bus_MV_0_node_172 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_563-11_1_4_load_3 | 0 | 5.461e-05 | 1.3687e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_563-11_1_4_load_227 | 3 | 9.6168e-05 | 2.4102e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_563-11_1_4_load_38 | 6 | 0.0001053 | 2.639e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_563-11_1_4_load_41 | 7 | 0.00011181 | 2.8023e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_563-11_1_4_load_7 | 8 | 5.1155e-05 | 1.2821e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_563-11_1_4_load_10 | 11 | 8.404e-05 | 2.1062e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_563-11_1_4_load_55 | 13 | 0.00027405 | 6.8682e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_563-11_1_4_load_21 | 15 | 8.123e-05 | 2.0358e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_563-11_1_4_load_12 | 16 | 0.00025845 | 6.4774e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_563-11_1_4_load_24 | 18 | 0.00011063 | 2.7726e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_563-11_1_4_load_13 | 19 | 5.1132e-05 | 1.2815e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_563-11_1_4_load_54 | 22 | 6.3472e-05 | 1.5908e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_563-11_1_4_load_70 | 23 | 8.5519e-05 | 2.1433e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_563-11_1_4_load_72 | 24 | 0.00014697 | 3.6835e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_563-11_1_4_load_34 | 25 | 8.3107e-05 | 2.0829e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_563-11_1_4_load_48 | 26 | 0.00021791 | 5.4614e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_563-11_1_4_load_17 | 27 | 8.5037e-05 | 2.1312e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_563-11_1_4_load_45 | 30 | 0.00014287 | 3.5806e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_563-11_1_4_load_14 | 33 | 6.6168e-05 | 1.6583e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_563-11_1_4_load_172 | 36 | 0.00018437 | 4.6207e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_563-11_1_4_load_20 | 38 | 0.00016261 | 4.0754e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_563-11_1_4_load_18 | 39 | 5.6482e-05 | 1.4156e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_563-11_1_4_load_74 | 41 | 0.00011207 | 2.8088e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_563-11_1_4_load_25 | 43 | 0.00019658 | 4.9267e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_563-11_1_4_load_27 | 44 | 0.0001009 | 2.5287e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_563-11_1_4_load_46 | 45 | 0.00011312 | 2.835e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_563-11_1_4_load_35 | 47 | 8.3158e-05 | 2.0841e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_563-11_1_4_load_36 | 48 | 6.6795e-05 | 1.6741e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_563-11_1_4_load_33 | 49 | 0.00013049 | 3.2704e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_563-11_1_4_load_171 | 50 | 0.00021245 | 5.3244e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_563-11_1_4_load_29 | 51 | 6.7423e-05 | 1.6898e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_563-11_1_4_load_31 | 53 | 9.9774e-05 | 2.5006e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_563-11_1_4_load_37 | 55 | 0.00010552 | 2.6446e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_563-11_1_4_load_204 | 57 | 7.8122e-05 | 1.9579e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_563-11_1_4_load_50 | 59 | 6.0661e-05 | 1.5203e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_563-11_1_4_load_52 | 60 | 6.6513e-05 | 1.667e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_563-11_1_4_load_111 | 61 | 0.00025476 | 6.3848e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_563-11_1_4_load_109 | 62 | 7.7602e-05 | 1.9449e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_563-11_1_4_load_113 | 63 | 0.00061503 | 0.00015414 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_563-11_1_4_load_123 | 65 | 0.00020159 | 5.0524e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_563-11_1_4_load_106 | 66 | 6.6977e-05 | 1.6786e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_563-11_1_4_load_110 | 67 | 0.00030255 | 7.5826e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_563-11_1_4_load_119 | 68 | 5.7747e-05 | 1.4473e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_563-11_1_4_load_104 | 69 | 0.00019824 | 4.9684e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_563-11_1_4_load_98 | 70 | 0.00012759 | 3.1978e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_563-11_1_4_load_100 | 72 | 0.00035911 | 9.0002e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_563-11_1_4_load_101 | 73 | 0.00036169 | 9.0647e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_563-11_1_4_load_68 | 74 | 0.00028286 | 7.0892e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_563-11_1_4_load_69 | 75 | 0.00043045 | 0.00010788 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_563-11_1_4_load_76 | 76 | 0.00012962 | 3.2487e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_563-11_1_4_load_77 | 77 | 4.8721e-05 | 1.2211e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_563-11_1_4_load_78 | 78 | 0.00017166 | 4.3022e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_563-11_1_4_load_84 | 80 | 0.0001213 | 3.04e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_563-11_1_4_load_79 | 81 | 0.00021746 | 5.45e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_563-11_1_4_load_82 | 83 | 0.00015017 | 3.7636e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_563-11_1_4_load_85 | 84 | 0.00020146 | 5.0491e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_563-11_1_4_load_86 | 85 | 6.1713e-05 | 1.5467e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_563-11_1_4_load_87 | 86 | 0.00010804 | 2.7078e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_563-11_1_4_load_89 | 88 | 5.9882e-05 | 1.5008e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_563-11_1_4_load_97 | 90 | 0.00011783 | 2.9531e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_563-11_1_4_load_228 | 91 | 0.00011868 | 2.9744e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_563-11_1_4_load_90 | 93 | 7.8361e-05 | 1.9639e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_563-11_1_4_load_95 | 94 | 5.3893e-05 | 1.3507e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_563-11_1_4_load_103 | 95 | 0.00015716 | 3.9388e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_563-11_1_4_load_107 | 97 | 8.6252e-05 | 2.1617e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_563-11_1_4_load_108 | 98 | 8.9752e-05 | 2.2494e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_563-11_1_4_load_194 | 100 | 0.00015861 | 3.975e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_563-11_1_4_load_191 | 101 | 0.00018326 | 4.593e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_563-11_1_4_load_114 | 102 | 6.3746e-05 | 1.5976e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_563-11_1_4_load_118 | 106 | 8.514e-05 | 2.1338e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_563-11_1_4_load_120 | 107 | 0.00015079 | 3.7792e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_563-11_1_4_load_121 | 108 | 5.5654e-05 | 1.3948e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_563-11_1_4_load_124 | 109 | 9.3975e-05 | 2.3552e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_563-11_1_4_load_122 | 110 | 7.1828e-05 | 1.8002e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_563-11_1_4_load_131 | 115 | 0.00012098 | 3.032e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_563-11_1_4_load_236 | 116 | 0.00024111 | 6.0428e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_563-11_1_4_load_235 | 117 | 8.0971e-05 | 2.0293e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_563-11_1_4_load_129 | 119 | 5.9612e-05 | 1.494e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_563-11_1_4_load_132 | 120 | 6.7795e-05 | 1.6991e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_563-11_1_4_load_128 | 121 | 0.00017103 | 4.2865e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_563-11_1_4_load_222 | 122 | 0.00026321 | 6.5968e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_563-11_1_4_load_224 | 124 | 0.00016587 | 4.1571e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_563-11_1_4_load_134 | 126 | 0.00016271 | 4.078e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_563-11_1_4_load_135 | 127 | 0.00029355 | 7.3572e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_563-11_1_4_load_205 | 129 | 0.00016045 | 4.0213e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_563-11_1_4_load_206 | 131 | 0.00018927 | 4.7435e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_563-11_1_4_load_138 | 132 | 0.00084985 | 0.00021299 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_563-11_1_4_load_137 | 133 | 0.00020408 | 5.1146e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_563-11_1_4_load_225 | 136 | 6.9483e-05 | 1.7414e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_563-11_1_4_load_226 | 137 | 0.00022283 | 5.5847e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_563-11_1_4_load_142 | 139 | 0.0001352 | 3.3885e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_563-11_1_4_load_143 | 140 | 9.9899e-05 | 2.5037e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_563-11_1_4_load_145 | 141 | 0.00012899 | 3.2327e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_563-11_1_4_load_146 | 142 | 9.5522e-05 | 2.394e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_563-11_1_4_load_148 | 143 | 0.0001598 | 4.0049e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_563-11_1_4_load_149 | 144 | 0.00011743 | 2.9432e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_563-11_1_4_load_152 | 147 | 0.0002334 | 5.8495e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_563-11_1_4_load_153 | 149 | 0.00010347 | 2.5931e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_563-11_1_4_load_157 | 150 | 0.00013837 | 3.4678e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_563-11_1_4_load_155 | 151 | 0.00020735 | 5.1967e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_563-11_1_4_load_158 | 152 | 6.5288e-05 | 1.6363e-05 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_563-11_1_4_load_159 | 155 | 0.00016134 | 4.0436e-05 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_563-11_1_4_load_160 | 156 | 0.00015627 | 3.9164e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_563-11_1_4_load_161 | 157 | 0.00018401 | 4.6117e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_563-11_1_4_load_166 | 159 | 4.9411e-05 | 1.2384e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_563-11_1_4_load_162 | 160 | 0.00012112 | 3.0355e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_563-11_1_4_load_164 | 161 | 0.00019927 | 4.9943e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_563-11_1_4_load_167 | 162 | 9.6309e-05 | 2.4137e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_563-11_1_4_load_169 | 163 | 7.096e-05 | 1.7784e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_563-11_1_4_load_173 | 164 | 0.00016552 | 4.1483e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_563-11_1_4_load_193 | 165 | 0.00010498 | 2.631e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_563-11_1_4_load_195 | 166 | 0.00020191 | 5.0604e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_563-11_1_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.08553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_563-11_1_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.097504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_563-11_1_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.026816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_563-11_1_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.068453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_563-11_1_4_line_4 | NAYY 4x150 SE | 4 | 7 | 0.014675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_563-11_1_4_line_5 | NAYY 4x150 SE | 4 | 5 | 0.060235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_563-11_1_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.24214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_563-11_1_4_line_7 | NAYY 4x150 SE | 6 | 55 | 0.04637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_563-11_1_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.20773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_563-11_1_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.064008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_563-11_1_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.040704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_563-11_1_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.095309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_563-11_1_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.1697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_563-11_1_4_line_13 | NAYY 4x150 SE | 12 | 14 | 0.21517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_563-11_1_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.032664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_563-11_1_4_line_15 | NAYY 4x150 SE | 13 | 21 | 0.061353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_563-11_1_4_line_16 | NAYY 4x150 SE | 14 | 25 | 0.016581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_563-11_1_4_line_17 | NAYY 4x150 SE | 15 | 26 | 0.24672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_563-11_1_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.15499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_563-11_1_4_line_19 | NAYY 4x150 SE | 16 | 18 | 0.19874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_563-11_1_4_line_20 | NAYY 4x150 SE | 17 | 27 | 0.071583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_563-11_1_4_line_21 | NAYY 4x150 SE | 17 | 28 | 0.16657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_563-11_1_4_line_22 | NAYY 4x150 SE | 18 | 29 | 0.28718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_563-11_1_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.32925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_563-11_1_4_line_24 | NAYY 4x150 SE | 20 | 30 | 0.0042764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_563-11_1_4_line_25 | NAYY 4x150 SE | 20 | 31 | 0.18305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_563-11_1_4_line_26 | NAYY 4x150 SE | 20 | 32 | 0.28476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_563-11_1_4_line_27 | NAYY 4x150 SE | 21 | 22 | 0.012844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_563-11_1_4_line_28 | NAYY 4x150 SE | 21 | 23 | 0.236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_563-11_1_4_line_29 | NAYY 4x150 SE | 22 | 24 | 0.061527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_563-11_1_4_line_30 | NAYY 4x150 SE | 24 | 28 | 0.044127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_563-11_1_4_line_31 | NAYY 4x150 SE | 25 | 47 | 0.19234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_563-11_1_4_line_32 | NAYY 4x150 SE | 26 | 45 | 0.0094809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_563-11_1_4_line_33 | NAYY 4x150 SE | 27 | 40 | 0.12479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_563-11_1_4_line_34 | NAYY 4x150 SE | 29 | 34 | 0.049273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_563-11_1_4_line_35 | NAYY 4x150 SE | 29 | 33 | 0.018554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_563-11_1_4_line_36 | NAYY 4x150 SE | 31 | 60 | 0.055062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_563-11_1_4_line_37 | NAYY 4x150 SE | 31 | 59 | 0.061404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_563-11_1_4_line_38 | NAYY 4x150 SE | 32 | 63 | 0.011048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_563-11_1_4_line_39 | NAYY 4x150 SE | 32 | 61 | 0.067775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_563-11_1_4_line_40 | NAYY 4x150 SE | 34 | 38 | 0.013685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_563-11_1_4_line_41 | NAYY 4x150 SE | 34 | 39 | 0.17957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_563-11_1_4_line_42 | NAYY 4x150 SE | 35 | 36 | 0.28035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_563-11_1_4_line_43 | NAYY 4x150 SE | 35 | 37 | 0.085125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_563-11_1_4_line_44 | NAYY 4x150 SE | 36 | 50 | 0.018389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_563-11_1_4_line_45 | NAYY 4x150 SE | 37 | 44 | 0.26829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_563-11_1_4_line_46 | NAYY 4x150 SE | 37 | 43 | 0.031282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_563-11_1_4_line_47 | NAYY 4x150 SE | 39 | 43 | 0.21649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_563-11_1_4_line_48 | NAYY 4x150 SE | 40 | 41 | 0.029132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_563-11_1_4_line_49 | NAYY 4x150 SE | 40 | 42 | 0.21879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_563-11_1_4_line_50 | NAYY 4x150 SE | 42 | 77 | 0.057544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_563-11_1_4_line_51 | NAYY 4x150 SE | 44 | 48 | 0.013044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_563-11_1_4_line_52 | NAYY 4x150 SE | 45 | 46 | 0.11055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_563-11_1_4_line_53 | NAYY 4x150 SE | 46 | 64 | 0.030761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_563-11_1_4_line_54 | NAYY 4x150 SE | 46 | 65 | 0.28364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_563-11_1_4_line_55 | NAYY 4x150 SE | 48 | 49 | 0.027567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_563-11_1_4_line_56 | NAYY 4x150 SE | 49 | 52 | 0.030466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_563-11_1_4_line_57 | NAYY 4x150 SE | 50 | 164 | 0.020769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_563-11_1_4_line_58 | NAYY 4x150 SE | 51 | 52 | 0.010049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_563-11_1_4_line_59 | NAYY 4x150 SE | 51 | 53 | 0.044378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_563-11_1_4_line_60 | NAYY 4x150 SE | 52 | 54 | 0.063206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_563-11_1_4_line_61 | NAYY 4x150 SE | 54 | 55 | 0.086722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_563-11_1_4_line_62 | NAYY 4x150 SE | 56 | 57 | 0.082461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_563-11_1_4_line_63 | NAYY 4x150 SE | 56 | 58 | 0.11584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_563-11_1_4_line_64 | NAYY 4x150 SE | 58 | 163 | 0.10715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_563-11_1_4_line_65 | NAYY 4x150 SE | 58 | 162 | 0.068728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_563-11_1_4_line_66 | NAYY 4x150 SE | 60 | 75 | 0.26365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_563-11_1_4_line_67 | NAYY 4x150 SE | 61 | 62 | 0.047441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_563-11_1_4_line_68 | NAYY 4x150 SE | 62 | 67 | 0.024156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_563-11_1_4_line_69 | NAYY 4x150 SE | 64 | 66 | 0.018714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_563-11_1_4_line_70 | NAYY 4x150 SE | 64 | 67 | 0.016758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_563-11_1_4_line_71 | NAYY 4x150 SE | 65 | 68 | 0.00069745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_563-11_1_4_line_72 | NAYY 4x150 SE | 66 | 69 | 0.0061826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_563-11_1_4_line_73 | NAYY 4x150 SE | 68 | 104 | 0.20745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_563-11_1_4_line_74 | NAYY 4x150 SE | 69 | 95 | 0.019812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_563-11_1_4_line_75 | NAYY 4x150 SE | 70 | 71 | 0.066567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_563-11_1_4_line_76 | NAYY 4x150 SE | 71 | 72 | 0.02335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_563-11_1_4_line_77 | NAYY 4x150 SE | 71 | 73 | 0.045306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_563-11_1_4_line_78 | NAYY 4x150 SE | 73 | 74 | 0.25945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_563-11_1_4_line_79 | NAYY 4x150 SE | 74 | 75 | 0.016836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_563-11_1_4_line_80 | NAYY 4x150 SE | 76 | 77 | 0.13976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_563-11_1_4_line_81 | NAYY 4x150 SE | 77 | 78 | 0.17469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_563-11_1_4_line_82 | NAYY 4x150 SE | 78 | 79 | 0.34253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_563-11_1_4_line_83 | NAYY 4x150 SE | 79 | 80 | 0.11729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_563-11_1_4_line_84 | NAYY 4x150 SE | 79 | 81 | 0.038224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_563-11_1_4_line_85 | NAYY 4x150 SE | 80 | 84 | 0.1448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_563-11_1_4_line_86 | NAYY 4x150 SE | 81 | 82 | 0.04113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_563-11_1_4_line_87 | NAYY 4x150 SE | 82 | 83 | 0.16229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_563-11_1_4_line_88 | NAYY 4x150 SE | 84 | 85 | 0.02553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_563-11_1_4_line_89 | NAYY 4x150 SE | 84 | 86 | 0.049327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_563-11_1_4_line_90 | NAYY 4x150 SE | 85 | 87 | 0.12566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_563-11_1_4_line_91 | NAYY 4x150 SE | 86 | 88 | 0.039866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_563-11_1_4_line_92 | NAYY 4x150 SE | 87 | 89 | 0.045578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_563-11_1_4_line_93 | NAYY 4x150 SE | 87 | 90 | 0.10542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_563-11_1_4_line_94 | NAYY 4x150 SE | 89 | 91 | 0.022141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_563-11_1_4_line_95 | NAYY 4x150 SE | 89 | 92 | 0.044735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_563-11_1_4_line_96 | NAYY 4x150 SE | 92 | 94 | 0.09398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_563-11_1_4_line_97 | NAYY 4x150 SE | 92 | 93 | 0.010778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_563-11_1_4_line_98 | NAYY 4x150 SE | 95 | 96 | 0.30367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_563-11_1_4_line_99 | NAYY 4x150 SE | 96 | 97 | 0.13951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_563-11_1_4_line_100 | NAYY 4x150 SE | 96 | 98 | 0.07893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_563-11_1_4_line_101 | NAYY 4x150 SE | 97 | 99 | 0.014441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_563-11_1_4_line_102 | NAYY 4x150 SE | 99 | 100 | 0.017312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_563-11_1_4_line_103 | NAYY 4x150 SE | 99 | 101 | 0.015449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_563-11_1_4_line_104 | NAYY 4x150 SE | 100 | 166 | 0.0098498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_563-11_1_4_line_105 | NAYY 4x150 SE | 101 | 165 | 0.0096413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_563-11_1_4_line_106 | NAYY 4x150 SE | 102 | 103 | 0.039187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_563-11_1_4_line_107 | NAYY 4x150 SE | 102 | 104 | 0.10793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_563-11_1_4_line_108 | NAYY 4x150 SE | 103 | 105 | 0.025011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_563-11_1_4_line_109 | NAYY 4x150 SE | 103 | 106 | 0.014885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_563-11_1_4_line_110 | NAYY 4x150 SE | 104 | 107 | 0.015626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_563-11_1_4_line_111 | NAYY 4x150 SE | 105 | 108 | 0.063174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_563-11_1_4_line_112 | NAYY 4x150 SE | 107 | 109 | 0.061304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_563-11_1_4_line_113 | NAYY 4x150 SE | 108 | 110 | 0.0089692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_563-11_1_4_line_114 | NAYY 4x150 SE | 109 | 111 | 0.0078326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_563-11_1_4_line_115 | NAYY 4x150 SE | 111 | 112 | 0.005233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_563-11_1_4_line_116 | NAYY 4x150 SE | 111 | 113 | 0.032259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_563-11_1_4_line_117 | NAYY 4x150 SE | 112 | 114 | 0.19046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_563-11_1_4_line_118 | NAYY 4x150 SE | 112 | 115 | 0.067396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_563-11_1_4_line_119 | NAYY 4x150 SE | 113 | 116 | 0.011597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_563-11_1_4_line_120 | NAYY 4x150 SE | 113 | 117 | 0.019132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_563-11_1_4_line_121 | NAYY 4x150 SE | 114 | 118 | 0.12556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_563-11_1_4_line_122 | NAYY 4x150 SE | 114 | 119 | 0.10847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_563-11_1_4_line_123 | NAYY 4x150 SE | 115 | 120 | 0.0070743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_563-11_1_4_line_124 | NAYY 4x150 SE | 118 | 122 | 0.04552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_563-11_1_4_line_125 | NAYY 4x150 SE | 118 | 123 | 0.11612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_563-11_1_4_line_126 | NAYY 4x150 SE | 119 | 121 | 0.0034782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_563-11_1_4_line_127 | NAYY 4x150 SE | 123 | 124 | 0.026941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_563-11_1_4_line_128 | NAYY 4x150 SE | 123 | 125 | 0.091598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_563-11_1_4_line_129 | NAYY 4x150 SE | 125 | 135 | 0.021615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_563-11_1_4_line_130 | NAYY 4x150 SE | 125 | 136 | 0.025719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_563-11_1_4_line_131 | NAYY 4x150 SE | 125 | 134 | 0.1396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_563-11_1_4_line_132 | NAYY 4x150 SE | 126 | 127 | 0.016443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_563-11_1_4_line_133 | NAYY 4x150 SE | 127 | 128 | 0.019082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_563-11_1_4_line_134 | NAYY 4x150 SE | 128 | 129 | 0.073351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_563-11_1_4_line_135 | NAYY 4x150 SE | 128 | 130 | 0.084896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_563-11_1_4_line_136 | NAYY 4x150 SE | 130 | 131 | 0.10137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_563-11_1_4_line_137 | NAYY 4x150 SE | 130 | 132 | 0.032383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_563-11_1_4_line_138 | NAYY 4x150 SE | 132 | 133 | 0.0094014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_563-11_1_4_line_139 | NAYY 4x150 SE | 133 | 134 | 0.0034115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_563-11_1_4_line_140 | NAYY 4x150 SE | 135 | 137 | 0.014329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_563-11_1_4_line_141 | NAYY 4x150 SE | 135 | 138 | 0.029295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_563-11_1_4_line_142 | NAYY 4x150 SE | 138 | 142 | 0.02113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_563-11_1_4_line_143 | NAYY 4x150 SE | 138 | 139 | 0.043817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_563-11_1_4_line_144 | NAYY 4x150 SE | 139 | 140 | 0.0029985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_563-11_1_4_line_145 | NAYY 4x150 SE | 140 | 141 | 0.073642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_563-11_1_4_line_146 | NAYY 4x150 SE | 142 | 143 | 0.06427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_563-11_1_4_line_147 | NAYY 4x150 SE | 143 | 144 | 0.016224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_563-11_1_4_line_148 | NAYY 4x150 SE | 144 | 145 | 0.015537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_563-11_1_4_line_149 | NAYY 4x150 SE | 145 | 146 | 0.007119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_563-11_1_4_line_150 | NAYY 4x150 SE | 145 | 147 | 0.026354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_563-11_1_4_line_151 | NAYY 4x150 SE | 146 | 148 | 0.13714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_563-11_1_4_line_152 | NAYY 4x150 SE | 146 | 149 | 0.093195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_563-11_1_4_line_153 | NAYY 4x150 SE | 148 | 150 | 0.071729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_563-11_1_4_line_154 | NAYY 4x150 SE | 148 | 151 | 0.034461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_563-11_1_4_line_155 | NAYY 4x150 SE | 151 | 154 | 0.088451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_563-11_1_4_line_156 | NAYY 4x150 SE | 152 | 153 | 0.0090176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_563-11_1_4_line_157 | NAYY 4x150 SE | 153 | 159 | 0.094136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_563-11_1_4_line_158 | NAYY 4x150 SE | 153 | 158 | 0.012806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_563-11_1_4_line_159 | NAYY 4x150 SE | 154 | 155 | 0.018396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_563-11_1_4_line_160 | NAYY 4x150 SE | 154 | 156 | 0.058757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_563-11_1_4_line_161 | NAYY 4x150 SE | 155 | 157 | 0.09525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_563-11_1_4_line_162 | NAYY 4x150 SE | 156 | 158 | 0.032539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_563-11_1_4_line_163 | NAYY 4x150 SE | 157 | 160 | 0.0035672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_563-11_1_4_line_164 | NAYY 4x150 SE | 158 | 161 | 0.037551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_563-11_1_4_line_165 | NAYY 4x150 SE | 159 | 162 | 0.021276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_563-11_1_4_trafo_172 | 0.25 MVA 20/0.4 kV | 167 | 36 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34
0 | 2614352.6444 | 1157690.783 | 2614348.2542 | 1157679.9672 | 2614336.1705 | 1157670.7117 | 2614329.4902 | 1157668.606 | 2614317.9765 | 1157667.9673 | 2614308.9333 | 1157666.5118 | 2614292.9098 | 1157660.1152 | 2614285.9188 | 1157659.6984 | 2614279.2358 | 1157659.8473
1 | 2614352.6444 | 1157690.783 | 2614309.0336 | 1157727.7201 | 2614270.647 | 1157740.7802
2 | 2614282.7095 | 1157716.8191 | 2614270.647 | 1157740.7802
3 | 2614242.4308 | 1157768.2161 | 2614240.3609 | 1157774.6811 | 2614239.5758 | 1157779.2704 | 2614240.4548 | 1157783.6413 | 2614243.8891 | 1157780.5257 | 2614270.647 | 1157740.7802
4 | 2614242.4308 | 1157768.2161 | 2614227.7568 | 1157768.3483
5 | 2614257.7235 | 1157710.5904 | 2614257.0498 | 1157726.4299 | 2614255.049 | 1157736.0744 | 2614251.4769 | 1157745.604 | 2614242.4308 | 1157768.2161
6 | 2614257.7235 | 1157710.5904 | 2614249.3927 | 1157702.9114 | 2614241.522 | 1157695.1779 | 2614234.2659 | 1157686.9011 | 2614227.2248 | 1157678.4693 | 2614191.8138 | 1157629.0505 | 2614174.2613 | 1157604.386 | 2614165.6045 | 1157591.7372 | 2614157.7069 | 1157579.0458 | 2614152.3562 | 1157568.9282 | 2614147.3814 | 1157558.7226 | 2614143.2431 | 1157548.1522 | 2614139.7568 | 1157537.4276 | 2614135.0507 | 1157520.486 | 2614131.7265 | 1157507.4729
7 | 2614116.997 | 1157463.6525 | 2614119.4405 | 1157468.1903 | 2614122.9707 | 1157476.6027 | 2614125.6265 | 1157485.0909 | 2614130.4391 | 1157502.433 | 2614131.7265 | 1157507.4729
8 | 2613780.6309 | 1156443.6912 | 2613791.1275 | 1156457.6443 | 2613801.0724 | 1156468.0388 | 2613812.978 | 1156476.0588 | 2613823.271 | 1156478.4168 | 2613834.995 | 1156478.6549 | 2613846.5116 | 1156479.0814 | 2613858.2153 | 1156481.4872 | 2613867.4707 | 1156484.8768 | 2613873.8463 | 1156486.7368 | 2613878.3752 | 1156484.6906 | 2613878.7982 | 1156480.8008 | 2613877.1599 | 1156476.2837 | 2613869.1518 | 1156470.7292 | 2613861.3525 | 1156464.3637 | 2613855.6079 | 1156458.192 | 2613845.9511 | 1156452.6338 | 2613841.6424 | 1156448.9332 | 2613838.1569 | 1156444.0117 | 2613837.9616 | 1156438.8865 | 2613838.7976 | 1156432.1184 | 2613847.6848 | 1156411.4026
9 | 2613865.1075 | 1156351.8057 | 2613864.0691 | 1156356.5167 | 2613865.4847 | 1156364.5239 | 2613865.2675 | 1156372.3161 | 2613863.607 | 1156377.4371 | 2613860.3023 | 1156383.9883 | 2613856.7962 | 1156388.0823 | 2613854.1082 | 1156393.2009 | 2613852.2428 | 1156400.7781 | 2613847.6848 | 1156411.4026
10 | 2613780.6309 | 1156443.6912 | 2613777.1626 | 1156471.586 | 2613782.931 | 1156482.782
11 | 2613780.6309 | 1156443.6912 | 2613779.3843 | 1156425.4127 | 2613770.6705 | 1156419.8679 | 2613767.8194 | 1156419.2389 | 2613763.5254 | 1156419.1513 | 2613735.2102 | 1156437.8294 | 2613727.043 | 1156444.8032 | 2613720.6302 | 1156449.1797 | 2613713.5271 | 1156450.1863
12 | 2613865.1075 | 1156351.8057 | 2614008.64 | 1156261.2682
13 | 2613671.302 | 1156648.622 | 2613661.8279 | 1156643.6982 | 2613667.2854 | 1156634.4393 | 2613670.3567 | 1156629.2325 | 2613684.026 | 1156616.8462 | 2613710.4943 | 1156468.7886 | 2613713.5271 | 1156450.1863
14 | 2613713.5271 | 1156450.1863 | 2613706.7571 | 1156446.3802 | 2613691.1514 | 1156436.6178 | 2613685.8538 | 1156432.8686
15 | 2614040.4556 | 1156211.2076 | 2614031.3937 | 1156216.8671 | 2614024.0694 | 1156223.8424 | 2614019.633 | 1156232.214 | 2614016.1114 | 1156242.8667 | 2614008.64 | 1156261.2682
16 | 2613671.302 | 1156648.622 | 2613666.063 | 1156659.6045 | 2613663.1623 | 1156662.9298
17 | 2613685.8538 | 1156432.8686 | 2613439.6157 | 1156417.4774
18 | 2614185.6652 | 1156417.4372 | 2614171.0932 | 1156421.7052 | 2614157.2039 | 1156425.8858 | 2614143.2037 | 1156431.5892 | 2614134.9724 | 1156433.004 | 2614123.8771 | 1156429.4985 | 2614113.3913 | 1156427.6287 | 2614104.3357 | 1156430.6868 | 2614095.2621 | 1156434.8789 | 2614077.9779 | 1156441.4863 | 2614072.8273 | 1156447.0104 | 2614064.3771 | 1156453.5495 | 2614057.5841 | 1156456.4018 | 2614048.5314 | 1156458.2261 | 2614042.0625 | 1156456.7167
19 | 2614042.0625 | 1156456.7167 | 2614110.5503 | 1156643.2855
20 | 2614185.6652 | 1156417.4372 | 2614207.3166 | 1156412.4634 | 2614240.2422 | 1156409.9841 | 2614256.5856 | 1156410.3858
21 | 2614185.6652 | 1156417.4372 | 2614112.5531 | 1156267.77
22 | 2614024.2259 | 1156810.6326 | 2614040.4532 | 1156803.0109 | 2614058.537 | 1156788.4013 | 2614063.603 | 1156786.1342 | 2614077.7553 | 1156783.8549 | 2614090.9142 | 1156783.4298 | 2614108.2362 | 1156786.4939 | 2614111.1137 | 1156785.578 | 2614113.3968 | 1156783.1265 | 2614114.8837 | 1156780.1063 | 2614114.4546 | 1156776.6925 | 2614105.8983 | 1156763.1547 | 2614078.0614 | 1156682.1165 | 2614072.7571 | 1156674.7338 | 2614064.3463 | 1156667.7441 | 2614062.8146 | 1156663.6385 | 2614062.6239 | 1156659.9362 | 2614064.3183 | 1156656.7275 | 2614068.905 | 1156652.8918 | 2614103.7911 | 1156644.28 | 2614110.5503 | 1156643.2855
23 | 2613454.222 | 1156011.6763 | 2613461.5064 | 1156005.2004 | 2613469.7377 | 1156003.9959 | 2613474.7155 | 1156010.5436 | 2613478.8049 | 1156019.9796 | 2613497.8254 | 1156046.5017 | 2613517.5321 | 1156085.0648 | 2613530.4769 | 1156091.8638 | 2613568.1359 | 1156085.8007 | 2613602.6763 | 1156092.2259 | 2613615.3932 | 1156108.2513 | 2613616.5715 | 1156133.2663 | 2613620.2353 | 1156144.2578 | 2613617.9826 | 1156157.059 | 2613623.2177 | 1156175.1798 | 2613630.2251 | 1156189.4804 | 2613647.6954 | 1156195.6673 | 2613650.748 | 1156200.1542
24 | 2613454.222 | 1156011.6763 | 2613451.357 | 1156008.5016
25 | 2613454.222 | 1156011.6763 | 2613591.2669 | 1155890.3228
26 | 2613454.222 | 1156011.6763 | 2613359.6633 | 1156280.277
27 | 2614040.4556 | 1156211.2076 | 2614044.8037 | 1156221.0892 | 2614045.0904 | 1156223.1171
28 | 2614040.4556 | 1156211.2076 | 2614137.1069 | 1155995.9043
29 | 2614045.0904 | 1156223.1171 | 2614049.0135 | 1156250.8692 | 2614049.9529 | 1156262.4216 | 2614052.7353 | 1156266.2299 | 2614058.2794 | 1156269.6223 | 2614065.2385 | 1156271.2281 | 2614068.7886 | 1156271.2772
30 | 2614112.5531 | 1156267.77 | 2614092.3378 | 1156271.6025 | 2614068.7886 | 1156271.2772
31 | 2613643.1864 | 1156790.8045 | 2613636.9018 | 1156775.1624 | 2613642.8308 | 1156770.9737 | 2613637.0195 | 1156767.1698 | 2613648.2106 | 1156762.1148 | 2613642.4188 | 1156759.8562 | 2613636.6329 | 1156744.8246 | 2613652.7196 | 1156731.4098 | 2613664.9858 | 1156698.5213 | 2613644.9546 | 1156689.5605 | 2613634.9271 | 1156688.6263 | 2613647.2201 | 1156681.2059 | 2613663.1623 | 1156662.9298
32 | 2613439.6157 | 1156417.4774 | 2613435.2423 | 1156409.0655
33 | 2614309.9596 | 1156385.0142 | 2614313.6072 | 1156389.2916 | 2614316.6163 | 1156394.4346 | 2614324.1595 | 1156421.3102 | 2614323.9354 | 1156428.5021 | 2614322.347 | 1156432.2224 | 2614319.4431 | 1156434.4499 | 2614315.708 | 1156434.719 | 2614312.1461 | 1156433.1209 | 2614304.9129 | 1156424.2772 | 2614295.5426 | 1156417.6962 | 2614282.0264 | 1156413.2287 | 2614263.2532 | 1156410.5497 | 2614256.5856 | 1156410.3858
34 | 2614024.2259 | 1156810.6326 | 2614029.9854 | 1156820.1062 | 2614033.2082 | 1156822.3926 | 2614037.1084 | 1156823.5466 | 2614047.41 | 1156825.1603 | 2614050.9183 | 1156826.6914 | 2614053.6428 | 1156828.8877 | 2614060.0665 | 1156839.5968
35 | 2614024.2259 | 1156810.6326 | 2614014.9361 | 1156799.2165 | 2614012.1585 | 1156796.5714
36 | 2613591.2669 | 1155890.3228 | 2613574.4188 | 1155883.2815 | 2613566.9316 | 1155877.4952 | 2613564.1552 | 1155867.3506 | 2613561.5928 | 1155850.7256
37 | 2613591.2669 | 1155890.3228 | 2613611.45 | 1155908.0214 | 2613624.4342 | 1155917.8555 | 2613637.3198 | 1155920.4192 | 2613642.3503 | 1155921.4438
38 | 2613359.6633 | 1156280.277 | 2613368.2011 | 1156287.2892
39 | 2613359.6633 | 1156280.277 | 2613347.5279 | 1156278.616 | 2613330.6411 | 1156275.5773 | 2613312.4944 | 1156280.5509 | 2613308.0052 | 1156292.4246 | 2613312.992 | 1156297.133
40 | 2614060.0665 | 1156839.5968 | 2614069.0442 | 1156849.945
41 | 2614060.0665 | 1156839.5968 | 2614055.8175 | 1156866.4335 | 2614059.0816 | 1156877.3243 | 2614065.9653 | 1156884.6884 | 2614076.2015 | 1156888.0027 | 2614086.0314 | 1156888.0256 | 2614095.0681 | 1156889.4696 | 2614104.0474 | 1156899.1287 | 2614116.044 | 1156916.921 | 2614121.1317 | 1156931.5513 | 2614116.1123 | 1156973.0156 | 2614118.5322 | 1156981.9997
42 | 2613839.6886 | 1156973.8769 | 2613832.2463 | 1156972.6481 | 2613830.6774 | 1156971.3328 | 2613820.1707 | 1156948.8421 | 2613810.678 | 1156928.8438 | 2613806.6523 | 1156922.2314 | 2613802.3475 | 1156916.9523 | 2613793.9337 | 1156911.3081 | 2613790.1519 | 1156908.6648 | 2613786.5412 | 1156904.9658 | 2613779.7781 | 1156895.0344 | 2613776.6964 | 1156891.3589 | 2613774.8258 | 1156887.8751 | 2613773.54 | 1156883.4589 | 2613770.7003 | 1156871.1797 | 2613768.5298 | 1156864.6938 | 2613767.6625 | 1156861.6903 | 2613766.8498 | 1156858.309 | 2613765.5698 | 1156854.7155 | 2613763.4754 | 1156851.8648 | 2613753.809 | 1156840.6373 | 2613750.9274 | 1156836.6399 | 2613748.1471 | 1156831.8868 | 2613737.6612 | 1156813.4983 | 2613733.6208 | 1156806.5412 | 2613730.155 | 1156799.7745 | 2613728.6829 | 1156796.3361 | 2613727.6109 | 1156792.3094 | 2613727.1256 | 1156786.5499 | 2613726.7493 | 1156776.6775 | 2613726.1238 | 1156771.8515 | 2613724.8708 | 1156766.5016 | 2613721.2443 | 1156756.2105 | 2613714.9904 | 1156737.9984 | 2613712.8673 | 1156734.1334
43 | 2613899.9497 | 1157032.9888 | 2613890.3887 | 1157026.1634 | 2613877.3224 | 1157016.562 | 2613870.9935 | 1157011.3004 | 2613864.8106 | 1157005.9058 | 2613857.8039 | 1156998.6195 | 2613851.304 | 1156991.0119 | 2613845.0585 | 1156982.7491 | 2613839.6886 | 1156973.8769
44 | 2613700.8051 | 1156720.7201 | 2613704.8021 | 1156723.5015 | 2613709.3166 | 1156727.6693 | 2613712.8673 | 1156734.1334
45 | 2613899.9497 | 1157032.9888 | 2613909.1575 | 1157039.9912 | 2613917.239 | 1157046.6464 | 2613924.9205 | 1157053.8343 | 2613930.397 | 1157059.6387 | 2613935.4736 | 1157065.9535 | 2613939.7522 | 1157072.5222 | 2613943.5935 | 1157079.1788 | 2613949.5276 | 1157092.6658 | 2613953.6587 | 1157106.6378 | 2613970.5289 | 1157165.4391 | 2613975.0045 | 1157179.5898 | 2613979.7269 | 1157193.1296 | 2613985.7918 | 1157206.3502 | 2613992.171 | 1157219.5493 | 2614018.8465 | 1157267.949
46 | 2613899.9497 | 1157032.9888 | 2613898.2127 | 1157041.4667 | 2613915.2223 | 1157056.3896
47 | 2613915.2223 | 1157056.3896 | 2614118.5322 | 1156981.9997
48 | 2614336.8282 | 1156395.1384 | 2614332.603 | 1156391.8712 | 2614323.3577 | 1156387.5472 | 2614317.6023 | 1156386.0884 | 2614309.9596 | 1156385.0142
49 | 2614414.9723 | 1156351.4249 | 2614355.3466 | 1156350.1268 | 2614324.1862 | 1156345.3727 | 2614320.8627 | 1156343.4417 | 2614319.2674 | 1156340.3364 | 2614317.6486 | 1156330.9279 | 2614318.7554 | 1156316.9347 | 2614317.8816 | 1156313.531 | 2614315.2891 | 1156310.5344 | 2614311.7408 | 1156309.6367 | 2614308.394 | 1156311.0406 | 2614306.6609 | 1156314.3159 | 2614306.1403 | 1156326.8987 | 2614305.6022 | 1156330.7215 | 2614295.6763 | 1156354.7099 | 2614294.3729 | 1156361.0988 | 2614295.5052 | 1156368.6941 | 2614298.721 | 1156373.9932 | 2614309.9596 | 1156385.0142
50 | 2614414.9723 | 1156351.4249 | 2614439.0772 | 1156372.4706 | 2614444.3328 | 1156380.9095 | 2614448.0766 | 1156389.8451 | 2614447.6636 | 1156395.8026
51 | 2614018.8465 | 1157267.949 | 2614025.1428 | 1157279.3731
52 | 2613333.4387 | 1156387.4498 | 2613337.9363 | 1156385.6255 | 2613341.1106 | 1156385.7881 | 2613345.1802 | 1156386.8198 | 2613353.2027 | 1156389.6056 | 2613360.8985 | 1156391.0121 | 2613368.4584 | 1156391.4957 | 2613388.5591 | 1156390.5064 | 2613401.0496 | 1156390.9899 | 2613412.1354 | 1156392.1261 | 2613419.2484 | 1156393.5315 | 2613424.214 | 1156395.0766 | 2613427.3922 | 1156396.9068 | 2613431.8274 | 1156402.4972 | 2613435.2423 | 1156409.0655
53 | 2613310.894 | 1156366.5787 | 2613315.3844 | 1156371.5021 | 2613322.0329 | 1156378.4091 | 2613333.4387 | 1156387.4498
54 | 2613234.8483 | 1156653.4089 | 2613333.4387 | 1156387.4498
55 | 2614038.3362 | 1157303.5754 | 2614037.0344 | 1157300.9491 | 2614025.1428 | 1157279.3731
56 | 2614051.0944 | 1157331.23 | 2614044.5588 | 1157316.1296 | 2614038.3362 | 1157303.5754
57 | 2613691.5299 | 1156702.8168 | 2613694.7478 | 1156714.0963 | 2613699.1445 | 1156719.5645 | 2613700.8051 | 1156720.7201
58 | 2614051.0944 | 1157331.23 | 2614060.779 | 1157328.5496
59 | 2614077.8801 | 1157365.4537 | 2614077.8901 | 1157361.1516 | 2614072.9735 | 1157352.1246 | 2614069.0868 | 1157342.0661 | 2614066.2312 | 1157333.6553 | 2614064.3977 | 1157327.548 | 2614060.779 | 1157328.5496
60 | 2614051.0944 | 1157331.23 | 2614059.1958 | 1157352.1592 | 2614070.728 | 1157391.2609
61 | 2614070.728 | 1157391.2609 | 2614074.5348 | 1157402.7088 | 2614076.8603 | 1157408.2503 | 2614079.6309 | 1157413.6149 | 2614084.4285 | 1157421.0187 | 2614089.6407 | 1157428.1566 | 2614101.7995 | 1157441.7361 | 2614106.8068 | 1157447.9397 | 2614111.5297 | 1157454.4539 | 2614115.6466 | 1157461.1446 | 2614116.997 | 1157463.6525
62 | 2613944.8173 | 1157532.2611 | 2613945.6581 | 1157516.7665 | 2613951.3704 | 1157473.4027 | 2613951.3572 | 1157469.145 | 2613949.7565 | 1157465.0837 | 2613939.7373 | 1157454.4887
63 | 2613944.8173 | 1157532.2611 | 2613948.2938 | 1157540.74 | 2613953.0454 | 1157548.1768 | 2613960.0897 | 1157555.43 | 2613970.8774 | 1157561.8248 | 2613985.9526 | 1157567.4513 | 2613993.3596 | 1157573.6826 | 2614010.2552 | 1157594.332 | 2614015.3095 | 1157616.6436
64 | 2614015.3095 | 1157616.6436 | 2614022.3762 | 1157624.1415 | 2614029.2107 | 1157632.5393 | 2614042.7515 | 1157648.4119 | 2614075.9706 | 1157704.5614
65 | 2614015.3095 | 1157616.6436 | 2614017.2973 | 1157648.7863 | 2614023.3302 | 1157665.6198 | 2614024.3015 | 1157669.9464 | 2614023.8357 | 1157672.4354 | 2614021.6086 | 1157674.0866 | 2614018.4656 | 1157673.9459 | 2614015.1436 | 1157671.6593 | 2614014.25 | 1157670.1845
66 | 2613561.5928 | 1155850.7256 | 2613731.1517 | 1155648.8308
67 | 2613312.992 | 1156297.133 | 2613319.063 | 1156302.8652 | 2613332.3527 | 1156316.6124 | 2613332.5371 | 1156333.8102 | 2613332.7591 | 1156336.5734
68 | 2613332.7591 | 1156336.5734 | 2613333.6865 | 1156348.1198 | 2613323.9165 | 1156356.0322
69 | 2613310.894 | 1156366.5787 | 2613298.2431 | 1156352.7888
70 | 2613310.894 | 1156366.5787 | 2613323.9165 | 1156356.0322
71 | 2613234.8483 | 1156653.4089 | 2613234.6286 | 1156654.0709
72 | 2613294.0636 | 1156348.2329 | 2613298.2431 | 1156352.7888
73 | 2613238.0222 | 1156835.7392 | 2613231.5283 | 1156831.9676 | 2613224.0123 | 1156829.2387 | 2613219.9997 | 1156826.7954 | 2613216.3879 | 1156823.4303 | 2613212.6206 | 1156817.5747 | 2613210.5547 | 1156812.0452 | 2613209.6323 | 1156806.0847 | 2613209.678 | 1156799.1814 | 2613211.1056 | 1156791.5363 | 2613213.2388 | 1156783.8038 | 2613216.1962 | 1156777.8518 | 2613220.5093 | 1156772.592 | 2613224.4506 | 1156769.0766 | 2613231.2941 | 1156763.8001 | 2613232.9004 | 1156762.0917 | 2613234.0015 | 1156760.0153 | 2613234.3984 | 1156757.3259 | 2613234.2665 | 1156754.5354 | 2613231.8039 | 1156744.614 | 2613229.3881 | 1156734.3036 | 2613227.9946 | 1156726.3411 | 2613224.477 | 1156707.9243 | 2613223.7017 | 1156701.3082 | 2613223.7124 | 1156692.9041 | 2613224.3758 | 1156687.6251 | 2613225.5059 | 1156682.7808 | 2613232.1081 | 1156661.6626 | 2613234.6286 | 1156654.0709
74 | 2613294.0636 | 1156348.2329 | 2613280.6701 | 1156333.6336
75 | 2614026.4017 | 1155707.9487 | 2614028.2028 | 1155711.7215 | 2614030.8254 | 1155715.1292 | 2614036.5529 | 1155722.3238 | 2614041.1193 | 1155730.8164 | 2614046.6656 | 1155743.3688 | 2614051.8914 | 1155755.1868 | 2614057.9576 | 1155766.2339
76 | 2614026.4017 | 1155707.9487 | 2614026.4164 | 1155701.5901 | 2614026.9944 | 1155693.7876 | 2614025.5721 | 1155688.6706 | 2614023.0635 | 1155685.7412
77 | 2614026.4017 | 1155707.9487 | 2614013.3416 | 1155697.8135 | 2614004.88 | 1155692.2911 | 2613995.8429 | 1155686.9231 | 2613988.4801 | 1155683.4074
78 | 2613988.4801 | 1155683.4074 | 2613733.8833 | 1155633.4362
79 | 2613731.1517 | 1155648.8308 | 2613733.2199 | 1155646.5788 | 2613734.8666 | 1155644.1258 | 2613735.1633 | 1155641.8142 | 2613735.0762 | 1155639.6685 | 2613733.8833 | 1155633.4362
80 | 2614447.6636 | 1156395.8026 | 2614453.0548 | 1156385.9884 | 2614451.6735 | 1156360.7615 | 2614449.9621 | 1156342.126 | 2614447.7171 | 1156334.9393 | 2614439.5027 | 1156329.1835 | 2614423.1714 | 1156325.0203 | 2614403.4446 | 1156316.9804 | 2614398.726 | 1156311.6331 | 2614392.68 | 1156300.1575 | 2614391.1995 | 1156291.519
81 | 2614447.6636 | 1156395.8026 | 2614436.1715 | 1156417.1746 | 2614433.9158 | 1156427.3187 | 2614433.5751 | 1156438.3233 | 2614431.3054 | 1156447.9115 | 2614419.9471 | 1156464.7038 | 2614411.9541 | 1156478.7027 | 2614406.3977 | 1156483.881 | 2614402.896 | 1156486.0181 | 2614384.0395 | 1156492.6543 | 2614373.1988 | 1156498.2535 | 2614363.9435 | 1156504.6569 | 2614359.2934 | 1156509.237 | 2614357.2076 | 1156512.4781 | 2614356.447 | 1156516.3559 | 2614357.2355 | 1156520.1152 | 2614359.616 | 1156525.1345 | 2614361.7521 | 1156528.4039
82 | 2614512.3785 | 1156809.7844 | 2614499.4737 | 1156803.3614 | 2614488.9411 | 1156798.9784 | 2614471.1764 | 1156791.9768 | 2614465.5496 | 1156788.217 | 2614461.3208 | 1156783.4268 | 2614456.403 | 1156774.9441 | 2614450.8684 | 1156764.7259 | 2614448.9579 | 1156758.785 | 2614448.8372 | 1156751.5478 | 2614451.3533 | 1156741.5156 | 2614452.7991 | 1156733.2927 | 2614452.9186 | 1156725.0445 | 2614451.246 | 1156693.4137 | 2614450.7496 | 1156686.1312 | 2614449.0694 | 1156680.1353 | 2614445.4327 | 1156674.6017 | 2614429.0685 | 1156658.9215 | 2614424.8078 | 1156654.5981 | 2614420.8715 | 1156649.2638 | 2614413.7942 | 1156639.5533 | 2614408.6776 | 1156630.7812 | 2614404.0387 | 1156621.032 | 2614400.5965 | 1156611.0744 | 2614395.3416 | 1156592.764 | 2614390.1694 | 1156578.3001 | 2614376.3176 | 1156550.6979 | 2614361.7521 | 1156528.4039
83 | 2614512.3785 | 1156809.7844 | 2614510.8472 | 1156815.2278 | 2614510.8784 | 1156818.1738 | 2614513.5769 | 1156834.3883 | 2614520.1421 | 1156862.3846 | 2614522.7662 | 1156871.2175 | 2614525.8577 | 1156880.2182 | 2614530.3359 | 1156892.8241 | 2614535.3985 | 1156904.7422 | 2614539.2891 | 1156913.0334 | 2614543.9086 | 1156921.093
84 | 2614512.3785 | 1156809.7844 | 2614543.0973 | 1156828.0895 | 2614545.3092 | 1156829.1763
85 | 2614543.9086 | 1156921.093 | 2614453.1255 | 1157033.9016
86 | 2614584.0997 | 1156842.6622 | 2614577.175 | 1156839.7885 | 2614554.6715 | 1156832.9642 | 2614548.9179 | 1156830.9494 | 2614545.3092 | 1156829.1763
87 | 2614584.0997 | 1156842.6622 | 2614583.9179 | 1156838.5486 | 2614583.3525 | 1156834.5452 | 2614580.8622 | 1156824.3119 | 2614577.9382 | 1156815.8674 | 2614575.9328 | 1156811.238 | 2614573.2837 | 1156806.4293 | 2614559.9929 | 1156791.5677 | 2614556.6063 | 1156787.3574 | 2614553.4896 | 1156782.4697 | 2614551.3626 | 1156777.351 | 2614549.4524 | 1156771.3879 | 2614546.242 | 1156757.6511 | 2614542.2959 | 1156743.7236 | 2614538.2067 | 1156731.908 | 2614533.4653 | 1156720.2797 | 2614531.5896 | 1156715.8953 | 2614530.8008 | 1156712.2693 | 2614530.9062 | 1156709.9018 | 2614532.2226 | 1156707.7372 | 2614534.9617 | 1156707.0434 | 2614537.8957 | 1156708.1955 | 2614543.9168 | 1156713.8239
88 | 2614453.1255 | 1157033.9016 | 2614470.5707 | 1157052.542
89 | 2614453.1255 | 1157033.9016 | 2614447.1575 | 1157027.5247 | 2614432.9001 | 1157012.9834 | 2614426.2065 | 1157006.5087 | 2614419.1508 | 1157000.7779 | 2614417.6432 | 1156999.7477
90 | 2614583.8254 | 1157102.3899 | 2614575.0599 | 1157099.9342 | 2614567.1457 | 1157097.3472 | 2614524.5117 | 1157082.8485 | 2614504.0707 | 1157076.3629 | 2614497.3602 | 1157073.79 | 2614490.9653 | 1157070.7287 | 2614484.9862 | 1157066.9458 | 2614479.9821 | 1157062.5983 | 2614470.5707 | 1157052.542
91 | 2614382.1129 | 1156981.8638 | 2614383.6482 | 1156982.3509 | 2614390.8867 | 1156985.3807 | 2614397.8408 | 1156988.7323 | 2614408.9071 | 1156994.3169 | 2614414.2209 | 1156997.4089 | 2614417.6432 | 1156999.7477
92 | 2614583.8254 | 1157102.3899 | 2614594.0405 | 1157104.6712 | 2614600.0346 | 1157105.3749 | 2614604.5597 | 1157104.8189 | 2614614.5421 | 1157101.8749 | 2614620.9704 | 1157100.6121 | 2614628.6525 | 1157100.8419
93 | 2614583.8254 | 1157102.3899 | 2614574.8878 | 1157114.0407 | 2614571.4854 | 1157119.602 | 2614569.5715 | 1157124.7666 | 2614569.0984 | 1157130.1792 | 2614570.474 | 1157135.2295 | 2614572.3569 | 1157139.7807 | 2614587.8486 | 1157169.9774 | 2614593.7589 | 1157179.9744 | 2614602.3279 | 1157193.8909 | 2614602.8875 | 1157194.9803
94 | 2614628.6525 | 1157100.8419 | 2614609.3111 | 1157089.9675
95 | 2614628.6525 | 1157100.8419 | 2614636.1301 | 1157103.2056 | 2614650.0464 | 1157109.5425 | 2614660.503 | 1157113.3586 | 2614670.7323 | 1157116.0736
96 | 2614670.7323 | 1157116.0736 | 2614665.987 | 1157128.3904 | 2614664.4869 | 1157133.6116 | 2614664.3126 | 1157139.0917 | 2614665.6128 | 1157146.7097 | 2614675.9872 | 1157174.9155 | 2614677.983 | 1157183.4134 | 2614678.3725 | 1157190.3845 | 2614675.6913 | 1157195.7028 | 2614669.0397 | 1157197.3986 | 2614665.5356 | 1157196.813
97 | 2614670.7323 | 1157116.0736 | 2614676.4562 | 1157117.5772 | 2614680.9432 | 1157119.4436
98 | 2613076.0182 | 1156113.0635 | 2613079.9499 | 1156121.2315 | 2613083.9285 | 1156128.944 | 2613088.4619 | 1156135.457 | 2613093.8715 | 1156141.0159 | 2613117.9559 | 1156159.9107 | 2613128.5509 | 1156168.3045 | 2613137.1984 | 1156176.594 | 2613145.174 | 1156186.9943 | 2613154.1699 | 1156200.7428 | 2613161.1096 | 1156211.4744 | 2613165.4996 | 1156216.8199 | 2613170.4273 | 1156221.7886 | 2613178.0968 | 1156228.3752 | 2613194.4581 | 1156240.3613 | 2613205.0688 | 1156248.5218 | 2613226.3963 | 1156268.8228 | 2613236.963 | 1156279.4846 | 2613246.9392 | 1156290.1783 | 2613276.6297 | 1156329.2294 | 2613280.6701 | 1156333.6336
99 | 2613076.0182 | 1156113.0635 | 2613068.3983 | 1156094.1043 | 2613064.2622 | 1156084.6685 | 2613059.5732 | 1156075.6428 | 2613054.5981 | 1156067.6726 | 2613049.1627 | 1156059.7903 | 2613043.2514 | 1156052.1071 | 2613037.0251 | 1156044.69 | 2613029.7332 | 1156037.0817 | 2613022.1031 | 1156029.8505 | 2613014.2565 | 1156023.3971 | 2613006.1794 | 1156017.1767 | 2612996.1189 | 1156009.6514 | 2612990.936 | 1156006.0889
100 | 2613077.1659 | 1156036.2725 | 2613080.3972 | 1156056.256 | 2613080.8225 | 1156065.2391 | 2613080.4737 | 1156074.0761 | 2613079.7839 | 1156084.5353 | 2613079.9198 | 1156092.6174 | 2613080.4974 | 1156102.09 | 2613080.7096 | 1156106.7927 | 2613079.9988 | 1156109.2702 | 2613076.0182 | 1156113.0635
101 | 2612979.0351 | 1155997.9089 | 2612990.936 | 1156006.0889
102 | 2612979.0351 | 1155997.9089 | 2612982.1754 | 1155989.0335 | 2612984.201 | 1155981.4007
103 | 2612979.0351 | 1155997.9089 | 2612976.6013 | 1156002.8172 | 2612974.5308 | 1156006.3478 | 2612971.8553 | 1156009.5214 | 2612970.6647 | 1156010.7715
104 | 2612981.1912 | 1155972.3676 | 2612984.0723 | 1155977.0539 | 2612984.201 | 1155981.4007
105 | 2612964.0155 | 1156017.7531 | 2612970.6647 | 1156010.7715
106 | 2613134.4851 | 1156761.777 | 2613150.6368 | 1156763.7797 | 2613161.6976 | 1156765.5046 | 2613172.8071 | 1156769.2287
107 | 2613238.0222 | 1156835.7392 | 2613223.7703 | 1156834.6742 | 2613218.0457 | 1156833.2387 | 2613203.7803 | 1156827.816 | 2613197.5158 | 1156824.3228 | 2613193.8188 | 1156821.3133 | 2613190.7221 | 1156817.3268 | 2613188.4189 | 1156811.6078 | 2613187.1251 | 1156803.6677 | 2613187.4179 | 1156788.9278 | 2613186.9569 | 1156782.368 | 2613184.3531 | 1156777.3376 | 2613180.3672 | 1156773.238 | 2613173.7809 | 1156769.5552 | 2613172.8071 | 1156769.2287
108 | 2613134.4851 | 1156761.777 | 2613125.8023 | 1156759.6015 | 2613117.9191 | 1156756.3606 | 2613111.1252 | 1156752.9552
109 | 2613134.4851 | 1156761.777 | 2613137.9428 | 1156765.5419 | 2613146.8515 | 1156769.5602
110 | 2613238.0222 | 1156835.7392 | 2613250.0642 | 1156837.5554 | 2613253.4316 | 1156838.2945
111 | 2613111.1252 | 1156752.9552 | 2613110.0253 | 1156740.3689 | 2613108.8497 | 1156713.1974 | 2613107.9019 | 1156701.2116 | 2613106.5327 | 1156696.1395 | 2613103.9682 | 1156690.6423
112 | 2613253.4316 | 1156838.2945 | 2613260.1424 | 1156839.7675 | 2613266.9683 | 1156842.506 | 2613272.1518 | 1156845.9079 | 2613286.1502 | 1156857.6556 | 2613299.5789 | 1156870.3692 | 2613302.4205 | 1156873.3413
113 | 2613098.2169 | 1156683.7598 | 2613103.9682 | 1156690.6423
114 | 2613307.8333 | 1156879.0027 | 2613302.4205 | 1156873.3413
115 | 2613307.8333 | 1156879.0027 | 2613311.2443 | 1156882.9788
116 | 2613304.9669 | 1156847.0918 | 2613304.1248 | 1156856.9281 | 2613306.204 | 1156870.2615 | 2613307.8333 | 1156879.0027
117 | 2613440.2254 | 1157022.6109 | 2613399.1245 | 1156968.7597 | 2613388.0782 | 1156957.2185 | 2613375.4855 | 1156944.551 | 2613346.7261 | 1156919.5195 | 2613337.0996 | 1156910.7495 | 2613327.0926 | 1156900.6892 | 2613311.2443 | 1156882.9788
118 | 2613311.2443 | 1156882.9788 | 2613302.3585 | 1156889.5292 | 2613299.3126 | 1156893.8246 | 2613298.6898 | 1156898.1254 | 2613298.8553 | 1156916.9906 | 2613294.9421 | 1156918.2048 | 2613290.2018 | 1156922.5076 | 2613289.3678 | 1156928.6533 | 2613291.3239 | 1156935.2608 | 2613293.6875 | 1156938.8371
119 | 2613302.1159 | 1156836.0133 | 2613304.367 | 1156840.943 | 2613304.9669 | 1156847.0918
120 | 2613318.3681 | 1156834.0037 | 2613316.0958 | 1156838.7121 | 2613304.9669 | 1156847.0918
121 | 2613440.2254 | 1157022.6109 | 2613485.852 | 1157085.5324 | 2613497.8602 | 1157109.0486 | 2613509.8964 | 1157126.8954
122 | 2613440.2254 | 1157022.6109 | 2613441.35 | 1157020.2678 | 2613441.4253 | 1157017.4443 | 2613431.1294 | 1156992.6203 | 2613428.1436 | 1156983.6982 | 2613427.0026 | 1156976.1363 | 2613425.3711 | 1156947.7631 | 2613424.136 | 1156937.6999 | 2613422.3805 | 1156930.6258 | 2613419.6783 | 1156925.1393 | 2613415.25 | 1156919.5177
123 | 2613296.5311 | 1156945.2772 | 2613294.6864 | 1156940.3485 | 2613293.6875 | 1156938.8371
124 | 2613509.8964 | 1157126.8954 | 2613508.0515 | 1157132.4496 | 2613513.4745 | 1157141.7441 | 2613517.9707 | 1157154.0491 | 2613519.5996 | 1157159.3776 | 2613525.1314 | 1157168.0054
125 | 2613509.8964 | 1157126.8954 | 2613562.8609 | 1157185.5875 | 2613586.3191 | 1157214.4433
126 | 2613413.0977 | 1156916.7854 | 2613415.25 | 1156919.5177
127 | 2613595.1035 | 1157239.2975 | 2613589.9754 | 1157231.9046 | 2613587.5223 | 1157224.9289 | 2613586.3191 | 1157214.4433
128 | 2613643.0318 | 1157286.4732 | 2613612.6902 | 1157246.8964 | 2613586.3191 | 1157214.4433
129 | 2613643.0318 | 1157286.4732 | 2613658.1163 | 1157301.9927
130 | 2613643.0318 | 1157286.4732 | 2613640.8292 | 1157297.6182 | 2613641.0038 | 1157311.9702
131 | 2613643.0318 | 1157286.4732 | 2613642.3953 | 1157279.7351 | 2613637.6066 | 1157268.0964 | 2613634.1576 | 1157247.1782 | 2613629.6914 | 1157221.7445 | 2613630.1292 | 1157207.8053 | 2613632.4532 | 1157183.6208 | 2613631.4644 | 1157163.1195 | 2613632.1563 | 1157148.7029
132 | 2613554.6737 | 1157030.5903 | 2613538.4854 | 1157027.707
133 | 2613573.4603 | 1157033.9363 | 2613554.6737 | 1157030.5903
134 | 2613573.4603 | 1157033.9363 | 2613570.0843 | 1157024.702 | 2613566.9267 | 1157013.8451 | 2613563.9719 | 1157001.4323 | 2613562.7528 | 1156991.169 | 2613562.7757 | 1156984.3656 | 2613563.407 | 1156976.4187 | 2613564.6571 | 1156969.4514 | 2613569.8058 | 1156964.3271
135 | 2613573.4603 | 1157033.9363 | 2613584.8355 | 1157049.036 | 2613600.3341 | 1157071.6598 | 2613610.3697 | 1157089.1021 | 2613619.0047 | 1157105.463
136 | 2613689.9556 | 1157126.9672 | 2613682.1528 | 1157122.4361 | 2613676.6084 | 1157116.076 | 2613663.7061 | 1157094.9253 | 2613658.3705 | 1157087.743 | 2613652.6216 | 1157083.628 | 2613646.2519 | 1157082.791 | 2613640.0746 | 1157085.0337 | 2613627.3063 | 1157092.7976 | 2613621.9253 | 1157098.9219 | 2613619.0047 | 1157105.463
137 | 2613619.0047 | 1157105.463 | 2613628.4278 | 1157136.4445
138 | 2613628.4278 | 1157136.4445 | 2613631.1636 | 1157145.439
139 | 2613632.1563 | 1157148.7029 | 2613631.1636 | 1157145.439
140 | 2613658.1163 | 1157301.9927 | 2613658.2837 | 1157309.3412 | 2613661.1445 | 1157315.7064
141 | 2613658.1163 | 1157301.9927 | 2613663.5682 | 1157308.4972 | 2613670.8232 | 1157328.0121
142 | 2613670.8232 | 1157328.0121 | 2613677.8634 | 1157347.9345
143 | 2613670.8232 | 1157328.0121 | 2613679.0398 | 1157315.5356 | 2613689.1361 | 1157305.9315 | 2613696.7611 | 1157300.824 | 2613702.2985 | 1157299.2164
144 | 2613705.1781 | 1157298.3804 | 2613702.2985 | 1157299.2164
145 | 2613774.5468 | 1157275.9885 | 2613763.0168 | 1157282.1097 | 2613749.4307 | 1157288.8488 | 2613730.4958 | 1157294.3307 | 2613717.5405 | 1157296.7691 | 2613708.6913 | 1157297.3605 | 2613705.1781 | 1157298.3804
146 | 2613709.3624 | 1157403.17 | 2613705.4252 | 1157398.7365 | 2613692.5813 | 1157382.5883 | 2613683.4237 | 1157363.6693 | 2613677.8634 | 1157347.9345
147 | 2613709.3624 | 1157403.17 | 2613720.1355 | 1157415.301
148 | 2613730.363 | 1157426.9959 | 2613725.3085 | 1157421.126 | 2613720.1355 | 1157415.301
149 | 2613730.363 | 1157426.9959 | 2613735.0122 | 1157432.3981
150 | 2613729.1083 | 1157452.7947 | 2613727.718 | 1157433.7266 | 2613730.363 | 1157426.9959
151 | 2613735.0122 | 1157432.3981 | 2613780.8234 | 1157485.6175 | 2613802.8892 | 1157508.8794 | 2613823.3862 | 1157520.7209 | 2613833.7872 | 1157525.3248
152 | 2613735.0122 | 1157432.3981 | 2613743.1454 | 1157429.6596 | 2613766.1777 | 1157429.3008 | 2613786.1288 | 1157428.5236 | 2613815.5508 | 1157423.4661 | 2613827.1839 | 1157421.753
153 | 2613833.7872 | 1157525.3248 | 2613836.5085 | 1157518.8389 | 2613851.8487 | 1157465.7811 | 2613854.7521 | 1157456.7722
154 | 2613833.7872 | 1157525.3248 | 2613828.8734 | 1157531.7389 | 2613828.2379 | 1157538.0851 | 2613829.2593 | 1157544.0348 | 2613831.7058 | 1157550.3991 | 2613835.8591 | 1157556.2163
155 | 2613859.4823 | 1157640.7407 | 2613845.0249 | 1157572.9741 | 2613839.2105 | 1157560.9103 | 2613835.8591 | 1157556.2163
156 | 2613938.058 | 1157584.2045 | 2613932.9219 | 1157576.7926
157 | 2613938.058 | 1157584.2045 | 2613959.7241 | 1157610.801 | 2613985.3216 | 1157634.7053 | 2614002.7626 | 1157652.3483
158 | 2613938.058 | 1157584.2045 | 2613938.4732 | 1157597.0007
159 | 2613859.4823 | 1157640.7407 | 2613844.2124 | 1157650.9998
160 | 2613859.4823 | 1157640.7407 | 2613864.3493 | 1157637.9949 | 2613870.8429 | 1157631.3399 | 2613879.8237 | 1157623.2787 | 2613889.9545 | 1157618.6219 | 2613906.6794 | 1157610.2785 | 2613908.531 | 1157609.6281
161 | 2613844.2124 | 1157650.9998 | 2613843.9487 | 1157651.1769 | 2613831.9374 | 1157656.8633 | 2613787.2306 | 1157674.7923 | 2613761.803 | 1157683.7388 | 2613755.5247 | 1157685.4971
162 | 2613938.4732 | 1157597.0007 | 2613921.1735 | 1157605.1871 | 2613908.531 | 1157609.6281
163 | 2613752.0896 | 1157686.4591 | 2613755.5247 | 1157685.4971
164 | 2613938.4732 | 1157597.0007 | 2613938.7241 | 1157604.5606 | 2613937.6717 | 1157615.4191 | 2613935.7752 | 1157633.2568 | 2613936.202 | 1157634.3137
165 | 2614002.7626 | 1157652.3483 | 2614004.5199 | 1157654.126 | 2614014.25 | 1157670.1845

## bus_geodata
| x | y | coords
0 | 2614279.2358 | 1157659.8473
1 | 2614352.6444 | 1157690.783
2 | 2614270.647 | 1157740.7802
3 | 2614282.7095 | 1157716.8191
4 | 2614242.4308 | 1157768.2161
5 | 2614257.7235 | 1157710.5904
6 | 2614131.7265 | 1157507.4729
7 | 2614227.7568 | 1157768.3483
8 | 2613847.6848 | 1156411.4026
9 | 2613780.6309 | 1156443.6912
10 | 2613865.1075 | 1156351.8057
11 | 2613782.931 | 1156482.782
12 | 2613713.5271 | 1156450.1863
13 | 2614008.64 | 1156261.2682
14 | 2613671.302 | 1156648.622
15 | 2613685.8538 | 1156432.8686
16 | 2614042.0625 | 1156456.7167
17 | 2614185.6652 | 1156417.4372
18 | 2614110.5503 | 1156643.2855
19 | 2613650.748 | 1156200.1542
20 | 2613454.222 | 1156011.6763
21 | 2614040.4556 | 1156211.2076
22 | 2614045.0904 | 1156223.1171
23 | 2614137.1069 | 1155995.9043
24 | 2614068.7886 | 1156271.2772
25 | 2613663.1623 | 1156662.9298
26 | 2613439.6157 | 1156417.4774
27 | 2614256.5856 | 1156410.3858
28 | 2614112.5531 | 1156267.77
29 | 2614024.2259 | 1156810.6326
30 | 2613451.357 | 1156008.5016
31 | 2613591.2669 | 1155890.3228
32 | 2613359.6633 | 1156280.277
33 | 2614012.1585 | 1156796.5714
34 | 2614060.0665 | 1156839.5968
35 | 2613839.6886 | 1156973.8769
36 | 2613712.8673 | 1156734.1334
37 | 2613899.9497 | 1157032.9888
38 | 2614069.0442 | 1156849.945
39 | 2614118.5322 | 1156981.9997
40 | 2614309.9596 | 1156385.0142
41 | 2614336.8282 | 1156395.1384
42 | 2614414.9723 | 1156351.4249
43 | 2613915.2223 | 1157056.3896
44 | 2614018.8465 | 1157267.949
45 | 2613435.2423 | 1156409.0655
46 | 2613333.4387 | 1156387.4498
47 | 2613643.1864 | 1156790.8045
48 | 2614025.1428 | 1157279.3731
49 | 2614038.3362 | 1157303.5754
50 | 2613700.8051 | 1156720.7201
51 | 2614060.779 | 1157328.5496
52 | 2614051.0944 | 1157331.23
53 | 2614077.8801 | 1157365.4537
54 | 2614070.728 | 1157391.2609
55 | 2614116.997 | 1157463.6525
56 | 2613944.8173 | 1157532.2611
57 | 2613939.7373 | 1157454.4887
58 | 2614015.3095 | 1157616.6436
59 | 2613642.3503 | 1155921.4438
60 | 2613561.5928 | 1155850.7256
61 | 2613312.992 | 1156297.133
62 | 2613332.7591 | 1156336.5734
63 | 2613368.2011 | 1156287.2892
64 | 2613310.894 | 1156366.5787
65 | 2613234.8483 | 1156653.4089
66 | 2613298.2431 | 1156352.7888
67 | 2613323.9165 | 1156356.0322
68 | 2613234.6286 | 1156654.0709
69 | 2613294.0636 | 1156348.2329
70 | 2614057.9576 | 1155766.2339
71 | 2614026.4017 | 1155707.9487
72 | 2614023.0635 | 1155685.7412
73 | 2613988.4801 | 1155683.4074
74 | 2613733.8833 | 1155633.4362
75 | 2613731.1517 | 1155648.8308
76 | 2614391.1995 | 1156291.519
77 | 2614447.6636 | 1156395.8026
78 | 2614361.7521 | 1156528.4039
79 | 2614512.3784 | 1156809.7844
80 | 2614543.9086 | 1156921.093
81 | 2614545.3092 | 1156829.1763
82 | 2614584.0997 | 1156842.6622
83 | 2614543.9168 | 1156713.8239
84 | 2614453.1255 | 1157033.9016
85 | 2614470.5707 | 1157052.542
86 | 2614417.6432 | 1156999.7477
87 | 2614583.8254 | 1157102.3899
88 | 2614382.1129 | 1156981.8638
89 | 2614628.6525 | 1157100.8419
90 | 2614602.8875 | 1157194.9803
91 | 2614609.3111 | 1157089.9675
92 | 2614670.7323 | 1157116.0736
93 | 2614680.9432 | 1157119.4436
94 | 2614665.5356 | 1157196.813
95 | 2613280.6701 | 1156333.6336
96 | 2613076.0182 | 1156113.0635
97 | 2612990.936 | 1156006.0889
98 | 2613077.1659 | 1156036.2725
99 | 2612979.0351 | 1155997.9089
100 | 2612984.201 | 1155981.4007
101 | 2612970.6647 | 1156010.7715
102 | 2613172.8071 | 1156769.2287
103 | 2613134.4851 | 1156761.777
104 | 2613238.0222 | 1156835.7392
105 | 2613111.1252 | 1156752.9552
106 | 2613146.8515 | 1156769.5602
107 | 2613253.4316 | 1156838.2945
108 | 2613103.9682 | 1156690.6423
109 | 2613302.4205 | 1156873.3413
110 | 2613098.2169 | 1156683.7598
111 | 2613307.8333 | 1156879.0027
112 | 2613311.2443 | 1156882.9788
113 | 2613304.9669 | 1156847.0918
114 | 2613440.2254 | 1157022.6109
115 | 2613293.6875 | 1156938.8371
116 | 2613302.1159 | 1156836.0133
117 | 2613318.3681 | 1156834.0037
118 | 2613509.8964 | 1157126.8954
119 | 2613415.25 | 1156919.5177
120 | 2613296.5311 | 1156945.2772
121 | 2613413.0977 | 1156916.7854
122 | 2613525.1314 | 1157168.0054
123 | 2613586.3191 | 1157214.4433
124 | 2613595.1035 | 1157239.2975
125 | 2613643.0318 | 1157286.4732
126 | 2613538.4854 | 1157027.707
127 | 2613554.6737 | 1157030.5903
128 | 2613573.4603 | 1157033.9363
129 | 2613569.8058 | 1156964.3271
130 | 2613619.0047 | 1157105.463
131 | 2613689.9556 | 1157126.9672
132 | 2613628.4278 | 1157136.4445
133 | 2613631.1636 | 1157145.439
134 | 2613632.1563 | 1157148.7029
135 | 2613658.1163 | 1157301.9927
136 | 2613641.0038 | 1157311.9702
137 | 2613661.1445 | 1157315.7064
138 | 2613670.8232 | 1157328.0121
139 | 2613702.2985 | 1157299.2164
140 | 2613705.1781 | 1157298.3804
141 | 2613774.5468 | 1157275.9885
142 | 2613677.8634 | 1157347.9345
143 | 2613709.3624 | 1157403.17
144 | 2613720.1355 | 1157415.301
145 | 2613730.363 | 1157426.9959
146 | 2613735.0122 | 1157432.3981
147 | 2613729.1083 | 1157452.7947
148 | 2613833.7872 | 1157525.3248
149 | 2613827.1839 | 1157421.753
150 | 2613854.7521 | 1157456.7722
151 | 2613835.8591 | 1157556.2163
152 | 2613932.9219 | 1157576.7926
153 | 2613938.058 | 1157584.2045
154 | 2613859.4823 | 1157640.7407
155 | 2613844.2124 | 1157650.9998
156 | 2613908.531 | 1157609.6281
157 | 2613755.5247 | 1157685.4971
158 | 2613938.4732 | 1157597.0007
159 | 2614002.7626 | 1157652.3483
160 | 2613752.0896 | 1157686.4591
161 | 2613936.202 | 1157634.3137
162 | 2614014.25 | 1157670.1845
163 | 2614075.9706 | 1157704.5614
164 | 2613691.5299 | 1156702.8168
165 | 2612964.0155 | 1156017.7531
166 | 2612981.1912 | 1155972.3676
167 | 2613712.8673 | 1156734.1334

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1