## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_563-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_563-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_563-13_0_3_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_563-13_0_3_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_563-13_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_563-13_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_563-13_0_3_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_563-13_0_3_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_563-13_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_563-13_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_563-13_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_563-13_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_563-13_0_3_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_563-13_0_3_node_28 | 0.4 | n |  | TRUE
14 | bus_LV_563-13_0_3_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_563-13_0_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_563-13_0_3_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_563-13_0_3_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_563-13_0_3_node_202 | 0.4 | n |  | TRUE
19 | bus_LV_563-13_0_3_node_200 | 0.4 | n |  | TRUE
20 | bus_LV_563-13_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_563-13_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_563-13_0_3_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_563-13_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_563-13_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_563-13_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_563-13_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_563-13_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_563-13_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_563-13_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_563-13_0_3_node_274 | 0.4 | n |  | TRUE
31 | bus_LV_563-13_0_3_node_217 | 0.4 | n |  | TRUE
32 | bus_LV_563-13_0_3_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_563-13_0_3_node_216 | 0.4 | n |  | TRUE
34 | bus_LV_563-13_0_3_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_563-13_0_3_node_104 | 0.4 | n |  | TRUE
36 | bus_LV_563-13_0_3_node_105 | 0.4 | n |  | TRUE
37 | bus_LV_563-13_0_3_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_563-13_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_563-13_0_3_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_563-13_0_3_node_272 | 0.4 | n |  | TRUE
41 | bus_LV_563-13_0_3_node_199 | 0.4 | n |  | TRUE
42 | bus_LV_563-13_0_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_563-13_0_3_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_563-13_0_3_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_563-13_0_3_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_563-13_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_563-13_0_3_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_563-13_0_3_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_563-13_0_3_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_563-13_0_3_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_563-13_0_3_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_563-13_0_3_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_563-13_0_3_node_193 | 0.4 | n |  | TRUE
54 | bus_LV_563-13_0_3_node_201 | 0.4 | n |  | TRUE
55 | bus_LV_563-13_0_3_node_183 | 0.4 | n |  | TRUE
56 | bus_LV_563-13_0_3_node_195 | 0.4 | n |  | TRUE
57 | bus_LV_563-13_0_3_node_158 | 0.4 | n |  | TRUE
58 | bus_LV_563-13_0_3_node_157 | 0.4 | n |  | TRUE
59 | bus_LV_563-13_0_3_node_151 | 0.4 | n |  | TRUE
60 | bus_LV_563-13_0_3_node_149 | 0.4 | n |  | TRUE
61 | bus_LV_563-13_0_3_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_563-13_0_3_node_108 | 0.4 | n |  | TRUE
63 | bus_LV_563-13_0_3_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_563-13_0_3_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_563-13_0_3_node_112 | 0.4 | n |  | TRUE
66 | bus_LV_563-13_0_3_node_116 | 0.4 | n |  | TRUE
67 | bus_LV_563-13_0_3_node_127 | 0.4 | n |  | TRUE
68 | bus_LV_563-13_0_3_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_563-13_0_3_node_115 | 0.4 | n |  | TRUE
70 | bus_LV_563-13_0_3_node_117 | 0.4 | n |  | TRUE
71 | bus_LV_563-13_0_3_node_137 | 0.4 | n |  | TRUE
72 | bus_LV_563-13_0_3_node_138 | 0.4 | n |  | TRUE
73 | bus_LV_563-13_0_3_node_128 | 0.4 | n |  | TRUE
74 | bus_LV_563-13_0_3_node_129 | 0.4 | n |  | TRUE
75 | bus_LV_563-13_0_3_node_113 | 0.4 | n |  | TRUE
76 | bus_LV_563-13_0_3_node_118 | 0.4 | n |  | TRUE
77 | bus_LV_563-13_0_3_node_141 | 0.4 | n |  | TRUE
78 | bus_LV_563-13_0_3_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_563-13_0_3_node_120 | 0.4 | n |  | TRUE
80 | bus_LV_563-13_0_3_node_264 | 0.4 | n |  | TRUE
81 | bus_LV_563-13_0_3_node_125 | 0.4 | n |  | TRUE
82 | bus_LV_563-13_0_3_node_123 | 0.4 | n |  | TRUE
83 | bus_LV_563-13_0_3_node_124 | 0.4 | n |  | TRUE
84 | bus_LV_563-13_0_3_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_563-13_0_3_node_121 | 0.4 | n |  | TRUE
86 | bus_LV_563-13_0_3_node_273 | 0.4 | n |  | TRUE
87 | bus_LV_563-13_0_3_node_122 | 0.4 | n |  | TRUE
88 | bus_LV_563-13_0_3_node_265 | 0.4 | n |  | TRUE
89 | bus_LV_563-13_0_3_node_130 | 0.4 | n |  | TRUE
90 | bus_LV_563-13_0_3_node_133 | 0.4 | n |  | TRUE
91 | bus_LV_563-13_0_3_node_135 | 0.4 | n |  | TRUE
92 | bus_LV_563-13_0_3_node_131 | 0.4 | n |  | TRUE
93 | bus_LV_563-13_0_3_node_132 | 0.4 | n |  | TRUE
94 | bus_LV_563-13_0_3_node_134 | 0.4 | n |  | TRUE
95 | bus_LV_563-13_0_3_node_136 | 0.4 | n |  | TRUE
96 | bus_LV_563-13_0_3_node_246 | 0.4 | n |  | TRUE
97 | bus_LV_563-13_0_3_node_249 | 0.4 | n |  | TRUE
98 | bus_LV_563-13_0_3_node_224 | 0.4 | n |  | TRUE
99 | bus_LV_563-13_0_3_node_142 | 0.4 | n |  | TRUE
100 | bus_LV_563-13_0_3_node_143 | 0.4 | n |  | TRUE
101 | bus_LV_563-13_0_3_node_144 | 0.4 | n |  | TRUE
102 | bus_LV_563-13_0_3_node_145 | 0.4 | n |  | TRUE
103 | bus_LV_563-13_0_3_node_146 | 0.4 | n |  | TRUE
104 | bus_LV_563-13_0_3_node_147 | 0.4 | n |  | TRUE
105 | bus_LV_563-13_0_3_node_148 | 0.4 | n |  | TRUE
106 | bus_LV_563-13_0_3_node_242 | 0.4 | n |  | TRUE
107 | bus_LV_563-13_0_3_node_154 | 0.4 | n |  | TRUE
108 | bus_LV_563-13_0_3_node_243 | 0.4 | n |  | TRUE
109 | bus_LV_563-13_0_3_node_152 | 0.4 | n |  | TRUE
110 | bus_LV_563-13_0_3_node_150 | 0.4 | n |  | TRUE
111 | bus_LV_563-13_0_3_node_159 | 0.4 | n |  | TRUE
112 | bus_LV_563-13_0_3_node_160 | 0.4 | n |  | TRUE
113 | bus_LV_563-13_0_3_node_162 | 0.4 | n |  | TRUE
114 | bus_LV_563-13_0_3_node_169 | 0.4 | n |  | TRUE
115 | bus_LV_563-13_0_3_node_170 | 0.4 | n |  | TRUE
116 | bus_LV_563-13_0_3_node_207 | 0.4 | n |  | TRUE
117 | bus_LV_563-13_0_3_node_210 | 0.4 | n |  | TRUE
118 | bus_LV_563-13_0_3_node_205 | 0.4 | n |  | TRUE
119 | bus_LV_563-13_0_3_node_194 | 0.4 | n |  | TRUE
120 | bus_LV_563-13_0_3_node_196 | 0.4 | n |  | TRUE
121 | bus_LV_563-13_0_3_node_197 | 0.4 | n |  | TRUE
122 | bus_LV_563-13_0_3_node_198 | 0.4 | n |  | TRUE
123 | bus_LV_563-13_0_3_node_204 | 0.4 | n |  | TRUE
124 | bus_LV_563-13_0_3_node_206 | 0.4 | n |  | TRUE
125 | bus_LV_563-13_0_3_node_208 | 0.4 | n |  | TRUE
126 | bus_LV_563-13_0_3_node_209 | 0.4 | n |  | TRUE
127 | bus_LV_563-13_0_3_node_211 | 0.4 | n |  | TRUE
128 | bus_LV_563-13_0_3_node_212 | 0.4 | n |  | TRUE
129 | bus_LV_563-13_0_3_node_214 | 0.4 | n |  | TRUE
130 | bus_LV_563-13_0_3_node_215 | 0.4 | n |  | TRUE
131 | bus_LV_563-13_0_3_node_218 | 0.4 | n |  | TRUE
132 | bus_LV_563-13_0_3_node_219 | 0.4 | n |  | TRUE
133 | bus_LV_563-13_0_3_node_220 | 0.4 | n |  | TRUE
134 | bus_LV_563-13_0_3_node_221 | 0.4 | n |  | TRUE
135 | bus_LV_563-13_0_3_node_222 | 0.4 | n |  | TRUE
136 | bus_LV_563-13_0_3_node_223 | 0.4 | n |  | TRUE
137 | bus_LV_563-13_0_3_node_247 | 0.4 | n |  | TRUE
138 | bus_LV_563-13_0_3_node_248 | 0.4 | n |  | TRUE
139 | bus_LV_563-13_0_3_node_250 | 0.4 | n |  | TRUE
140 | bus_LV_563-13_0_3_node_251 | 0.4 | n |  | TRUE
141 | bus_LV_563-13_0_3_node_266 | 0.4 | n |  | TRUE
142 | bus_LV_563-13_0_3_node_270 | 0.4 | n |  | TRUE
143 | bus_LV_563-13_0_3_node_267 | 0.4 | n |  | TRUE
144 | bus_LV_563-13_0_3_node_271 | 0.4 | n |  | TRUE
145 | bus_LV_563-13_0_3_node_268 | 0.4 | n |  | TRUE
146 | bus_MV_80_1_node_215 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_563-13_0_3_load_0 | 0 | 5.8729e-05 | 1.4719e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_563-13_0_3_load_8 | 2 | 4.9046e-05 | 1.2292e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_563-13_0_3_load_13 | 3 | 0.00010308 | 2.5834e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_563-13_0_3_load_2 | 6 | 0.00034944 | 8.7578e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_563-13_0_3_load_6 | 9 | 0.00057422 | 0.00014391 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_563-13_0_3_load_22 | 10 | 0.00018424 | 4.6174e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_563-13_0_3_load_21 | 11 | 0.00019251 | 4.8247e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_563-13_0_3_load_30 | 12 | 0.00031054 | 7.7828e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_563-13_0_3_load_28 | 13 | 0.001684 | 0.00042204 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_563-13_0_3_load_16 | 15 | 5.9519e-05 | 1.4917e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_563-13_0_3_load_14 | 16 | 0.00016979 | 4.2552e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_563-13_0_3_load_27 | 17 | 0.00061779 | 0.00015483 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_563-13_0_3_load_202 | 18 | 0.001011 | 0.00025338 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_563-13_0_3_load_200 | 19 | 0.00025553 | 6.4042e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_563-13_0_3_load_15 | 20 | 0.00011818 | 2.9619e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_563-13_0_3_load_10 | 21 | 0.00048752 | 0.00012218 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_563-13_0_3_load_26 | 25 | 0.00036558 | 9.1622e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_563-13_0_3_load_25 | 26 | 0.00048188 | 0.00012077 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_563-13_0_3_load_18 | 28 | 0.0009186 | 0.00023022 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_563-13_0_3_load_19 | 29 | 0.0001814 | 4.5462e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_563-13_0_3_load_274 | 30 | 0.00032664 | 8.1864e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_563-13_0_3_load_217 | 31 | 0.00096595 | 0.00024209 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_563-13_0_3_load_20 | 32 | 0.00055063 | 0.000138 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_563-13_0_3_load_104 | 35 | 0.00033465 | 8.3871e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_563-13_0_3_load_105 | 36 | 0.00029347 | 7.3551e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_563-13_0_3_load_24 | 38 | 0.0004471 | 0.00011205 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_563-13_0_3_load_29 | 39 | 0.0007253 | 0.00018178 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_563-13_0_3_load_272 | 40 | 0.00038323 | 9.6047e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_563-13_0_3_load_199 | 41 | 0.00059868 | 0.00015004 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_563-13_0_3_load_32 | 42 | 0.001078 | 0.00027018 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_563-13_0_3_load_33 | 43 | 0.0021805 | 0.00054648 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_563-13_0_3_load_37 | 47 | 0.00086376 | 0.00021648 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_563-13_0_3_load_40 | 49 | 0.00064598 | 0.0001619 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_563-13_0_3_load_41 | 50 | 0.00032162 | 8.0605e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_563-13_0_3_load_43 | 52 | 0.00059133 | 0.0001482 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_563-13_0_3_load_193 | 53 | 0.00093839 | 0.00023518 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_563-13_0_3_load_201 | 54 | 0.00054858 | 0.00013749 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_563-13_0_3_load_183 | 55 | 0.00040436 | 0.00010134 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_563-13_0_3_load_195 | 56 | 0.0002511 | 6.2932e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_563-13_0_3_load_158 | 57 | 0.00092531 | 0.0002319 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_563-13_0_3_load_157 | 58 | 0.0012749 | 0.00031952 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_563-13_0_3_load_149 | 60 | 0.0016433 | 0.00041186 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_563-13_0_3_load_107 | 61 | 0.00018009 | 4.5134e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_563-13_0_3_load_110 | 64 | 0.00025649 | 6.4284e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_563-13_0_3_load_112 | 65 | 0.00076407 | 0.00019149 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_563-13_0_3_load_116 | 66 | 0.00065453 | 0.00016404 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_563-13_0_3_load_127 | 67 | 0.00017554 | 4.3995e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_563-13_0_3_load_115 | 69 | 0.00044526 | 0.00011159 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_563-13_0_3_load_137 | 71 | 0.00018553 | 4.6497e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_563-13_0_3_load_128 | 73 | 0.00067353 | 0.0001688 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_563-13_0_3_load_113 | 75 | 0.00020634 | 5.1714e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_563-13_0_3_load_141 | 77 | 0.0012368 | 0.00030997 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_563-13_0_3_load_119 | 78 | 0.00050107 | 0.00012558 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_563-13_0_3_load_264 | 80 | 0.00075085 | 0.00018818 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_563-13_0_3_load_124 | 83 | 0.00047933 | 0.00012013 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_563-13_0_3_load_126 | 84 | 0.00080394 | 0.00020149 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_563-13_0_3_load_273 | 86 | 0.00037053 | 9.2863e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_563-13_0_3_load_122 | 87 | 0.00059075 | 0.00014805 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_563-13_0_3_load_265 | 88 | 0.0005435 | 0.00013621 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_563-13_0_3_load_130 | 89 | 0.00044535 | 0.00011161 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_563-13_0_3_load_135 | 91 | 0.00049505 | 0.00012407 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_563-13_0_3_load_131 | 92 | 0.00038501 | 9.6493e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_563-13_0_3_load_132 | 93 | 0.00021634 | 5.422e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_563-13_0_3_load_134 | 94 | 0.00022194 | 5.5623e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_563-13_0_3_load_136 | 95 | 0.00017705 | 4.4373e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_563-13_0_3_load_246 | 96 | 0.00070793 | 0.00017742 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_563-13_0_3_load_249 | 97 | 0.00027131 | 6.7998e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_563-13_0_3_load_142 | 99 | 0.0010486 | 0.00026279 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_563-13_0_3_load_143 | 100 | 0.0005111 | 0.00012809 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_563-13_0_3_load_144 | 101 | 0.00050636 | 0.00012691 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_563-13_0_3_load_145 | 102 | 0.0008651 | 0.00021682 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_563-13_0_3_load_146 | 103 | 0.00050973 | 0.00012775 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_563-13_0_3_load_147 | 104 | 0.00050404 | 0.00012633 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_563-13_0_3_load_148 | 105 | 0.00066909 | 0.00016769 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_563-13_0_3_load_242 | 106 | 0.0005117 | 0.00012824 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_563-13_0_3_load_154 | 107 | 0.00067136 | 0.00016826 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_563-13_0_3_load_243 | 108 | 0.00050995 | 0.00012781 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_563-13_0_3_load_152 | 109 | 0.00066215 | 0.00016595 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_563-13_0_3_load_150 | 110 | 0.00075067 | 0.00018814 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_563-13_0_3_load_159 | 111 | 0.0007474 | 0.00018732 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_563-13_0_3_load_160 | 112 | 0.0014954 | 0.00037479 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_563-13_0_3_load_162 | 113 | 0.0006681 | 0.00016744 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_563-13_0_3_load_169 | 114 | 0.0015311 | 0.00038373 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_563-13_0_3_load_170 | 115 | 0.00051173 | 0.00012825 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_563-13_0_3_load_210 | 117 | 0.0021773 | 0.00054568 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_563-13_0_3_load_205 | 118 | 0.00049455 | 0.00012395 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_563-13_0_3_load_194 | 119 | 0.00028143 | 7.0532e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_563-13_0_3_load_196 | 120 | 0.00023349 | 5.8517e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_563-13_0_3_load_197 | 121 | 0.00024736 | 6.1994e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_563-13_0_3_load_198 | 122 | 0.00040309 | 0.00010102 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_563-13_0_3_load_204 | 123 | 0.0016596 | 0.00041594 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_563-13_0_3_load_211 | 127 | 0.0047816 | 0.0011984 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_563-13_0_3_load_212 | 128 | 0.00049468 | 0.00012398 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_563-13_0_3_load_215 | 130 | 0.00025702 | 6.4417e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_563-13_0_3_load_218 | 131 | 0.00090628 | 0.00022714 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_563-13_0_3_load_219 | 132 | 0.0010012 | 0.00025093 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_563-13_0_3_load_220 | 133 | 0.0006676 | 0.00016732 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_563-13_0_3_load_221 | 134 | 0.00066618 | 0.00016696 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_563-13_0_3_load_222 | 135 | 0.0010428 | 0.00026135 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_563-13_0_3_load_223 | 136 | 0.00050136 | 0.00012565 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_563-13_0_3_load_247 | 137 | 0.0043088 | 0.0010799 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_563-13_0_3_load_248 | 138 | 0.0015067 | 0.00037762 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_563-13_0_3_load_250 | 139 | 0.0017806 | 0.00044625 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_563-13_0_3_load_251 | 140 | 0.0034566 | 0.00086631 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_563-13_0_3_load_266 | 141 | 0.00071074 | 0.00017813 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_563-13_0_3_load_270 | 142 | 0.0015122 | 0.000379 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_563-13_0_3_load_267 | 143 | 0.0010342 | 0.00025919 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_563-13_0_3_load_271 | 144 | 0.0010951 | 0.00027446 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_563-13_0_3_load_268 | 145 | 0.00032429 | 8.1276e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_563-13_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_563-13_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.080193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_563-13_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.054428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_563-13_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.085432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_563-13_0_3_line_4 | NAYY 4x150 SE | 2 | 21 | 0.0072991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_563-13_0_3_line_5 | NAYY 4x150 SE | 3 | 23 | 0.064977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_563-13_0_3_line_6 | NAYY 4x150 SE | 4 | 5 | 0.036955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_563-13_0_3_line_7 | NAYY 4x150 SE | 5 | 15 | 0.12701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_563-13_0_3_line_8 | NAYY 4x150 SE | 5 | 16 | 0.021857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_563-13_0_3_line_9 | NAYY 4x150 SE | 6 | 7 | 0.065589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_563-13_0_3_line_10 | NAYY 4x150 SE | 7 | 8 | 0.012122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_563-13_0_3_line_11 | NAYY 4x150 SE | 7 | 9 | 0.053488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_563-13_0_3_line_12 | NAYY 4x150 SE | 8 | 12 | 0.011321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_563-13_0_3_line_13 | NAYY 4x150 SE | 8 | 13 | 0.044451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_563-13_0_3_line_14 | NAYY 4x150 SE | 9 | 14 | 0.018477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_563-13_0_3_line_15 | NAYY 4x150 SE | 10 | 11 | 0.0058251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_563-13_0_3_line_16 | NAYY 4x150 SE | 11 | 37 | 0.031259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_563-13_0_3_line_17 | NAYY 4x150 SE | 13 | 17 | 0.068143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_563-13_0_3_line_18 | NAYY 4x150 SE | 14 | 18 | 0.02677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_563-13_0_3_line_19 | NAYY 4x150 SE | 14 | 19 | 0.097274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_563-13_0_3_line_20 | NAYY 4x150 SE | 16 | 20 | 0.02923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_563-13_0_3_line_21 | NAYY 4x150 SE | 17 | 39 | 0.063207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_563-13_0_3_line_22 | NAYY 4x150 SE | 19 | 41 | 0.0010457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_563-13_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.017792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_563-13_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.10615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_563-13_0_3_line_25 | NAYY 4x150 SE | 24 | 25 | 0.11916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_563-13_0_3_line_26 | NAYY 4x150 SE | 25 | 26 | 0.030766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_563-13_0_3_line_27 | NAYY 4x150 SE | 26 | 30 | 0.12591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_563-13_0_3_line_28 | NAYY 4x150 SE | 26 | 37 | 0.26043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_563-13_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.17175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_563-13_0_3_line_30 | NAYY 4x150 SE | 27 | 29 | 0.062393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_563-13_0_3_line_31 | NAYY 4x150 SE | 27 | 30 | 0.12092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_563-13_0_3_line_32 | NAYY 4x150 SE | 27 | 31 | 0.091489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_563-13_0_3_line_33 | NAYY 4x150 SE | 28 | 32 | 0.029441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_563-13_0_3_line_34 | NAYY 4x150 SE | 31 | 33 | 0.062113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_563-13_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.028733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_563-13_0_3_line_36 | NAYY 4x150 SE | 33 | 86 | 0.078926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_563-13_0_3_line_37 | NAYY 4x150 SE | 33 | 129 | 0.010773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_563-13_0_3_line_38 | NAYY 4x150 SE | 34 | 35 | 0.0036482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_563-13_0_3_line_39 | NAYY 4x150 SE | 34 | 36 | 0.021503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_563-13_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.018394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_563-13_0_3_line_41 | NAYY 4x150 SE | 39 | 40 | 0.085631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_563-13_0_3_line_42 | NAYY 4x150 SE | 40 | 145 | 0.021672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_563-13_0_3_line_43 | NAYY 4x150 SE | 41 | 122 | 0.023568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_563-13_0_3_line_44 | NAYY 4x150 SE | 42 | 43 | 0.08019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_563-13_0_3_line_45 | NAYY 4x150 SE | 42 | 44 | 0.0269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_563-13_0_3_line_46 | NAYY 4x150 SE | 43 | 45 | 0.080962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_563-13_0_3_line_47 | NAYY 4x150 SE | 44 | 46 | 0.004244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_563-13_0_3_line_48 | NAYY 4x150 SE | 44 | 47 | 0.064345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_563-13_0_3_line_49 | NAYY 4x150 SE | 45 | 48 | 0.022401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_563-13_0_3_line_50 | NAYY 4x150 SE | 46 | 49 | 0.046745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_563-13_0_3_line_51 | NAYY 4x150 SE | 46 | 50 | 0.16911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_563-13_0_3_line_52 | NAYY 4x150 SE | 48 | 51 | 0.075367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_563-13_0_3_line_53 | NAYY 4x150 SE | 48 | 52 | 0.0092166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_563-13_0_3_line_54 | NAYY 4x150 SE | 49 | 53 | 0.023029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_563-13_0_3_line_55 | NAYY 4x150 SE | 51 | 54 | 0.18905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_563-13_0_3_line_56 | NAYY 4x150 SE | 52 | 55 | 0.015945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_563-13_0_3_line_57 | NAYY 4x150 SE | 53 | 56 | 0.018763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_563-13_0_3_line_58 | NAYY 4x150 SE | 56 | 119 | 0.028986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_563-13_0_3_line_59 | NAYY 4x150 SE | 57 | 58 | 0.032431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_563-13_0_3_line_60 | NAYY 4x150 SE | 57 | 59 | 0.073344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_563-13_0_3_line_61 | NAYY 4x150 SE | 58 | 111 | 0.04806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_563-13_0_3_line_62 | NAYY 4x150 SE | 59 | 60 | 0.070995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_563-13_0_3_line_63 | NAYY 4x150 SE | 60 | 110 | 0.053205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_563-13_0_3_line_64 | NAYY 4x150 SE | 61 | 62 | 0.0045266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_563-13_0_3_line_65 | NAYY 4x150 SE | 61 | 63 | 0.039998 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_563-13_0_3_line_66 | NAYY 4x150 SE | 62 | 64 | 0.026232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_563-13_0_3_line_67 | NAYY 4x150 SE | 63 | 65 | 0.050609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_563-13_0_3_line_68 | NAYY 4x150 SE | 63 | 66 | 0.0845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_563-13_0_3_line_69 | NAYY 4x150 SE | 64 | 67 | 0.12849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_563-13_0_3_line_70 | NAYY 4x150 SE | 66 | 71 | 0.20155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_563-13_0_3_line_71 | NAYY 4x150 SE | 66 | 68 | 0.07428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_563-13_0_3_line_72 | NAYY 4x150 SE | 67 | 73 | 0.015545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_563-13_0_3_line_73 | NAYY 4x150 SE | 68 | 69 | 0.041795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_563-13_0_3_line_74 | NAYY 4x150 SE | 69 | 70 | 0.1664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_563-13_0_3_line_75 | NAYY 4x150 SE | 70 | 82 | 0.018967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_563-13_0_3_line_76 | NAYY 4x150 SE | 70 | 83 | 0.011278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_563-13_0_3_line_77 | NAYY 4x150 SE | 70 | 79 | 0.10907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_563-13_0_3_line_78 | NAYY 4x150 SE | 71 | 72 | 0.076003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_563-13_0_3_line_79 | NAYY 4x150 SE | 72 | 77 | 0.047536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_563-13_0_3_line_80 | NAYY 4x150 SE | 73 | 74 | 0.067529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_563-13_0_3_line_81 | NAYY 4x150 SE | 74 | 89 | 0.018291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_563-13_0_3_line_82 | NAYY 4x150 SE | 74 | 90 | 0.1198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_563-13_0_3_line_83 | NAYY 4x150 SE | 75 | 76 | 0.0088312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_563-13_0_3_line_84 | NAYY 4x150 SE | 76 | 78 | 0.012181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_563-13_0_3_line_85 | NAYY 4x150 SE | 76 | 79 | 0.14514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_563-13_0_3_line_86 | NAYY 4x150 SE | 79 | 85 | 0.098836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_563-13_0_3_line_87 | NAYY 4x150 SE | 80 | 81 | 0.10329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_563-13_0_3_line_88 | NAYY 4x150 SE | 81 | 82 | 0.049485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_563-13_0_3_line_89 | NAYY 4x150 SE | 82 | 84 | 0.033081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_563-13_0_3_line_90 | NAYY 4x150 SE | 84 | 88 | 0.031034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_563-13_0_3_line_91 | NAYY 4x150 SE | 85 | 86 | 0.070568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_563-13_0_3_line_92 | NAYY 4x150 SE | 87 | 88 | 0.10627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_563-13_0_3_line_93 | NAYY 4x150 SE | 90 | 91 | 0.014859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_563-13_0_3_line_94 | NAYY 4x150 SE | 90 | 92 | 0.088563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_563-13_0_3_line_95 | NAYY 4x150 SE | 92 | 93 | 0.1213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_563-13_0_3_line_96 | NAYY 4x150 SE | 93 | 94 | 0.017942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_563-13_0_3_line_97 | NAYY 4x150 SE | 94 | 95 | 0.015599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_563-13_0_3_line_98 | NAYY 4x150 SE | 95 | 96 | 0.014804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_563-13_0_3_line_99 | NAYY 4x150 SE | 96 | 97 | 0.018573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_563-13_0_3_line_100 | NAYY 4x150 SE | 96 | 98 | 0.085301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_563-13_0_3_line_101 | NAYY 4x150 SE | 97 | 141 | 0.011664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_563-13_0_3_line_102 | NAYY 4x150 SE | 98 | 137 | 0.022316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_563-13_0_3_line_103 | NAYY 4x150 SE | 98 | 138 | 0.011116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_563-13_0_3_line_104 | NAYY 4x150 SE | 98 | 135 | 0.10769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_563-13_0_3_line_105 | NAYY 4x150 SE | 99 | 100 | 0.014695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_563-13_0_3_line_106 | NAYY 4x150 SE | 99 | 101 | 0.00023502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_563-13_0_3_line_107 | NAYY 4x150 SE | 100 | 102 | 0.0028088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_563-13_0_3_line_108 | NAYY 4x150 SE | 101 | 103 | 0.0073348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_563-13_0_3_line_109 | NAYY 4x150 SE | 102 | 104 | 0.012765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_563-13_0_3_line_110 | NAYY 4x150 SE | 103 | 105 | 0.0030251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_563-13_0_3_line_111 | NAYY 4x150 SE | 104 | 106 | 0.007208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_563-13_0_3_line_112 | NAYY 4x150 SE | 105 | 107 | 0.007927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_563-13_0_3_line_113 | NAYY 4x150 SE | 106 | 108 | 0.0031124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_563-13_0_3_line_114 | NAYY 4x150 SE | 107 | 109 | 0.0044387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_563-13_0_3_line_115 | NAYY 4x150 SE | 108 | 136 | 0.0040845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_563-13_0_3_line_116 | NAYY 4x150 SE | 109 | 110 | 0.0081875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_563-13_0_3_line_117 | NAYY 4x150 SE | 111 | 112 | 0.0073443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_563-13_0_3_line_118 | NAYY 4x150 SE | 112 | 113 | 0.022306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_563-13_0_3_line_119 | NAYY 4x150 SE | 113 | 114 | 0.042125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_563-13_0_3_line_120 | NAYY 4x150 SE | 114 | 115 | 0.0023797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_563-13_0_3_line_121 | NAYY 4x150 SE | 115 | 116 | 0.066351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_563-13_0_3_line_122 | NAYY 4x150 SE | 116 | 117 | 0.022607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_563-13_0_3_line_123 | NAYY 4x150 SE | 116 | 118 | 0.03113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_563-13_0_3_line_124 | NAYY 4x150 SE | 118 | 123 | 0.10789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_563-13_0_3_line_125 | NAYY 4x150 SE | 119 | 120 | 0.017565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_563-13_0_3_line_126 | NAYY 4x150 SE | 120 | 121 | 0.021264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_563-13_0_3_line_127 | NAYY 4x150 SE | 121 | 122 | 0.0053182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_563-13_0_3_line_128 | NAYY 4x150 SE | 123 | 124 | 0.065383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_563-13_0_3_line_129 | NAYY 4x150 SE | 124 | 125 | 0.05009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_563-13_0_3_line_130 | NAYY 4x150 SE | 125 | 126 | 0.055419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_563-13_0_3_line_131 | NAYY 4x150 SE | 125 | 127 | 0.017856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_563-13_0_3_line_132 | NAYY 4x150 SE | 126 | 128 | 0.13236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_563-13_0_3_line_133 | NAYY 4x150 SE | 129 | 130 | 0.096867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_563-13_0_3_line_134 | NAYY 4x150 SE | 131 | 132 | 0.0056298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_563-13_0_3_line_135 | NAYY 4x150 SE | 131 | 133 | 0.0049323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_563-13_0_3_line_136 | NAYY 4x150 SE | 132 | 134 | 0.0077625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_563-13_0_3_line_137 | NAYY 4x150 SE | 133 | 135 | 0.00014584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_563-13_0_3_line_138 | NAYY 4x150 SE | 134 | 136 | 0.016705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_563-13_0_3_line_139 | NAYY 4x150 SE | 137 | 139 | 0.018153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_563-13_0_3_line_140 | NAYY 4x150 SE | 138 | 140 | 0.035462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_563-13_0_3_line_141 | NAYY 4x150 SE | 139 | 142 | 0.009079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_563-13_0_3_line_142 | NAYY 4x150 SE | 141 | 143 | 0.0022141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_563-13_0_3_line_143 | NAYY 4x150 SE | 142 | 144 | 0.0084572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_563-13_0_3_line_144 | NAYY 4x150 SE | 143 | 145 | 0.010441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_563-13_0_3_trafo_246 | 0.25 MVA 20/0.4 kV | 146 | 96 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2614365.0051 | 1157802.7455 | 2614373.7026 | 1157811.9336
1 | 2614373.7026 | 1157811.9336 | 2614453.6381 | 1157818.3535
2 | 2614373.7026 | 1157811.9336 | 2614417.4225 | 1157779.5144
3 | 2614365.0051 | 1157802.7455 | 2614355.0838 | 1157803.1333 | 2614346.6035 | 1157803.6245 | 2614334.3635 | 1157805.4408 | 2614296.5587 | 1157812.577 | 2614288.7452 | 1157813.1254 | 2614280.1746 | 1157812.9495
4 | 2614457.9325 | 1157824.2555 | 2614453.6381 | 1157818.3535
5 | 2614425.9165 | 1157715.4919 | 2614426.4333 | 1157736.648 | 2614417.4225 | 1157779.5144
6 | 2614245.8974 | 1157819.6497 | 2614260.638 | 1157810.7357 | 2614270.0863 | 1157812.6256 | 2614280.1746 | 1157812.9495
7 | 2614245.8974 | 1157819.6497 | 2614253.8601 | 1157827.3056 | 2614275.1783 | 1157831.4691 | 2614292.6342 | 1157834.9565 | 2614312.0896 | 1157835.7585 | 2614315.6812 | 1157837.4234 | 2614354.2001 | 1157873.8404
8 | 2614245.8974 | 1157819.6497 | 2614242.9878 | 1157821.366 | 2614225.0197 | 1157825.681
9 | 2614844.5432 | 1158444.9223 | 2614837.9032 | 1158420.594 | 2614834.6422 | 1158412.4819 | 2614831.1316 | 1158406.1257 | 2614826.4318 | 1158400.2002 | 2614820.3127 | 1158394.7046 | 2614813.4233 | 1158389.5921
10 | 2614833.1417 | 1158449.1297 | 2614844.5432 | 1158444.9223
11 | 2614844.5432 | 1158444.9223 | 2614849.7467 | 1158464.2447 | 2614854.3994 | 1158479.9306 | 2614857.4772 | 1158487.7086 | 2614861.1838 | 1158495.3993 | 2614861.284 | 1158495.5881
12 | 2614833.4597 | 1158438.2474 | 2614831.7424 | 1158444.5796 | 2614833.1417 | 1158449.1297
13 | 2614833.1417 | 1158449.1297 | 2614831.339 | 1158452.7827 | 2614831.0521 | 1158457.2509 | 2614832.5136 | 1158486.4133 | 2614831.8403 | 1158493.0801
14 | 2614869.9509 | 1158511.9069 | 2614861.284 | 1158495.5881
15 | 2614779.0018 | 1158092.1422 | 2614782.743 | 1158096.6071
16 | 2614752.1845 | 1158078.9594 | 2614763.9257 | 1158080.2887 | 2614774.1299 | 1158086.3278 | 2614779.0018 | 1158092.1422
17 | 2614824.2857 | 1158555.3958 | 2614831.4478 | 1158552.0543 | 2614833.3999 | 1158546.8788 | 2614835.6824 | 1158538.269 | 2614836.1163 | 1158526.9978 | 2614831.8424 | 1158509.9789 | 2614831.0444 | 1158500.9614 | 2614831.8403 | 1158493.0801
18 | 2614895.5964 | 1158503.9883 | 2614869.9509 | 1158511.9069
19 | 2614869.9509 | 1158511.9069 | 2614881.9896 | 1158535.2592 | 2614884.7266 | 1158541.3023 | 2614887.2179 | 1158547.5115 | 2614889.4558 | 1158553.8979 | 2614891.4253 | 1158560.3504 | 2614892.9276 | 1158566.6239 | 2614894.1998 | 1158572.9413 | 2614895.9925 | 1158585.8076 | 2614898.4318 | 1158603.9221
20 | 2614196.5975 | 1157832.5065 | 2614225.0197 | 1157825.681
21 | 2614818.2245 | 1158614.6751 | 2614816.6996 | 1158564.4576 | 2614817.3239 | 1158559.9569 | 2614820.2126 | 1158557.296 | 2614824.2857 | 1158555.3958
22 | 2614898.4318 | 1158603.9221 | 2614898.5714 | 1158604.9584
23 | 2614443.7413 | 1157715.5011 | 2614434.5117 | 1157715.0789 | 2614425.9165 | 1157715.4919
24 | 2614443.7413 | 1157715.5011 | 2614449.658 | 1157716.3046 | 2614450.4698 | 1157716.6511 | 2614455.0581 | 1157718.3185 | 2614485.6263 | 1157746.4167 | 2614511.379 | 1157749.2576 | 2614533.3673 | 1157764.9071
25 | 2614533.3673 | 1157764.9071 | 2614539.7628 | 1157773.8047 | 2614543.1377 | 1157779.5045 | 2614544.4533 | 1157787.1337 | 2614543.1912 | 1157801.849 | 2614539.5726 | 1157827.3529 | 2614539.1217 | 1157836.2896 | 2614539.9776 | 1157843.8065 | 2614542.5974 | 1157851.0719 | 2614546.8802 | 1157858.5304 | 2614553.7009 | 1157869.0965 | 2614555.8438 | 1157873.7928 | 2614556.0902 | 1157876.517
26 | 2614560.6082 | 1157902.541 | 2614551.9575 | 1157892.6817 | 2614551.1222 | 1157889.3336 | 2614551.5603 | 1157885.7107 | 2614555.6446 | 1157880.0955 | 2614556.0902 | 1157876.517
27 | 2614471.133 | 1157991.1252 | 2614560.6082 | 1157902.541
28 | 2614560.6082 | 1157902.541 | 2614752.1845 | 1158078.9594
29 | 2614357.1248 | 1158031.4066 | 2614360.9351 | 1158034.5617 | 2614363.3178 | 1158038.4137 | 2614371.6324 | 1158052.6182 | 2614391.1477 | 1158082.7018 | 2614394.4237 | 1158088.09 | 2614396.4587 | 1158093.0307 | 2614397.7725 | 1158098.2697 | 2614398.6608 | 1158101.8625 | 2614399.8341 | 1158104.9335 | 2614403.162 | 1158111.0111 | 2614409.9163 | 1158123.6668 | 2614413.4213 | 1158129.4335 | 2614416.935 | 1158134.7446 | 2614426.7684 | 1158148.4748 | 2614437.2464 | 1158161.9065 | 2614448.9209 | 1158175.085
30 | 2614319.4052 | 1157983.7602 | 2614326.5024 | 1157997.4393 | 2614337.8943 | 1158016.8315 | 2614342.3275 | 1158022.4003 | 2614347.9589 | 1158026.9715 | 2614357.1248 | 1158031.4066
31 | 2614357.1248 | 1158031.4066 | 2614471.133 | 1157991.1252
32 | 2614357.1248 | 1158031.4066 | 2614302.9574 | 1158105.1369
33 | 2614448.9209 | 1158175.085 | 2614458.7604 | 1158186.1922 | 2614468.1536 | 1158197.3719
34 | 2614256.0449 | 1158070.998 | 2614256.7909 | 1158079.7374 | 2614262.4975 | 1158084.9535 | 2614270.5387 | 1158091.6647 | 2614279.536 | 1158096.0548 | 2614295.9752 | 1158101.2184 | 2614302.9574 | 1158105.1369
35 | 2614487.5761 | 1158218.4327 | 2614481.9748 | 1158210.9934 | 2614470.0661 | 1158199.6481 | 2614468.1536 | 1158197.3719
36 | 2614209.2012 | 1158134.5191 | 2614256.0449 | 1158070.998
37 | 2614266.0704 | 1158075.0125 | 2614256.0449 | 1158070.998
38 | 2614487.5761 | 1158218.4327 | 2614484.3445 | 1158216.7397
39 | 2614487.5761 | 1158218.4327 | 2614494.1108 | 1158223.4397 | 2614498.6142 | 1158231.5657 | 2614499.6913 | 1158235.3975
40 | 2614752.1845 | 1158078.9594 | 2614755.5632 | 1158089.2172 | 2614755.9586 | 1158096.7997
41 | 2614744.9956 | 1158659.0624 | 2614818.2245 | 1158614.6751
42 | 2614744.9956 | 1158659.0624 | 2614750.2156 | 1158680.0967
43 | 2614901.7168 | 1158628.3155 | 2614898.5714 | 1158604.9584
44 | 2614962.7545 | 1158810.4457 | 2614965.1683 | 1158816.7263 | 2614967.5951 | 1158824.1471 | 2614969.4243 | 1158831.433 | 2614970.3347 | 1158838.3165 | 2614970.4635 | 1158845.109 | 2614969.1947 | 1158852.9209 | 2614967.0147 | 1158860.3747 | 2614964.2991 | 1158867.4382 | 2614956.3913 | 1158884.9606 | 2614955.6634 | 1158886.7512
45 | 2614953.1044 | 1158785.3364 | 2614962.7545 | 1158810.4457
46 | 2614959.8294 | 1158963.7304 | 2614954.3719 | 1158954.4345 | 2614950.2037 | 1158944.5304 | 2614947.8449 | 1158934.4084 | 2614946.8216 | 1158923.6005 | 2614947.1688 | 1158916.4756 | 2614948.1368 | 1158909.4078 | 2614949.7942 | 1158902.5196 | 2614952.0031 | 1158895.7551 | 2614955.6634 | 1158886.7512
47 | 2614953.1044 | 1158785.3364 | 2614951.4967 | 1158781.4083
48 | 2614953.1044 | 1158785.3364 | 2614946.5568 | 1158789.0221 | 2614944.1992 | 1158793.8964 | 2614945.0297 | 1158799.0343 | 2614949.617 | 1158806.8718 | 2614955.1925 | 1158815.0007 | 2614958.085 | 1158829.3706 | 2614958.3869 | 1158841.9829
49 | 2614959.8294 | 1158963.7304 | 2614966.7365 | 1158972.5963 | 2614974.6579 | 1158980.4976
50 | 2614951.4967 | 1158781.4083 | 2614933.8916 | 1158738.105
51 | 2614951.4967 | 1158781.4083 | 2614961.5457 | 1158775.2634 | 2614994.6344 | 1158757.57 | 2615009.1635 | 1158746.9342 | 2615023.9474 | 1158729.44 | 2615033.5036 | 1158711.9218 | 2615042.1005 | 1158697.9585 | 2615043.5652 | 1158682.3211 | 2615038.8428 | 1158667.1462 | 2615033.293 | 1158657.71
52 | 2614974.6579 | 1158980.4976 | 2614988.5791 | 1158964.3797 | 2615000.4267 | 1158953.0368 | 2615013.5537 | 1158941.9751 | 2615020.0952 | 1158937.578 | 2615032.0026 | 1158933.0499
53 | 2614974.6579 | 1158980.4976 | 2614981.4591 | 1158985.706 | 2614982.0194 | 1158986.0358
54 | 2614933.8916 | 1158738.105 | 2614932.2514 | 1158734.0706 | 2614925.2305 | 1158716.7672
55 | 2615032.0026 | 1158933.0499 | 2615104.0317 | 1158911.2632 | 2615118.0076 | 1158907.185 | 2615129.6937 | 1158899.2548 | 2615133.4005 | 1158888.2586 | 2615127.3907 | 1158839.4416 | 2615137.6484 | 1158817.3801
56 | 2614996.0335 | 1158993.5868 | 2614991.5085 | 1158991.6227 | 2614982.0194 | 1158986.0358
57 | 2614918.3236 | 1158699.3226 | 2614921.7221 | 1158708.1206 | 2614925.2305 | 1158716.7672
58 | 2614909.4533 | 1158671.7533 | 2614909.8119 | 1158673.3073 | 2614912.4489 | 1158682.5628 | 2614915.408 | 1158691.7747 | 2614918.3236 | 1158699.3226
59 | 2614725.983 | 1159081.3266 | 2614731.5274 | 1159089.5651 | 2614748.4279 | 1159104.4194
60 | 2614821.6416 | 1159108.7839 | 2614748.4279 | 1159104.4194
61 | 2614696.5588 | 1159043.4689 | 2614704.0119 | 1159054.4473 | 2614719.5524 | 1159071.7715 | 2614725.983 | 1159081.3266
62 | 2614821.6416 | 1159108.7839 | 2614817.6729 | 1159101.8485 | 2614824.1039 | 1159064.3012 | 2614822.2795 | 1159045.6208 | 2614819.7192 | 1159040.0394
63 | 2614797.5353 | 1158991.6801 | 2614819.7192 | 1159040.0394
64 | 2614394.4472 | 1158457.7953 | 2614394.2972 | 1158462.3194
65 | 2614399.5935 | 1158501.7071 | 2614395.7712 | 1158487.6466 | 2614394.0012 | 1158471.2453 | 2614394.2972 | 1158462.3194
66 | 2614394.4472 | 1158457.7953 | 2614402.4214 | 1158473.0663 | 2614408.369 | 1158479.8505
67 | 2614399.5935 | 1158501.7071 | 2614405.0083 | 1158506.8892 | 2614409.1017 | 1158516.5371 | 2614413.801 | 1158529.2546 | 2614415.8714 | 1158538.6197 | 2614418.6927 | 1158544.8406 | 2614420.3506 | 1158546.9126
68 | 2614399.5935 | 1158501.7071 | 2614315.1281 | 1158499.2688
69 | 2614408.369 | 1158479.8505 | 2614526.9944 | 1158430.4657
70 | 2614315.1281 | 1158499.2688 | 2614158.5248 | 1158626.1402
71 | 2614294.0557 | 1158429.6542 | 2614292.9574 | 1158437.0553 | 2614298.238 | 1158447.2061 | 2614306.0523 | 1158462.1098 | 2614309.5075 | 1158479.1264 | 2614311.4928 | 1158492.1153 | 2614315.1281 | 1158499.2688
72 | 2614526.9944 | 1158430.4657 | 2614529.3715 | 1158434.8402 | 2614534.3218 | 1158444.1748
73 | 2614294.0557 | 1158429.6542 | 2614289.2009 | 1158424.2289 | 2614279.8911 | 1158396.5821 | 2614276.8013 | 1158392.2235
74 | 2614175.7783 | 1158297.3879 | 2614201.3466 | 1158296.2251 | 2614219.7439 | 1158299.7813 | 2614229.8054 | 1158304.6296 | 2614238.7908 | 1158323.6935 | 2614242.762 | 1158343.068 | 2614240.9269 | 1158363.8406 | 2614248.6413 | 1158378.9552 | 2614256.6289 | 1158382.2312 | 2614272.9996 | 1158386.861 | 2614276.8013 | 1158392.2235
75 | 2614175.7783 | 1158297.3879 | 2614157.9475 | 1158303.9938
76 | 2614175.7783 | 1158297.3879 | 2614171.2926 | 1158307.7381
77 | 2614224.1806 | 1158199.6421 | 2614175.7783 | 1158297.3879
78 | 2614191.1749 | 1158693.9314 | 2614189.4053 | 1158686.9683 | 2614183.1227 | 1158679.1719 | 2614179.7775 | 1158673.9615 | 2614177.0859 | 1158664.6172 | 2614171.856 | 1158655.6894 | 2614163.9876 | 1158637.6954 | 2614160.0707 | 1158627.8369 | 2614158.5248 | 1158626.1402
79 | 2614191.1749 | 1158693.9314 | 2614197.5231 | 1158703.1731 | 2614203.2474 | 1158716.9156 | 2614214.5107 | 1158735.1845
80 | 2614570.5181 | 1158499.4824 | 2614566.4427 | 1158498.3609 | 2614563.1542 | 1158495.1847 | 2614548.0861 | 1158468.6908 | 2614542.0705 | 1158455.1585 | 2614534.324 | 1158444.1789 | 2614534.3218 | 1158444.1748
81 | 2614570.5181 | 1158499.4824 | 2614571.544 | 1158509.5454 | 2614573.9935 | 1158517.344
82 | 2614679.4521 | 1158449.6213 | 2614570.5181 | 1158499.4824
83 | 2614343.0735 | 1158266.7452 | 2614346.3504 | 1158274.946
84 | 2614343.0735 | 1158266.7452 | 2614336.8152 | 1158261.55 | 2614334.0117 | 1158258.6303
85 | 2614224.1806 | 1158199.6421 | 2614230.3868 | 1158201.0241 | 2614240.6657 | 1158204.7279 | 2614253.9763 | 1158210.162 | 2614263.0153 | 1158213.0514 | 2614272.0601 | 1158213.4841 | 2614282.5889 | 1158212.0082 | 2614289.5408 | 1158212.5027 | 2614298.417 | 1158216.1477 | 2614306.9947 | 1158222.7935 | 2614315.2349 | 1158232.7847 | 2614322.4142 | 1158240.7945 | 2614330.7835 | 1158248.0624 | 2614337.7514 | 1158257.9171 | 2614343.0735 | 1158266.7452
86 | 2614224.1806 | 1158199.6421 | 2614219.1324 | 1158194.8057 | 2614213.1872 | 1158186.7988 | 2614204.5732 | 1158175.9176 | 2614199.245 | 1158169.5464 | 2614194.1179 | 1158165.6435 | 2614188.5635 | 1158164.1964 | 2614177.6716 | 1158163.5483 | 2614163.4863 | 1158161.6697 | 2614152.7932 | 1158161.2444 | 2614148.2703 | 1158161.2339 | 2614145.3994 | 1158159.5819 | 2614144.7876 | 1158155.6896
87 | 2614123.7892 | 1158339.7761 | 2614135.3768 | 1158367.2945 | 2614142.7622 | 1158375.716 | 2614160.8182 | 1158390.7213 | 2614174.1578 | 1158399.9793 | 2614182.7922 | 1158402.045 | 2614189.7784 | 1158404.1069 | 2614195.1127 | 1158407.8102
88 | 2614157.9475 | 1158303.9938 | 2614148.0203 | 1158313.7754 | 2614131.517 | 1158332.9574 | 2614123.7892 | 1158339.7761
89 | 2614157.9475 | 1158303.9938 | 2614151.9815 | 1158301.5453 | 2614125.6871 | 1158297.3202
90 | 2614095.0458 | 1158292.3966 | 2614125.6871 | 1158297.3202
91 | 2614144.7876 | 1158155.6896 | 2614145.821 | 1158153.0241 | 2614149.9401 | 1158152.011 | 2614154.8798 | 1158150.7886 | 2614163.3115 | 1158147.9403 | 2614171.9558 | 1158145.9151 | 2614176.2751 | 1158144.4912 | 2614179.1662 | 1158140.8073 | 2614184.5181 | 1158137.1291 | 2614189.2523 | 1158135.2949 | 2614196.2442 | 1158135.1112 | 2614204.2633 | 1158134.9188 | 2614209.2012 | 1158134.5191
92 | 2614080.4264 | 1158187.1414 | 2614095.0458 | 1158292.3966
93 | 2614679.4521 | 1158449.6213 | 2614682.1399 | 1158435.0095
94 | 2614679.4521 | 1158449.6213 | 2614680.5861 | 1158462.4638 | 2614682.3322 | 1158475.7301 | 2614697.0619 | 1158518.1536 | 2614702.2413 | 1158528.6381 | 2614704.6926 | 1158533.7712
95 | 2614720.21 | 1158651.3414 | 2614718.498 | 1158614.3757 | 2614717.0027 | 1158601.9992 | 2614720.5679 | 1158585.9555 | 2614720.2075 | 1158570.2913 | 2614716.5389 | 1158559.5437 | 2614708.6935 | 1158542.1494 | 2614704.6926 | 1158533.7712
96 | 2614721.0401 | 1158669.2643 | 2614720.21 | 1158651.3414
97 | 2614721.7619 | 1158684.8468 | 2614721.0401 | 1158669.2643
98 | 2614722.6748 | 1158699.617 | 2614722.2919 | 1158696.2922 | 2614721.7619 | 1158684.8468
99 | 2614722.6748 | 1158699.617 | 2614731.5312 | 1158698.3824 | 2614740.8494 | 1158695.947
100 | 2614751.5717 | 1158778.6155 | 2614749.9314 | 1158775.4432 | 2614726.6623 | 1158730.4197 | 2614725.0021 | 1158719.6659 | 2614722.6748 | 1158699.617
101 | 2614740.8494 | 1158695.947 | 2614745.5217 | 1158694.7258 | 2614751.9052 | 1158692.2846 | 2614751.9052 | 1158692.2846
102 | 2614751.5717 | 1158778.6155 | 2614755.6081 | 1158773.6562 | 2614762.4079 | 1158770.1822 | 2614770.0004 | 1158766.8642
103 | 2614751.5717 | 1158778.6155 | 2614747.7632 | 1158787.5662 | 2614746.9782 | 1158788.7111
104 | 2614751.5717 | 1158778.6155 | 2614754.1885 | 1158783.6799 | 2614760.8868 | 1158806.0963 | 2614767.5776 | 1158834.6712 | 2614775.1324 | 1158876.6438 | 2614776.2094 | 1158883.152
105 | 2614786.8473 | 1158947.4322 | 2614789.2467 | 1158961.9303
106 | 2614789.2467 | 1158961.9303 | 2614789.285 | 1158962.1622
107 | 2614786.8473 | 1158947.4322 | 2614786.3887 | 1158944.6611
108 | 2614789.285 | 1158962.1622 | 2614790.4826 | 1158969.3986
109 | 2614786.3887 | 1158944.6611 | 2614784.3045 | 1158932.0672
110 | 2614790.9765 | 1158972.3831 | 2614790.4826 | 1158969.3986
111 | 2614784.3045 | 1158932.0672 | 2614783.1277 | 1158924.9559
112 | 2614792.2708 | 1158980.2037 | 2614792.2708 | 1158980.2037 | 2614790.9765 | 1158972.3831
113 | 2614782.6195 | 1158921.8853 | 2614783.1277 | 1158924.9559
114 | 2614792.2708 | 1158980.2037 | 2614794.1215 | 1158984.2382
115 | 2614782.6195 | 1158921.8853 | 2614781.9526 | 1158917.8556
116 | 2614794.1215 | 1158984.2382 | 2614797.5353 | 1158991.6801
117 | 2614696.5588 | 1159043.4689 | 2614692.4337 | 1159037.3927
118 | 2614682.1204 | 1159017.6552 | 2614689.9589 | 1159033.7473 | 2614692.4337 | 1159037.3927
119 | 2614682.1204 | 1159017.6552 | 2614677.4357 | 1159008.0375 | 2614671.5189 | 1158988.8914 | 2614669.2311 | 1158977.7359 | 2614669.2311 | 1158977.7359
120 | 2614667.3036 | 1158976.3403 | 2614669.2311 | 1158977.7359
121 | 2614640.6601 | 1159029.8702 | 2614654.2539 | 1158996.6311 | 2614656.976 | 1158980.4074 | 2614659.9011 | 1158975.3009 | 2614664.6555 | 1158974.4231 | 2614667.3036 | 1158976.3403
122 | 2614640.6601 | 1159029.8702 | 2614645.3266 | 1159033.5833 | 2614649.4317 | 1159038.1066 | 2614652.916 | 1159042.6173 | 2614655.1666 | 1159046.9249
123 | 2614640.6601 | 1159029.8702 | 2614633.8753 | 1159043.0714 | 2614628.8785 | 1159058.5738
124 | 2614596.3316 | 1159161.0327 | 2614598.4703 | 1159157.6092 | 2614601.5327 | 1159149.5459 | 2614603.8178 | 1159133.2545 | 2614626.1524 | 1159067.0312 | 2614628.8785 | 1159058.5738
125 | 2614909.4533 | 1158671.7533 | 2614907.6201 | 1158663.8083 | 2614905.7793 | 1158654.579
126 | 2614902.4266 | 1158633.5861 | 2614903.6178 | 1158642.4322 | 2614905.6969 | 1158654.1654 | 2614905.7793 | 1158654.579
127 | 2614902.4266 | 1158633.5861 | 2614901.7168 | 1158628.3155
128 | 2614586.6919 | 1159223.2688 | 2614590.1926 | 1159211.4269 | 2614590.3355 | 1159203.0342 | 2614587.2538 | 1159184.2286 | 2614587.3172 | 1159177.0029 | 2614591.3144 | 1159169.0642 | 2614596.3316 | 1159161.0327
129 | 2614586.6919 | 1159223.2688 | 2614564.0813 | 1159264.5458 | 2614562.4655 | 1159267.1321
130 | 2614562.4655 | 1159267.1321 | 2614557.7071 | 1159253.8696 | 2614551.5734 | 1159241.96 | 2614542.7517 | 1159232.3118 | 2614532.9061 | 1159224.4953 | 2614531.2545 | 1159222.8461
131 | 2614562.4655 | 1159267.1321 | 2614556.8215 | 1159277.8349 | 2614554.7037 | 1159283.1873
132 | 2614494.5471 | 1159102.0648 | 2614502.1381 | 1159110.4872 | 2614506.0197 | 1159118.6894 | 2614508.2547 | 1159129.5557 | 2614510.2919 | 1159139.8101 | 2614514.7964 | 1159147.2024 | 2614520.7383 | 1159156.0211 | 2614527.5004 | 1159164.8528 | 2614527.8825 | 1159174.892 | 2614528.8765 | 1159188.6234 | 2614525.9485 | 1159210.9608 | 2614527.1638 | 1159218.7454 | 2614531.2545 | 1159222.8461
133 | 2614266.0704 | 1158075.0125 | 2614260.1101 | 1158066.8389 | 2614251.7002 | 1158057.1809 | 2614239.1465 | 1158045.9569 | 2614219.6412 | 1158034.0162 | 2614211.0112 | 1158029.8938 | 2614205.4623 | 1158029.2694 | 2614199.0903 | 1158029.8658 | 2614186.5341 | 1158032.7155
134 | 2614777.0385 | 1158888.162 | 2614777.9577 | 1158893.7163
135 | 2614777.0385 | 1158888.162 | 2614776.2332 | 1158883.2959
136 | 2614777.9577 | 1158893.7163 | 2614779.2251 | 1158901.3747
137 | 2614776.2094 | 1158883.152 | 2614776.2332 | 1158883.2959
138 | 2614779.2251 | 1158901.3747 | 2614781.9526 | 1158917.8556
139 | 2614787.3723 | 1158761.9809 | 2614776.3966 | 1158764.0689 | 2614770.0004 | 1158766.8642
140 | 2614728.9756 | 1158819.0915 | 2614733.524 | 1158808.4418 | 2614740.7476 | 1158797.7985 | 2614746.9782 | 1158788.7111
141 | 2614787.3723 | 1158761.9809 | 2614790.1851 | 1158761.4458 | 2614796.283 | 1158760.241
142 | 2614751.9052 | 1158692.2846 | 2614752.7304 | 1158690.2301
143 | 2614804.5798 | 1158758.6019 | 2614796.283 | 1158760.241
144 | 2614750.2156 | 1158680.0967 | 2614752.7304 | 1158690.2301 | 2614752.7304 | 1158690.2301

## bus_geodata
| x | y | coords
0 | 2614373.7026 | 1157811.9336
1 | 2614365.0051 | 1157802.7455
2 | 2614453.6381 | 1157818.3534
3 | 2614417.4225 | 1157779.5144
4 | 2614280.1746 | 1157812.9495
5 | 2614245.8974 | 1157819.6497
6 | 2614813.4233 | 1158389.5921
7 | 2614844.5432 | 1158444.9223
8 | 2614833.1417 | 1158449.1297
9 | 2614861.284 | 1158495.5881
10 | 2614782.743 | 1158096.6071
11 | 2614779.0018 | 1158092.1422
12 | 2614833.4597 | 1158438.2474
13 | 2614831.8403 | 1158493.0801
14 | 2614869.9509 | 1158511.9069
15 | 2614354.2001 | 1157873.8404
16 | 2614225.0197 | 1157825.681
17 | 2614824.2857 | 1158555.3958
18 | 2614895.5964 | 1158503.9883
19 | 2614898.4318 | 1158603.9221
20 | 2614196.5975 | 1157832.5065
21 | 2614457.9325 | 1157824.2555
22 | 2614443.7413 | 1157715.5011
23 | 2614425.9165 | 1157715.4919
24 | 2614533.3673 | 1157764.9071
25 | 2614556.0902 | 1157876.517
26 | 2614560.6082 | 1157902.541
27 | 2614357.1248 | 1158031.4066
28 | 2614448.9209 | 1158175.085
29 | 2614319.4052 | 1157983.7602
30 | 2614471.133 | 1157991.1252
31 | 2614302.9574 | 1158105.1369
32 | 2614468.1536 | 1158197.3719
33 | 2614256.0449 | 1158070.998
34 | 2614487.5761 | 1158218.4327
35 | 2614484.3445 | 1158216.7397
36 | 2614499.6912 | 1158235.3975
37 | 2614752.1845 | 1158078.9594
38 | 2614755.9586 | 1158096.7997
39 | 2614818.2245 | 1158614.6751
40 | 2614744.9956 | 1158659.0624
41 | 2614898.5714 | 1158604.9584
42 | 2614962.7545 | 1158810.4457
43 | 2614955.6634 | 1158886.7512
44 | 2614953.1044 | 1158785.3364
45 | 2614959.8294 | 1158963.7304
46 | 2614951.4967 | 1158781.4083
47 | 2614958.3869 | 1158841.9829
48 | 2614974.6579 | 1158980.4976
49 | 2614933.8916 | 1158738.105
50 | 2615033.293 | 1158657.71
51 | 2615032.0026 | 1158933.0499
52 | 2614982.0194 | 1158986.0358
53 | 2614925.2305 | 1158716.7672
54 | 2615137.6484 | 1158817.3801
55 | 2614996.0335 | 1158993.5868
56 | 2614918.3236 | 1158699.3226
57 | 2614748.4279 | 1159104.4194
58 | 2614725.983 | 1159081.3266
59 | 2614821.6416 | 1159108.7839
60 | 2614819.7192 | 1159040.0394
61 | 2614394.2972 | 1158462.3194
62 | 2614394.4472 | 1158457.7953
63 | 2614399.5935 | 1158501.7071
64 | 2614408.369 | 1158479.8505
65 | 2614420.3506 | 1158546.9126
66 | 2614315.1281 | 1158499.2688
67 | 2614526.9944 | 1158430.4657
68 | 2614294.0557 | 1158429.6542
69 | 2614276.8013 | 1158392.2235
70 | 2614175.7783 | 1158297.3879
71 | 2614158.5248 | 1158626.1402
72 | 2614191.1749 | 1158693.9314
73 | 2614534.3218 | 1158444.1748
74 | 2614570.5181 | 1158499.4824
75 | 2614346.3504 | 1158274.946
76 | 2614343.0735 | 1158266.7452
77 | 2614214.5107 | 1158735.1845
78 | 2614334.0117 | 1158258.6303
79 | 2614224.1806 | 1158199.6422
80 | 2614195.1127 | 1158407.8102
81 | 2614123.7892 | 1158339.7761
82 | 2614157.9475 | 1158303.9938
83 | 2614171.2926 | 1158307.7381
84 | 2614125.6871 | 1158297.3202
85 | 2614144.7876 | 1158155.6896
86 | 2614209.2012 | 1158134.5191
87 | 2614080.4264 | 1158187.1414
88 | 2614095.0458 | 1158292.3966
89 | 2614573.9935 | 1158517.344
90 | 2614679.4521 | 1158449.6213
91 | 2614682.1399 | 1158435.0095
92 | 2614704.6926 | 1158533.7712
93 | 2614720.21 | 1158651.3414
94 | 2614721.0401 | 1158669.2643
95 | 2614721.7619 | 1158684.8468
96 | 2614722.6748 | 1158699.617
97 | 2614740.8494 | 1158695.947
98 | 2614751.5717 | 1158778.6155
99 | 2614789.2467 | 1158961.9303
100 | 2614786.8473 | 1158947.4322
101 | 2614789.285 | 1158962.1622
102 | 2614786.3887 | 1158944.6611
103 | 2614790.4826 | 1158969.3986
104 | 2614784.3045 | 1158932.0672
105 | 2614790.9765 | 1158972.3831
106 | 2614783.1277 | 1158924.9559
107 | 2614792.2708 | 1158980.2037
108 | 2614782.6195 | 1158921.8853
109 | 2614794.1215 | 1158984.2382
110 | 2614797.5353 | 1158991.6801
111 | 2614696.5588 | 1159043.4689
112 | 2614692.4337 | 1159037.3927
113 | 2614682.1204 | 1159017.6552
114 | 2614669.2311 | 1158977.7359
115 | 2614667.3036 | 1158976.3403
116 | 2614640.6601 | 1159029.8702
117 | 2614655.1666 | 1159046.9249
118 | 2614628.8785 | 1159058.5738
119 | 2614909.4533 | 1158671.7533
120 | 2614905.7793 | 1158654.579
121 | 2614902.4266 | 1158633.5861
122 | 2614901.7168 | 1158628.3155
123 | 2614596.3316 | 1159161.0327
124 | 2614586.6919 | 1159223.2688
125 | 2614562.4655 | 1159267.1321
126 | 2614531.2545 | 1159222.8461
127 | 2614554.7037 | 1159283.1873
128 | 2614494.5471 | 1159102.0648
129 | 2614266.0704 | 1158075.0125
130 | 2614186.5341 | 1158032.7155
131 | 2614777.0385 | 1158888.162
132 | 2614777.9577 | 1158893.7163
133 | 2614776.2332 | 1158883.2959
134 | 2614779.2251 | 1158901.3747
135 | 2614776.2094 | 1158883.152
136 | 2614781.9526 | 1158917.8556
137 | 2614770.0004 | 1158766.8642
138 | 2614746.9782 | 1158788.7111
139 | 2614787.3723 | 1158761.9809
140 | 2614728.9756 | 1158819.0915
141 | 2614751.9052 | 1158692.2846
142 | 2614796.283 | 1158760.241
143 | 2614752.7304 | 1158690.2301
144 | 2614804.5798 | 1158758.6019
145 | 2614750.2156 | 1158680.0967
146 | 2614744.9956 | 1158659.0624

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1