## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_571-8_1_4_node_28 | 0.4 | n |  | TRUE
1 | bus_LV_571-8_1_4_node_29 | 0.4 | n |  | TRUE
2 | bus_LV_571-8_1_4_node_30 | 0.4 | n |  | TRUE
3 | bus_LV_571-8_1_4_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_571-8_1_4_node_32 | 0.4 | n |  | TRUE
5 | bus_LV_571-8_1_4_node_33 | 0.4 | n |  | TRUE
6 | bus_LV_571-8_1_4_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_571-8_1_4_node_255 | 0.4 | n |  | TRUE
8 | bus_LV_571-8_1_4_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_571-8_1_4_node_252 | 0.4 | n |  | TRUE
10 | bus_LV_571-8_1_4_node_249 | 0.4 | n |  | TRUE
11 | bus_LV_571-8_1_4_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_571-8_1_4_node_254 | 0.4 | n |  | TRUE
13 | bus_LV_571-8_1_4_node_250 | 0.4 | n |  | TRUE
14 | bus_LV_571-8_1_4_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_571-8_1_4_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_571-8_1_4_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_571-8_1_4_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_571-8_1_4_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_571-8_1_4_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_571-8_1_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_571-8_1_4_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_571-8_1_4_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_571-8_1_4_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_571-8_1_4_node_262 | 0.4 | n |  | TRUE
25 | bus_LV_571-8_1_4_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_571-8_1_4_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_571-8_1_4_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_571-8_1_4_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_571-8_1_4_node_51 | 0.4 | n |  | TRUE
30 | bus_LV_571-8_1_4_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_571-8_1_4_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_571-8_1_4_node_147 | 0.4 | n |  | TRUE
33 | bus_LV_571-8_1_4_node_56 | 0.4 | n |  | TRUE
34 | bus_LV_571-8_1_4_node_145 | 0.4 | n |  | TRUE
35 | bus_LV_571-8_1_4_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_571-8_1_4_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_571-8_1_4_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_571-8_1_4_node_57 | 0.4 | n |  | TRUE
39 | bus_LV_571-8_1_4_node_58 | 0.4 | n |  | TRUE
40 | bus_LV_571-8_1_4_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_571-8_1_4_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_571-8_1_4_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_571-8_1_4_node_61 | 0.4 | n |  | TRUE
44 | bus_LV_571-8_1_4_node_62 | 0.4 | n |  | TRUE
45 | bus_LV_571-8_1_4_node_66 | 0.4 | n |  | TRUE
46 | bus_LV_571-8_1_4_node_68 | 0.4 | n |  | TRUE
47 | bus_LV_571-8_1_4_node_104 | 0.4 | n |  | TRUE
48 | bus_LV_571-8_1_4_node_258 | 0.4 | n |  | TRUE
49 | bus_LV_571-8_1_4_node_256 | 0.4 | n |  | TRUE
50 | bus_LV_571-8_1_4_node_67 | 0.4 | n |  | TRUE
51 | bus_LV_571-8_1_4_node_69 | 0.4 | n |  | TRUE
52 | bus_LV_571-8_1_4_node_94 | 0.4 | n |  | TRUE
53 | bus_LV_571-8_1_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_571-8_1_4_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_571-8_1_4_node_91 | 0.4 | n |  | TRUE
56 | bus_LV_571-8_1_4_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_571-8_1_4_node_93 | 0.4 | n |  | TRUE
58 | bus_LV_571-8_1_4_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_571-8_1_4_node_105 | 0.4 | n |  | TRUE
60 | bus_LV_571-8_1_4_node_106 | 0.4 | n |  | TRUE
61 | bus_LV_571-8_1_4_node_143 | 0.4 | n |  | TRUE
62 | bus_LV_571-8_1_4_node_144 | 0.4 | n |  | TRUE
63 | bus_LV_571-8_1_4_node_137 | 0.4 | n |  | TRUE
64 | bus_LV_571-8_1_4_node_103 | 0.4 | n |  | TRUE
65 | bus_LV_571-8_1_4_node_96 | 0.4 | n |  | TRUE
66 | bus_LV_571-8_1_4_node_97 | 0.4 | n |  | TRUE
67 | bus_LV_571-8_1_4_node_98 | 0.4 | n |  | TRUE
68 | bus_LV_571-8_1_4_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_571-8_1_4_node_100 | 0.4 | n |  | TRUE
70 | bus_LV_571-8_1_4_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_571-8_1_4_node_102 | 0.4 | n |  | TRUE
72 | bus_LV_571-8_1_4_node_126 | 0.4 | n |  | TRUE
73 | bus_LV_571-8_1_4_node_127 | 0.4 | n |  | TRUE
74 | bus_LV_571-8_1_4_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_571-8_1_4_node_162 | 0.4 | n |  | TRUE
76 | bus_LV_571-8_1_4_node_166 | 0.4 | n |  | TRUE
77 | bus_LV_571-8_1_4_node_263 | 0.4 | n |  | TRUE
78 | bus_LV_571-8_1_4_node_146 | 0.4 | n |  | TRUE
79 | bus_LV_571-8_1_4_node_142 | 0.4 | n |  | TRUE
80 | bus_LV_571-8_1_4_node_107 | 0.4 | n |  | TRUE
81 | bus_LV_571-8_1_4_node_108 | 0.4 | n |  | TRUE
82 | bus_LV_571-8_1_4_node_109 | 0.4 | n |  | TRUE
83 | bus_LV_571-8_1_4_node_110 | 0.4 | n |  | TRUE
84 | bus_LV_571-8_1_4_node_111 | 0.4 | n |  | TRUE
85 | bus_LV_571-8_1_4_node_112 | 0.4 | n |  | TRUE
86 | bus_LV_571-8_1_4_node_113 | 0.4 | n |  | TRUE
87 | bus_LV_571-8_1_4_node_135 | 0.4 | n |  | TRUE
88 | bus_LV_571-8_1_4_node_138 | 0.4 | n |  | TRUE
89 | bus_LV_571-8_1_4_node_134 | 0.4 | n |  | TRUE
90 | bus_LV_571-8_1_4_node_139 | 0.4 | n |  | TRUE
91 | bus_LV_571-8_1_4_node_114 | 0.4 | n |  | TRUE
92 | bus_LV_571-8_1_4_node_115 | 0.4 | n |  | TRUE
93 | bus_LV_571-8_1_4_node_116 | 0.4 | n |  | TRUE
94 | bus_LV_571-8_1_4_node_117 | 0.4 | n |  | TRUE
95 | bus_LV_571-8_1_4_node_118 | 0.4 | n |  | TRUE
96 | bus_LV_571-8_1_4_node_119 | 0.4 | n |  | TRUE
97 | bus_LV_571-8_1_4_node_130 | 0.4 | n |  | TRUE
98 | bus_LV_571-8_1_4_node_129 | 0.4 | n |  | TRUE
99 | bus_LV_571-8_1_4_node_131 | 0.4 | n |  | TRUE
100 | bus_LV_571-8_1_4_node_128 | 0.4 | n |  | TRUE
101 | bus_LV_571-8_1_4_node_132 | 0.4 | n |  | TRUE
102 | bus_LV_571-8_1_4_node_120 | 0.4 | n |  | TRUE
103 | bus_LV_571-8_1_4_node_121 | 0.4 | n |  | TRUE
104 | bus_LV_571-8_1_4_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_571-8_1_4_node_123 | 0.4 | n |  | TRUE
106 | bus_LV_571-8_1_4_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_571-8_1_4_node_125 | 0.4 | n |  | TRUE
108 | bus_LV_571-8_1_4_node_180 | 0.4 | n |  | TRUE
109 | bus_LV_571-8_1_4_node_181 | 0.4 | n |  | TRUE
110 | bus_LV_571-8_1_4_node_160 | 0.4 | n |  | TRUE
111 | bus_LV_571-8_1_4_node_171 | 0.4 | n |  | TRUE
112 | bus_LV_571-8_1_4_node_133 | 0.4 | n |  | TRUE
113 | bus_LV_571-8_1_4_node_136 | 0.4 | n |  | TRUE
114 | bus_LV_571-8_1_4_node_140 | 0.4 | n |  | TRUE
115 | bus_LV_571-8_1_4_node_141 | 0.4 | n |  | TRUE
116 | bus_LV_571-8_1_4_node_149 | 0.4 | n |  | TRUE
117 | bus_LV_571-8_1_4_node_150 | 0.4 | n |  | TRUE
118 | bus_LV_571-8_1_4_node_183 | 0.4 | n |  | TRUE
119 | bus_LV_571-8_1_4_node_182 | 0.4 | n |  | TRUE
120 | bus_LV_571-8_1_4_node_185 | 0.4 | n |  | TRUE
121 | bus_LV_571-8_1_4_node_148 | 0.4 | n |  | TRUE
122 | bus_LV_571-8_1_4_node_184 | 0.4 | n |  | TRUE
123 | bus_LV_571-8_1_4_node_152 | 0.4 | n |  | TRUE
124 | bus_LV_571-8_1_4_node_153 | 0.4 | n |  | TRUE
125 | bus_LV_571-8_1_4_node_154 | 0.4 | n |  | TRUE
126 | bus_LV_571-8_1_4_node_155 | 0.4 | n |  | TRUE
127 | bus_LV_571-8_1_4_node_156 | 0.4 | n |  | TRUE
128 | bus_LV_571-8_1_4_node_157 | 0.4 | n |  | TRUE
129 | bus_LV_571-8_1_4_node_158 | 0.4 | n |  | TRUE
130 | bus_LV_571-8_1_4_node_159 | 0.4 | n |  | TRUE
131 | bus_LV_571-8_1_4_node_170 | 0.4 | n |  | TRUE
132 | bus_LV_571-8_1_4_node_164 | 0.4 | n |  | TRUE
133 | bus_LV_571-8_1_4_node_167 | 0.4 | n |  | TRUE
134 | bus_LV_571-8_1_4_node_165 | 0.4 | n |  | TRUE
135 | bus_LV_571-8_1_4_node_163 | 0.4 | n |  | TRUE
136 | bus_LV_571-8_1_4_node_168 | 0.4 | n |  | TRUE
137 | bus_LV_571-8_1_4_node_161 | 0.4 | n |  | TRUE
138 | bus_LV_571-8_1_4_node_172 | 0.4 | n |  | TRUE
139 | bus_LV_571-8_1_4_node_169 | 0.4 | n |  | TRUE
140 | bus_LV_571-8_1_4_node_173 | 0.4 | n |  | TRUE
141 | bus_LV_571-8_1_4_node_174 | 0.4 | n |  | TRUE
142 | bus_LV_571-8_1_4_node_175 | 0.4 | n |  | TRUE
143 | bus_LV_571-8_1_4_node_176 | 0.4 | n |  | TRUE
144 | bus_LV_571-8_1_4_node_177 | 0.4 | n |  | TRUE
145 | bus_LV_571-8_1_4_node_179 | 0.4 | n |  | TRUE
146 | bus_LV_571-8_1_4_node_186 | 0.4 | n |  | TRUE
147 | bus_LV_571-8_1_4_node_187 | 0.4 | n |  | TRUE
148 | bus_LV_571-8_1_4_node_188 | 0.4 | n |  | TRUE
149 | bus_LV_571-8_1_4_node_189 | 0.4 | n |  | TRUE
150 | bus_LV_571-8_1_4_node_190 | 0.4 | n |  | TRUE
151 | bus_LV_571-8_1_4_node_191 | 0.4 | n |  | TRUE
152 | bus_LV_571-8_1_4_node_192 | 0.4 | n |  | TRUE
153 | bus_LV_571-8_1_4_node_198 | 0.4 | n |  | TRUE
154 | bus_LV_571-8_1_4_node_199 | 0.4 | n |  | TRUE
155 | bus_LV_571-8_1_4_node_200 | 0.4 | n |  | TRUE
156 | bus_LV_571-8_1_4_node_201 | 0.4 | n |  | TRUE
157 | bus_LV_571-8_1_4_node_234 | 0.4 | n |  | TRUE
158 | bus_LV_571-8_1_4_node_235 | 0.4 | n |  | TRUE
159 | bus_LV_571-8_1_4_node_236 | 0.4 | n |  | TRUE
160 | bus_LV_571-8_1_4_node_237 | 0.4 | n |  | TRUE
161 | bus_LV_571-8_1_4_node_238 | 0.4 | n |  | TRUE
162 | bus_LV_571-8_1_4_node_239 | 0.4 | n |  | TRUE
163 | bus_LV_571-8_1_4_node_240 | 0.4 | n |  | TRUE
164 | bus_LV_571-8_1_4_node_241 | 0.4 | n |  | TRUE
165 | bus_LV_571-8_1_4_node_242 | 0.4 | n |  | TRUE
166 | bus_LV_571-8_1_4_node_243 | 0.4 | n |  | TRUE
167 | bus_LV_571-8_1_4_node_259 | 0.4 | n |  | TRUE
168 | bus_LV_571-8_1_4_node_261 | 0.4 | n |  | TRUE
169 | bus_LV_571-8_1_4_node_257 | 0.4 | n |  | TRUE
170 | bus_LV_571-8_1_4_node_251 | 0.4 | n |  | TRUE
171 | bus_LV_571-8_1_4_node_253 | 0.4 | n |  | TRUE
172 | bus_LV_571-8_1_4_node_260 | 0.4 | n |  | TRUE
173 | bus_MV_81_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_571-8_1_4_load_28 | 0 | 0.0002009 | 5.0351e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_571-8_1_4_load_29 | 1 | 0.00071576 | 0.00017939 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_571-8_1_4_load_31 | 3 | 0.00067245 | 0.00016853 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_571-8_1_4_load_32 | 4 | 0.00075588 | 0.00018944 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_571-8_1_4_load_35 | 6 | 0.0015352 | 0.00038476 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_571-8_1_4_load_255 | 7 | 0.0005656 | 0.00014175 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_571-8_1_4_load_249 | 10 | 0.00050968 | 0.00012774 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_571-8_1_4_load_36 | 11 | 0.00026223 | 6.5722e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_571-8_1_4_load_254 | 12 | 0.00074176 | 0.0001859 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_571-8_1_4_load_250 | 13 | 0.0005282 | 0.00013238 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_571-8_1_4_load_38 | 15 | 0.0012886 | 0.00032296 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_571-8_1_4_load_39 | 16 | 0.0023494 | 0.00058881 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_571-8_1_4_load_44 | 18 | 0.0012357 | 0.00030971 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_571-8_1_4_load_41 | 19 | 0.001343 | 0.0003366 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_571-8_1_4_load_42 | 21 | 0.00095828 | 0.00024017 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_571-8_1_4_load_262 | 24 | 0.00079702 | 0.00019975 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_571-8_1_4_load_50 | 25 | 0.00096763 | 0.00024251 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_571-8_1_4_load_47 | 26 | 0.00084602 | 0.00021203 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_571-8_1_4_load_48 | 27 | 0.00051418 | 0.00012887 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_571-8_1_4_load_49 | 28 | 0.00072667 | 0.00018212 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_571-8_1_4_load_51 | 29 | 0.00087867 | 0.00022022 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_571-8_1_4_load_59 | 30 | 0.0004073 | 0.00010208 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_571-8_1_4_load_52 | 31 | 0.00070893 | 0.00017768 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_571-8_1_4_load_147 | 32 | 0.00078452 | 0.00019662 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_571-8_1_4_load_53 | 35 | 0.0011522 | 0.00028877 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_571-8_1_4_load_54 | 36 | 0.00024359 | 6.105e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_571-8_1_4_load_58 | 39 | 0.0002271 | 5.6916e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_571-8_1_4_load_63 | 40 | 0.00033352 | 8.3588e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_571-8_1_4_load_64 | 41 | 0.00063336 | 0.00015874 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_571-8_1_4_load_65 | 42 | 0.00077676 | 0.00019467 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_571-8_1_4_load_66 | 45 | 0.00096503 | 0.00024186 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_571-8_1_4_load_68 | 46 | 0.00048777 | 0.00012225 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_571-8_1_4_load_104 | 47 | 0.0012767 | 0.00031997 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_571-8_1_4_load_258 | 48 | 0.00058965 | 0.00014778 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_571-8_1_4_load_67 | 50 | 0.00050107 | 0.00012558 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_571-8_1_4_load_69 | 51 | 0.0016322 | 0.00040906 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_571-8_1_4_load_94 | 52 | 0.00044949 | 0.00011265 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_571-8_1_4_load_70 | 53 | 0.00097891 | 0.00024534 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_571-8_1_4_load_90 | 54 | 0.00082046 | 0.00020563 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_571-8_1_4_load_91 | 55 | 0.00075164 | 0.00018838 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_571-8_1_4_load_92 | 56 | 0.00027218 | 6.8214e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_571-8_1_4_load_106 | 60 | 0.00052156 | 0.00013072 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_571-8_1_4_load_143 | 61 | 0.00051381 | 0.00012877 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_571-8_1_4_load_96 | 65 | 0.0019696 | 0.00049363 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_571-8_1_4_load_97 | 66 | 0.0016639 | 0.000417 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_571-8_1_4_load_98 | 67 | 0.0055269 | 0.0013852 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_571-8_1_4_load_99 | 68 | 0.0025331 | 0.00063486 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_571-8_1_4_load_102 | 71 | 0.0010862 | 0.00027222 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_571-8_1_4_load_126 | 72 | 0.0046541 | 0.0011664 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_571-8_1_4_load_127 | 73 | 0.0059401 | 0.0014887 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_571-8_1_4_load_151 | 74 | 0.00076949 | 0.00019285 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_571-8_1_4_load_162 | 75 | 0.0020854 | 0.00052265 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_571-8_1_4_load_166 | 76 | 0.002718 | 0.0006812 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_571-8_1_4_load_263 | 77 | 0.0010078 | 0.00025259 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_571-8_1_4_load_142 | 79 | 0.0011086 | 0.00027783 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_571-8_1_4_load_107 | 80 | 0.00059894 | 0.00015011 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_571-8_1_4_load_108 | 81 | 0.00060207 | 0.00015089 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_571-8_1_4_load_109 | 82 | 0.00053126 | 0.00013315 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_571-8_1_4_load_110 | 83 | 0.00077286 | 0.0001937 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_571-8_1_4_load_111 | 84 | 0.00051362 | 0.00012873 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_571-8_1_4_load_112 | 85 | 0.00048285 | 0.00012101 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_571-8_1_4_load_113 | 86 | 0.00048036 | 0.00012039 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_571-8_1_4_load_135 | 87 | 0.00117 | 0.00029322 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_571-8_1_4_load_138 | 88 | 0.00022556 | 5.653e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_571-8_1_4_load_114 | 91 | 0.00069643 | 0.00017454 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_571-8_1_4_load_115 | 92 | 0.00085741 | 0.00021489 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_571-8_1_4_load_116 | 93 | 0.0030375 | 0.00076127 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_571-8_1_4_load_119 | 96 | 0.0040511 | 0.0010153 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_571-8_1_4_load_130 | 97 | 0.00078643 | 0.0001971 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_571-8_1_4_load_129 | 98 | 0.0061449 | 0.0015401 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_571-8_1_4_load_131 | 99 | 0.0013321 | 0.00033385 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_571-8_1_4_load_128 | 100 | 0.0097713 | 0.0024489 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_571-8_1_4_load_120 | 102 | 0.00079001 | 0.000198 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_571-8_1_4_load_121 | 103 | 0.0015539 | 0.00038945 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_571-8_1_4_load_122 | 104 | 0.009095 | 0.0022794 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_571-8_1_4_load_124 | 106 | 0.000691 | 0.00017318 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_571-8_1_4_load_125 | 107 | 0.0015084 | 0.00037805 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_571-8_1_4_load_180 | 108 | 0.0012162 | 0.0003048 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_571-8_1_4_load_181 | 109 | 0.00094811 | 0.00023762 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_571-8_1_4_load_160 | 110 | 0.0067891 | 0.0017015 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_571-8_1_4_load_171 | 111 | 0.0019095 | 0.00047856 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_571-8_1_4_load_133 | 112 | 0.00025202 | 6.3163e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_571-8_1_4_load_136 | 113 | 0.0008138 | 0.00020396 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_571-8_1_4_load_140 | 114 | 0.00034242 | 8.5818e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_571-8_1_4_load_141 | 115 | 0.00057394 | 0.00014384 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_571-8_1_4_load_150 | 117 | 0.00093668 | 0.00023475 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_571-8_1_4_load_183 | 118 | 0.00024167 | 6.0569e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_571-8_1_4_load_182 | 119 | 0.00091411 | 0.0002291 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_571-8_1_4_load_185 | 120 | 0.00024176 | 6.059e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_571-8_1_4_load_148 | 121 | 0.00091899 | 0.00023032 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_571-8_1_4_load_184 | 122 | 0.00037092 | 9.2962e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_571-8_1_4_load_152 | 123 | 0.00092752 | 0.00023246 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_571-8_1_4_load_153 | 124 | 0.0016162 | 0.00040507 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_571-8_1_4_load_155 | 126 | 0.0015102 | 0.0003785 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_571-8_1_4_load_158 | 129 | 0.0018416 | 0.00046154 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_571-8_1_4_load_159 | 130 | 0.00062397 | 0.00015638 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_571-8_1_4_load_170 | 131 | 0.0011848 | 0.00029693 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_571-8_1_4_load_167 | 133 | 0.0025188 | 0.00063128 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_571-8_1_4_load_165 | 134 | 0.0018941 | 0.00047471 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_571-8_1_4_load_163 | 135 | 0.0025607 | 0.00064176 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_571-8_1_4_load_168 | 136 | 0.00063477 | 0.00015909 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_571-8_1_4_load_161 | 137 | 0.0024213 | 0.00060683 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_571-8_1_4_load_172 | 138 | 0.0036596 | 0.00091719 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_571-8_1_4_load_169 | 139 | 0.0020646 | 0.00051743 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_571-8_1_4_load_173 | 140 | 0.0025064 | 0.00062817 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_571-8_1_4_load_174 | 141 | 0.0020025 | 0.00050188 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_571-8_1_4_load_175 | 142 | 0.0022768 | 0.00057062 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_571-8_1_4_load_176 | 143 | 0.0037548 | 0.00094105 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_571-8_1_4_load_177 | 144 | 0.0013113 | 0.00032865 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_571-8_1_4_load_179 | 145 | 0.0010526 | 0.0002638 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_571-8_1_4_load_188 | 148 | 0.00050308 | 0.00012608 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_571-8_1_4_load_189 | 149 | 0.00027877 | 6.9866e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_571-8_1_4_load_190 | 150 | 0.00017265 | 4.3271e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_571-8_1_4_load_191 | 151 | 0.00021131 | 5.2959e-05 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_571-8_1_4_load_192 | 152 | 0.00070907 | 0.00017771 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_571-8_1_4_load_198 | 153 | 0.00034258 | 8.5859e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_571-8_1_4_load_199 | 154 | 0.00033508 | 8.398e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_571-8_1_4_load_200 | 155 | 0.00028321 | 7.0979e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_571-8_1_4_load_201 | 156 | 0.00059942 | 0.00015023 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_571-8_1_4_load_234 | 157 | 0.00041206 | 0.00010327 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_571-8_1_4_load_236 | 159 | 0.00018601 | 4.6619e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_571-8_1_4_load_237 | 160 | 0.0003739 | 9.3709e-05 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_571-8_1_4_load_240 | 163 | 0.00020054 | 5.0261e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_571-8_1_4_load_242 | 165 | 0.00072405 | 0.00018146 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_571-8_1_4_load_243 | 166 | 0.0030093 | 0.00075419 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_571-8_1_4_load_259 | 167 | 0.0010418 | 0.00026109 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_571-8_1_4_load_261 | 168 | 0.0012929 | 0.00032403 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_571-8_1_4_load_251 | 170 | 0.00053074 | 0.00013302 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_571-8_1_4_load_253 | 171 | 0.00030755 | 7.7078e-05 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_571-8_1_4_load_260 | 172 | 0.0016314 | 0.00040886 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 99 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_571-8_1_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.006688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_571-8_1_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.1437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_571-8_1_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0064991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_571-8_1_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.081338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_571-8_1_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.089701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_571-8_1_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.029622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_571-8_1_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.067723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_571-8_1_4_line_7 | NAYY 4x150 SE | 6 | 11 | 0.0019901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_571-8_1_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.025047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_571-8_1_4_line_9 | NAYY 4x150 SE | 8 | 9 | 0.019006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_571-8_1_4_line_10 | NAYY 4x150 SE | 8 | 10 | 0.055811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_571-8_1_4_line_11 | NAYY 4x150 SE | 9 | 12 | 0.080761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_571-8_1_4_line_12 | NAYY 4x150 SE | 10 | 13 | 0.01224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_571-8_1_4_line_13 | NAYY 4x150 SE | 11 | 14 | 0.020906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_571-8_1_4_line_14 | NAYY 4x150 SE | 12 | 166 | 0.05319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_571-8_1_4_line_15 | NAYY 4x150 SE | 13 | 170 | 0.014082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_571-8_1_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.035025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_571-8_1_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.018748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_571-8_1_4_line_18 | NAYY 4x150 SE | 16 | 17 | 0.037138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_571-8_1_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.01275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_571-8_1_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.013578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_571-8_1_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.020378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_571-8_1_4_line_22 | NAYY 4x150 SE | 19 | 21 | 0.012371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_571-8_1_4_line_23 | NAYY 4x150 SE | 20 | 25 | 0.01384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_571-8_1_4_line_24 | NAYY 4x150 SE | 20 | 26 | 0.0099358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_571-8_1_4_line_25 | NAYY 4x150 SE | 21 | 22 | 0.054791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_571-8_1_4_line_26 | NAYY 4x150 SE | 22 | 23 | 0.036084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_571-8_1_4_line_27 | NAYY 4x150 SE | 23 | 24 | 0.071182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_571-8_1_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.10489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_571-8_1_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.057941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_571-8_1_4_line_30 | NAYY 4x150 SE | 28 | 29 | 0.10077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_571-8_1_4_line_31 | NAYY 4x150 SE | 29 | 30 | 0.0072959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_571-8_1_4_line_32 | NAYY 4x150 SE | 30 | 33 | 0.056802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_571-8_1_4_line_33 | NAYY 4x150 SE | 31 | 32 | 0.097526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_571-8_1_4_line_34 | NAYY 4x150 SE | 32 | 34 | 0.022429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_571-8_1_4_line_35 | NAYY 4x150 SE | 33 | 36 | 0.021903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_571-8_1_4_line_36 | NAYY 4x150 SE | 34 | 78 | 0.001931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_571-8_1_4_line_37 | NAYY 4x150 SE | 34 | 97 | 0.012674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_571-8_1_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.00094008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_571-8_1_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.0081163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_571-8_1_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.039847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_571-8_1_4_line_41 | NAYY 4x150 SE | 37 | 39 | 0.0067806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_571-8_1_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.0050625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_571-8_1_4_line_43 | NAYY 4x150 SE | 38 | 41 | 0.066682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_571-8_1_4_line_44 | NAYY 4x150 SE | 39 | 42 | 0.099255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_571-8_1_4_line_45 | NAYY 4x150 SE | 40 | 43 | 0.0027538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_571-8_1_4_line_46 | NAYY 4x150 SE | 41 | 46 | 0.084729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_571-8_1_4_line_47 | NAYY 4x150 SE | 42 | 47 | 0.0046277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_571-8_1_4_line_48 | NAYY 4x150 SE | 43 | 44 | 0.040389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_571-8_1_4_line_49 | NAYY 4x150 SE | 44 | 45 | 0.01004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_571-8_1_4_line_50 | NAYY 4x150 SE | 45 | 50 | 0.022886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_571-8_1_4_line_51 | NAYY 4x150 SE | 46 | 51 | 0.018288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_571-8_1_4_line_52 | NAYY 4x150 SE | 47 | 52 | 0.0078977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_571-8_1_4_line_53 | NAYY 4x150 SE | 48 | 49 | 0.057322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_571-8_1_4_line_54 | NAYY 4x150 SE | 49 | 169 | 0.082708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_571-8_1_4_line_55 | NAYY 4x150 SE | 51 | 53 | 0.0023188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_571-8_1_4_line_56 | NAYY 4x150 SE | 52 | 57 | 0.0050956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_571-8_1_4_line_57 | NAYY 4x150 SE | 54 | 55 | 0.071403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_571-8_1_4_line_58 | NAYY 4x150 SE | 54 | 56 | 0.0036192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_571-8_1_4_line_59 | NAYY 4x150 SE | 55 | 57 | 0.016223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_571-8_1_4_line_60 | NAYY 4x150 SE | 57 | 58 | 0.012143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_571-8_1_4_line_61 | NAYY 4x150 SE | 58 | 59 | 0.018024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_571-8_1_4_line_62 | NAYY 4x150 SE | 58 | 60 | 0.06683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_571-8_1_4_line_63 | NAYY 4x150 SE | 59 | 61 | 0.020611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_571-8_1_4_line_64 | NAYY 4x150 SE | 59 | 62 | 0.033247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_571-8_1_4_line_65 | NAYY 4x150 SE | 59 | 63 | 0.02236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_571-8_1_4_line_66 | NAYY 4x150 SE | 60 | 64 | 0.036893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
67 | LV_571-8_1_4_line_67 | NAYY 4x150 SE | 62 | 77 | 0.026087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_571-8_1_4_line_68 | NAYY 4x150 SE | 62 | 78 | 0.027902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
69 | LV_571-8_1_4_line_69 | NAYY 4x150 SE | 63 | 79 | 0.012616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_571-8_1_4_line_70 | NAYY 4x150 SE | 64 | 74 | 0.020157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_571-8_1_4_line_71 | NAYY 4x150 SE | 64 | 69 | 0.006982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_571-8_1_4_line_72 | NAYY 4x150 SE | 65 | 66 | 0.012976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_571-8_1_4_line_73 | NAYY 4x150 SE | 65 | 67 | 0.0021569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_571-8_1_4_line_74 | NAYY 4x150 SE | 66 | 68 | 0.016807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_571-8_1_4_line_75 | NAYY 4x150 SE | 67 | 69 | 0.066654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_571-8_1_4_line_76 | NAYY 4x150 SE | 68 | 70 | 0.013971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_571-8_1_4_line_77 | NAYY 4x150 SE | 69 | 71 | 0.021965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_571-8_1_4_line_78 | NAYY 4x150 SE | 70 | 72 | 0.0045661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_571-8_1_4_line_79 | NAYY 4x150 SE | 70 | 73 | 0.038647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_571-8_1_4_line_80 | NAYY 4x150 SE | 72 | 75 | 0.016081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_571-8_1_4_line_81 | NAYY 4x150 SE | 73 | 76 | 0.014978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_571-8_1_4_line_82 | NAYY 4x150 SE | 75 | 110 | 0.018593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_571-8_1_4_line_83 | NAYY 4x150 SE | 76 | 111 | 0.024799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_571-8_1_4_line_84 | NAYY 4x150 SE | 78 | 121 | 0.039303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_571-8_1_4_line_85 | NAYY 4x150 SE | 80 | 81 | 0.011265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_571-8_1_4_line_86 | NAYY 4x150 SE | 80 | 82 | 0.022639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_571-8_1_4_line_87 | NAYY 4x150 SE | 81 | 83 | 0.032145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_571-8_1_4_line_88 | NAYY 4x150 SE | 82 | 84 | 0.011706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_571-8_1_4_line_89 | NAYY 4x150 SE | 83 | 85 | 0.010554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_571-8_1_4_line_90 | NAYY 4x150 SE | 84 | 86 | 0.050826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_571-8_1_4_line_91 | NAYY 4x150 SE | 85 | 87 | 0.013385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_571-8_1_4_line_92 | NAYY 4x150 SE | 86 | 88 | 0.032554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_571-8_1_4_line_93 | NAYY 4x150 SE | 87 | 89 | 0.014196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_571-8_1_4_line_94 | NAYY 4x150 SE | 88 | 90 | 0.011106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_571-8_1_4_line_95 | NAYY 4x150 SE | 89 | 113 | 0.060624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_571-8_1_4_line_96 | NAYY 4x150 SE | 89 | 101 | 0.021974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_571-8_1_4_line_97 | NAYY 4x150 SE | 90 | 114 | 0.052085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_571-8_1_4_line_98 | NAYY 4x150 SE | 90 | 115 | 0.057495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_571-8_1_4_line_99 | NAYY 4x150 SE | 91 | 92 | 0.019825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_571-8_1_4_line_100 | NAYY 4x150 SE | 91 | 93 | 0.0010735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_571-8_1_4_line_101 | NAYY 4x150 SE | 92 | 94 | 0.02071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_571-8_1_4_line_102 | NAYY 4x150 SE | 94 | 95 | 0.054792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_571-8_1_4_line_103 | NAYY 4x150 SE | 94 | 96 | 0.010253 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_571-8_1_4_line_104 | NAYY 4x150 SE | 95 | 97 | 0.028257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_571-8_1_4_line_105 | NAYY 4x150 SE | 95 | 98 | 0.041044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_571-8_1_4_line_106 | NAYY 4x150 SE | 96 | 99 | 0.012953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_571-8_1_4_line_107 | NAYY 4x150 SE | 98 | 100 | 0.034801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_571-8_1_4_line_108 | NAYY 4x150 SE | 99 | 101 | 0.036604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_571-8_1_4_line_109 | NAYY 4x150 SE | 100 | 106 | 0.056509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_571-8_1_4_line_110 | NAYY 4x150 SE | 101 | 112 | 0.026087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_571-8_1_4_line_111 | NAYY 4x150 SE | 102 | 103 | 0.0021243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_571-8_1_4_line_112 | NAYY 4x150 SE | 102 | 104 | 0.044165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_571-8_1_4_line_113 | NAYY 4x150 SE | 103 | 105 | 0.022618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_571-8_1_4_line_114 | NAYY 4x150 SE | 105 | 106 | 0.031769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_571-8_1_4_line_115 | NAYY 4x150 SE | 105 | 107 | 0.024195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_571-8_1_4_line_116 | NAYY 4x150 SE | 107 | 108 | 0.0024992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_571-8_1_4_line_117 | NAYY 4x150 SE | 108 | 109 | 0.0032909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_571-8_1_4_line_118 | NAYY 4x150 SE | 109 | 145 | 0.0020018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_571-8_1_4_line_119 | NAYY 4x150 SE | 110 | 137 | 0.018931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_571-8_1_4_line_120 | NAYY 4x150 SE | 111 | 138 | 0.0023233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_571-8_1_4_line_121 | NAYY 4x150 SE | 114 | 116 | 0.05011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_571-8_1_4_line_122 | NAYY 4x150 SE | 115 | 117 | 0.010025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_571-8_1_4_line_123 | NAYY 4x150 SE | 116 | 118 | 0.0036813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_571-8_1_4_line_124 | NAYY 4x150 SE | 116 | 119 | 0.017871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_571-8_1_4_line_125 | NAYY 4x150 SE | 117 | 120 | 0.053894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_571-8_1_4_line_126 | NAYY 4x150 SE | 120 | 122 | 0.026159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_571-8_1_4_line_127 | NAYY 4x150 SE | 122 | 146 | 0.051329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_571-8_1_4_line_128 | NAYY 4x150 SE | 123 | 124 | 0.0029143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_571-8_1_4_line_129 | NAYY 4x150 SE | 123 | 125 | 0.003745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_571-8_1_4_line_130 | NAYY 4x150 SE | 124 | 126 | 0.0087155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_571-8_1_4_line_131 | NAYY 4x150 SE | 125 | 127 | 0.01162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_571-8_1_4_line_132 | NAYY 4x150 SE | 125 | 128 | 0.087226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_571-8_1_4_line_133 | NAYY 4x150 SE | 126 | 129 | 0.026884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_571-8_1_4_line_134 | NAYY 4x150 SE | 127 | 130 | 0.0072123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_571-8_1_4_line_135 | NAYY 4x150 SE | 128 | 131 | 0.0081525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_571-8_1_4_line_136 | NAYY 4x150 SE | 129 | 132 | 0.041439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_571-8_1_4_line_137 | NAYY 4x150 SE | 130 | 133 | 0.031653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_571-8_1_4_line_138 | NAYY 4x150 SE | 132 | 134 | 0.040579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_571-8_1_4_line_139 | NAYY 4x150 SE | 132 | 135 | 0.016261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_571-8_1_4_line_140 | NAYY 4x150 SE | 133 | 136 | 0.0096651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_571-8_1_4_line_141 | NAYY 4x150 SE | 135 | 137 | 9.2136e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_571-8_1_4_line_142 | NAYY 4x150 SE | 136 | 139 | 0.0081304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_571-8_1_4_line_143 | NAYY 4x150 SE | 140 | 141 | 0.00089856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_571-8_1_4_line_144 | NAYY 4x150 SE | 140 | 142 | 0.0015091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_571-8_1_4_line_145 | NAYY 4x150 SE | 141 | 143 | 0.028004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_571-8_1_4_line_146 | NAYY 4x150 SE | 142 | 144 | 0.0075897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_571-8_1_4_line_147 | NAYY 4x150 SE | 144 | 145 | 0.013896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_571-8_1_4_line_148 | NAYY 4x150 SE | 146 | 147 | 0.003543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_571-8_1_4_line_149 | NAYY 4x150 SE | 146 | 148 | 0.042717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_571-8_1_4_line_150 | NAYY 4x150 SE | 147 | 149 | 0.065799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_571-8_1_4_line_151 | NAYY 4x150 SE | 149 | 150 | 0.047418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_571-8_1_4_line_152 | NAYY 4x150 SE | 150 | 151 | 0.020084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_571-8_1_4_line_153 | NAYY 4x150 SE | 151 | 152 | 0.018044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_571-8_1_4_line_154 | NAYY 4x150 SE | 152 | 153 | 0.013703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_571-8_1_4_line_155 | NAYY 4x150 SE | 153 | 154 | 0.034857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_571-8_1_4_line_156 | NAYY 4x150 SE | 154 | 155 | 0.0040893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_571-8_1_4_line_157 | NAYY 4x150 SE | 155 | 156 | 0.022977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_571-8_1_4_line_158 | NAYY 4x150 SE | 157 | 158 | 0.039138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_571-8_1_4_line_159 | NAYY 4x150 SE | 157 | 159 | 0.012061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_571-8_1_4_line_160 | NAYY 4x150 SE | 158 | 160 | 0.14427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_571-8_1_4_line_161 | NAYY 4x150 SE | 160 | 161 | 0.13823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
162 | LV_571-8_1_4_line_162 | NAYY 4x150 SE | 161 | 162 | 0.043788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_571-8_1_4_line_163 | NAYY 4x150 SE | 161 | 163 | 0.054918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_571-8_1_4_line_164 | NAYY 4x150 SE | 162 | 164 | 0.021175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_571-8_1_4_line_165 | NAYY 4x150 SE | 162 | 165 | 0.043398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
166 | LV_571-8_1_4_line_166 | NAYY 4x150 SE | 163 | 166 | 0.00069859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_571-8_1_4_line_167 | NAYY 4x150 SE | 164 | 167 | 0.076338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_571-8_1_4_line_168 | NAYY 4x150 SE | 167 | 168 | 0.027986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_571-8_1_4_line_169 | NAYY 4x150 SE | 168 | 169 | 0.056371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
170 | LV_571-8_1_4_line_170 | NAYY 4x150 SE | 169 | 172 | 0.04543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_571-8_1_4_line_171 | NAYY 4x150 SE | 170 | 171 | 0.015372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_571-8_1_4_trafo_131 | 0.25 MVA 20/0.4 kV | 173 | 99 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2628540.2636 | 1171926.1525 | 2628543.1 | 1171929.3731 | 2628544.9368 | 1171930.9122
1 | 2628413.0914 | 1171882.0556 | 2628424.4042 | 1171888.4234 | 2628439.0824 | 1171888.3149 | 2628451.3496 | 1171898.2669 | 2628469.1952 | 1171893.1265 | 2628486.6313 | 1171896.9444 | 2628505.9086 | 1171897.9695 | 2628527.211 | 1171915.4906 | 2628537.1813 | 1171922.6527 | 2628540.2636 | 1171926.1525
2 | 2628544.9368 | 1171930.9122 | 2628549.9184 | 1171935.0862
3 | 2628457.4533 | 1171827.1482 | 2628444.9488 | 1171830.1462 | 2628441.4477 | 1171831.3524 | 2628440.0509 | 1171832.3464 | 2628438.5505 | 1171835.8522 | 2628438.6534 | 1171838.3539 | 2628440.6502 | 1171847.9461 | 2628440.5495 | 1171851.4474 | 2628439.9502 | 1171855.2465 | 2628439.0497 | 1171858.0548 | 2628437.3514 | 1171861.3485 | 2628434.8523 | 1171864.1492 | 2628431.8513 | 1171866.3473 | 2628422.2477 | 1171870.5485 | 2628418.0497 | 1171873.5524 | 2628416.2495 | 1171875.7561 | 2628413.9518 | 1171879.6473 | 2628413.0914 | 1171882.0556
4 | 2628360.2096 | 1171828.3785 | 2628366.2516 | 1171833.3428 | 2628372.4611 | 1171840.0756 | 2628380.9821 | 1171851.3549 | 2628385.3913 | 1171863.5486 | 2628389.0346 | 1171874.3491 | 2628394.8185 | 1171883.7368 | 2628402.315 | 1171885.1952 | 2628409.0528 | 1171883.704 | 2628409.7128 | 1171886.4641 | 2628411.3766 | 1171885.6159 | 2628413.0914 | 1171882.0556
5 | 2628549.9184 | 1171935.0862 | 2628549.9184 | 1171935.0862 | 2628568.1291 | 1171958.4488
6 | 2628360.2096 | 1171828.3785 | 2628364.7541 | 1171821.652 | 2628366.7487 | 1171817.148 | 2628367.8381 | 1171813.1955 | 2628368.453 | 1171810.9528 | 2628370.0488 | 1171805.0462 | 2628370.6386 | 1171803.2481 | 2628371.5544 | 1171800.451 | 2628373.5476 | 1171796.2471 | 2628376.0479 | 1171791.5565 | 2628380.7539 | 1171784.6529 | 2628382.5526 | 1171781.1485 | 2628386.1476 | 1171766.5469
7 | 2628569.3526 | 1171960.0184 | 2628568.1291 | 1171958.4488
8 | 2628409.6887 | 1171775.029 | 2628399.3525 | 1171770.7558 | 2628392.8538 | 1171768.5462 | 2628386.1476 | 1171766.5469
9 | 2628404.7834 | 1171793.3597 | 2628405.6537 | 1171788.8504 | 2628407.7504 | 1171780.556 | 2628409.6887 | 1171775.029
10 | 2628404.7834 | 1171793.3597 | 2628410.0496 | 1171794.1517 | 2628424.647 | 1171788.5511 | 2628430.851 | 1171786.7461 | 2628438.8496 | 1171785.55 | 2628459.108 | 1171784.2249
11 | 2628409.6887 | 1171775.029 | 2628410.4486 | 1171772.8537 | 2628413.0484 | 1171768.1525 | 2628415.9509 | 1171764.153 | 2628419.1484 | 1171760.8553 | 2628424.053 | 1171757.2544 | 2628430.8478 | 1171753.4513 | 2628465.748 | 1171735.9518 | 2628471.7536 | 1171732.4562 | 2628474.7664 | 1171730.3302
12 | 2628459.108 | 1171784.2249 | 2628459.9284 | 1171784.1712 | 2628471.3431 | 1171783.9255
13 | 2628584.4108 | 1171974.2257 | 2628582.4512 | 1171972.949 | 2628575.1501 | 1171967.456 | 2628569.3526 | 1171960.0184
14 | 2628495.5329 | 1171684.1012 | 2628495.7481 | 1171688.8475 | 2628495.2522 | 1171696.6491 | 2628493.6486 | 1171704.1565 | 2628491.2534 | 1171710.8486 | 2628485.1481 | 1171720.847 | 2628480.9496 | 1171725.5518 | 2628476.151 | 1171729.3532 | 2628474.7664 | 1171730.3302
15 | 2628471.3431 | 1171783.9255 | 2628473.4758 | 1171783.8796 | 2628477.2753 | 1171784.2756 | 2628479.4751 | 1171784.9308 | 2628481.2743 | 1171786.1733 | 2628483.026 | 1171789.3721
16 | 2628584.4108 | 1171974.2257 | 2628588.8534 | 1171968.0547 | 2628596.8536 | 1171960.0553 | 2628608.9509 | 1171949.3518
17 | 2628584.4108 | 1171974.2257 | 2628588.1471 | 1171976.6558 | 2628600.3635 | 1171984.0717
18 | 2628631.3669 | 1172004.3645 | 2628627.1478 | 1172000.5536 | 2628623.5491 | 1171998.1463 | 2628600.3635 | 1171984.0717
19 | 2628631.3669 | 1172004.3645 | 2628635.0487 | 1172000.5467 | 2628639.6376 | 1171994.6824
20 | 2628631.3669 | 1172004.3645 | 2628626.7473 | 1172009.1561 | 2628622.2496 | 1172014.4184
21 | 2628653.2517 | 1171979.7561 | 2628649.0542 | 1171982.6487 | 2628639.6376 | 1171994.6824
22 | 2628614.0814 | 1172023.7034 | 2628616.1487 | 1172021.5564 | 2628622.2496 | 1172014.4184
23 | 2628653.2517 | 1171979.7561 | 2628660.9514 | 1171978.6477 | 2628666.8152 | 1171977.1125
24 | 2628653.2517 | 1171979.7561 | 2628652.352 | 1171975.9498 | 2628651.7534 | 1171969.955 | 2628651.7534 | 1171969.955
25 | 2628583.1482 | 1172067.6565 | 2628584.4503 | 1172062.4489 | 2628587.9501 | 1172053.4498 | 2628589.6489 | 1172050.0562 | 2628592.9511 | 1172045.6474 | 2628614.0814 | 1172023.7034
26 | 2628547.5535 | 1172065.8532 | 2628549.8537 | 1172064.6524 | 2628552.7539 | 1172064.3549 | 2628560.804 | 1172065.1268 | 2628583.1482 | 1172067.6565
27 | 2628584.4479 | 1172006.6536 | 2628568.3508 | 1172028.555 | 2628563.9508 | 1172033.848 | 2628554.7514 | 1172043.1535 | 2628552.2471 | 1172047.0547 | 2628549.6512 | 1172054.146 | 2628547.5535 | 1172065.8532
28 | 2628714.2538 | 1171888.3181 | 2628684.8505 | 1171915.0513 | 2628675.9472 | 1171924.7471 | 2628674.1498 | 1171927.9513 | 2628669.8491 | 1171939.6479 | 2628661.4526 | 1171955.3493 | 2628654.9514 | 1171961.7549 | 2628653.3495 | 1171964.0485 | 2628651.7534 | 1171969.955
29 | 2628714.2538 | 1171888.3181 | 2628743.1491 | 1171862.0468 | 2628756.9586 | 1171849.1599
30 | 2628845.2186 | 1171805.8358 | 2628843.9498 | 1171806.4564 | 2628841.9649 | 1171807.2695 | 2628826.9514 | 1171813.4563 | 2628821.9486 | 1171815.1554 | 2628796.9531 | 1171819.8492 | 2628789.4535 | 1171822.2478 | 2628783.2499 | 1171825.5532 | 2628778.7509 | 1171829.0557 | 2628771.653 | 1171835.4472 | 2628756.9586 | 1171849.1599
31 | 2628845.2186 | 1171805.8358 | 2628851.7726 | 1171802.6303
32 | 2628906.7373 | 1171790.7609 | 2628896.8299 | 1171792.8143 | 2628864.2974 | 1171796.5044 | 2628851.7726 | 1171802.6303
33 | 2628769.831 | 1171955.477 | 2628783.9535 | 1171958.1468 | 2628788.3495 | 1171958.5459 | 2628827.347 | 1171959.0551 | 2628840.2544 | 1171959.7507 | 2628843.6512 | 1171959.5558 | 2628847.4502 | 1171958.4512 | 2628862.5514 | 1171951.4534 | 2628865.3136 | 1171950.9387
34 | 2628887.2538 | 1171953.5508 | 2628881.1513 | 1171951.7539 | 2628873.2499 | 1171950.2486 | 2628870.0537 | 1171950.0553 | 2628865.3136 | 1171950.9387
35 | 2628906.7373 | 1171790.7609 | 2628909.9989 | 1171790.0873 | 2628922.1707 | 1171791.1241 | 2628927.4239 | 1171794.7043
36 | 2628887.2538 | 1171953.5508 | 2628888.0653 | 1171951.7983
37 | 2628887.2538 | 1171953.5508 | 2628883.2733 | 1171965.5832
38 | 2628927.4239 | 1171794.7043 | 2628928.2007 | 1171795.2338
39 | 2628934.91 | 1171799.801 | 2628931.6165 | 1171797.5618 | 2628928.2007 | 1171795.2338
40 | 2628945.7915 | 1171763.8126 | 2628944.9263 | 1171787.8319 | 2628935.1772 | 1171798.3237 | 2628934.91 | 1171799.801
41 | 2628934.91 | 1171799.801 | 2628932.8038 | 1171806.2462
42 | 2628945.7915 | 1171763.8126 | 2628941.8934 | 1171760.5826
43 | 2628945.7915 | 1171763.8126 | 2628990.8783 | 1171808.8196 | 2628992.7765 | 1171811.1113
44 | 2628932.8038 | 1171806.2462 | 2628932.7519 | 1171806.4051 | 2628932.8167 | 1171810.4186 | 2628934.1567 | 1171816.4726 | 2628935.6547 | 1171823.0721 | 2628939.4615 | 1171828.2931 | 2628941.8243 | 1171833.1958 | 2628942.9671 | 1171837.3146 | 2628943.2469 | 1171842.752 | 2628944.1474 | 1171873.3498 | 2628946.3092 | 1171880.286 | 2628950.8316 | 1171887.7894 | 2628952.9982 | 1171890.5457 | 2628956.5918 | 1171893.9981 | 2628960.3134 | 1171897.8513
45 | 2628939.773 | 1171758.8256 | 2628941.8934 | 1171760.5826
46 | 2628992.7765 | 1171811.1113 | 2629043.0823 | 1171871.8482 | 2629045.4674 | 1171877.2058
47 | 2628960.3134 | 1171897.8513 | 2628960.3134 | 1171897.8513 | 2628962.765 | 1171901.7763
48 | 2628939.773 | 1171758.8256 | 2628935.5147 | 1171747.2769 | 2628917.7031 | 1171738.8091 | 2628912.1959 | 1171732.4461
49 | 2628912.1959 | 1171732.4461 | 2628915.3934 | 1171722.9289
50 | 2628915.3934 | 1171722.9289 | 2628916.4096 | 1171719.9043 | 2628922.4682 | 1171701.1637
51 | 2629052.9052 | 1171893.9133 | 2629045.4674 | 1171877.2058
52 | 2628961.8549 | 1171909.5875 | 2628962.6454 | 1171905.9445 | 2628962.765 | 1171901.7763 | 2628962.765 | 1171901.7763
53 | 2628716.4135 | 1171635.4028 | 2628735.2052 | 1171645.3866 | 2628755.9752 | 1171660.7159 | 2628765.3253 | 1171664.8628
54 | 2628716.4135 | 1171635.4028 | 2628726.0825 | 1171633.6481 | 2628712.6057 | 1171625.5018 | 2628726.653 | 1171621.5224 | 2628713.3295 | 1171614.8887 | 2628709.4801 | 1171607.2998 | 2628712.5799 | 1171595.6864 | 2628708.854 | 1171589.4543
55 | 2629052.9052 | 1171893.9133 | 2629053.8482 | 1171896.0317
56 | 2628961.2344 | 1171914.6422 | 2628961.7224 | 1171910.1978 | 2628961.8549 | 1171909.5875
57 | 2628878.5915 | 1171893.4754 | 2628889.8084 | 1171897.8456 | 2628901.1853 | 1171901.9135 | 2628912.3061 | 1171903.5678 | 2628935.6364 | 1171903.1464 | 2628944.0853 | 1171903.7207 | 2628947.878 | 1171905.6096
58 | 2628875.2192 | 1171892.1615 | 2628878.5915 | 1171893.4754
59 | 2628961.2344 | 1171914.6422 | 2628953.8445 | 1171908.5813 | 2628947.878 | 1171905.6096
60 | 2628959.899 | 1171926.7086 | 2628961.2344 | 1171914.6422
61 | 2628941.9556 | 1171928.2564 | 2628947.5521 | 1171927.1494 | 2628957.1539 | 1171926.5509 | 2628959.899 | 1171926.7086
62 | 2628959.899 | 1171926.7086 | 2628967.6501 | 1171927.6464 | 2628991.4537 | 1171933.7531 | 2629024.032 | 1171944.948
63 | 2628941.9556 | 1171928.2564 | 2628934.859 | 1171926.3991 | 2628929.7653 | 1171924.7737 | 2628925.479 | 1171923.8082 | 2628922.2744 | 1171922.1919
64 | 2628909.3477 | 1171935.0475 | 2628914.4493 | 1171933.449 | 2628920.5514 | 1171932.1554 | 2628941.9556 | 1171928.2564
65 | 2628962.0476 | 1171937.947 | 2628952.3542 | 1171932.1529 | 2628947.2479 | 1171929.9494 | 2628941.9556 | 1171928.2564
66 | 2629059.5493 | 1171954.2478 | 2629054.1508 | 1171953.9549 | 2629048.5493 | 1171952.9496 | 2629040.0485 | 1171950.4517 | 2629024.032 | 1171944.948
67 | 2628909.3477 | 1171935.0475 | 2628901.0024 | 1171932.0058 | 2628896.4834 | 1171930.1498 | 2628889.9547 | 1171929.4848 | 2628884.1329 | 1171929.7347
68 | 2628909.3477 | 1171935.0475 | 2628905.0491 | 1171936.6499 | 2628899.7515 | 1171939.248 | 2628895.6541 | 1171941.9519 | 2628892.4503 | 1171944.9492 | 2628890.049 | 1171948.0503 | 2628888.0653 | 1171951.7983
69 | 2628962.0476 | 1171937.947 | 2628967.6533 | 1171942.8542 | 2628970.9536 | 1171946.85
70 | 2629059.5493 | 1171954.2478 | 2629064.2995 | 1171958.8954 | 2629069.233 | 1171963.5994 | 2629072.7084 | 1171966.1509 | 2629074.9837 | 1171966.9623
71 | 2629059.5493 | 1171954.2478 | 2629066.5487 | 1171954.0482
72 | 2629131.4272 | 1171969.9059 | 2629140.5506 | 1171970.9483 | 2629144.3365 | 1171971.1803
73 | 2629131.4272 | 1171969.9059 | 2629129.2842 | 1171969.661
74 | 2629144.3365 | 1171971.1803 | 2629149.2214 | 1171971.4795 | 2629161.1124 | 1171972.2074
75 | 2629066.5487 | 1171954.0482 | 2629081.5485 | 1171952.2531 | 2629087.4488 | 1171953.1488 | 2629091.8524 | 1171955.1489 | 2629101.3524 | 1171961.3536 | 2629106.4486 | 1171964.0463 | 2629116.3518 | 1171967.5516 | 2629121.3481 | 1171968.7542 | 2629129.2842 | 1171969.661
76 | 2629175.0418 | 1171973.2612 | 2629168.3524 | 1171972.6506 | 2629161.1124 | 1171972.2074
77 | 2629066.5487 | 1171954.0482 | 2629065.1329 | 1171952.6184 | 2629060.9826 | 1171950.4528 | 2629056.8366 | 1171948.9654 | 2629053.089 | 1171947.3464 | 2629051.6252 | 1171944.7936 | 2629051.9116 | 1171940.9263
78 | 2629175.0418 | 1171973.2612 | 2629179.5891 | 1171973.6756
79 | 2629175.0418 | 1171973.2612 | 2629190.9496 | 1171995.5498 | 2629197.0512 | 1172002.2495 | 2629198.633 | 1172003.7816
80 | 2629179.5891 | 1171973.6756 | 2629188.0539 | 1171974.4471 | 2629195.5239 | 1171975.7379
81 | 2629210.995 | 1172012.1425 | 2629203.9525 | 1172008.0527 | 2629200.0506 | 1172005.1545 | 2629198.633 | 1172003.7816
82 | 2629213.296 | 1171980.9108 | 2629208.1486 | 1171978.7469 | 2629202.551 | 1171976.9521 | 2629195.5239 | 1171975.7379
83 | 2629210.995 | 1172012.1425 | 2629215.1489 | 1172014.5548 | 2629216.4505 | 1172015.8507 | 2629221.4524 | 1172030.049 | 2629222.6496 | 1172032.356 | 2629223.0033 | 1172032.7173
84 | 2628925.9499 | 1171962.6526 | 2628888.0653 | 1171951.7983
85 | 2629015.8728 | 1172087.5808 | 2629006.1808 | 1172083.59 | 2629005.5854 | 1172083.0802
86 | 2629015.8728 | 1172087.5808 | 2629021.9434 | 1172090.0805 | 2629034.2001 | 1172098.7329 | 2629035.1497 | 1172099.2271
87 | 2628987.6206 | 1172057.0914 | 2628988.121 | 1172058.6123 | 2628991.9454 | 1172066.5015 | 2628997.5889 | 1172076.2337 | 2629005.5854 | 1172083.0802
88 | 2629045.534 | 1172104.6306 | 2629035.1497 | 1172099.2271
89 | 2628987.6206 | 1172057.0914 | 2628984.3219 | 1172047.0658
90 | 2629045.534 | 1172104.6306 | 2629051.6023 | 1172107.7883 | 2629064.0699 | 1172110.7834 | 2629079.2658 | 1172120.5508 | 2629088.2172 | 1172130.1135
91 | 2628986.2843 | 1172033.849 | 2628985.7931 | 1172035.4003 | 2628984.3219 | 1172047.0658 | 2628984.3219 | 1172047.0658
92 | 2629088.2172 | 1172130.1135 | 2629097.1622 | 1172139.6694 | 2629108.5445 | 1172155.4596
93 | 2628990.5696 | 1172020.3155 | 2628986.2843 | 1172033.849
94 | 2629115.0385 | 1172164.4686 | 2629108.5445 | 1172155.4596
95 | 2629043.5518 | 1172048.5523 | 2629014.7488 | 1172037.2519 | 2629004.0537 | 1172031.4529 | 2628998.8539 | 1172028.0483 | 2628991.7535 | 1172022.2556 | 2628990.5696 | 1172020.3155
96 | 2628990.5696 | 1172020.3155 | 2628989.7502 | 1172018.9553 | 2628985.8517 | 1172010.5545 | 2628983.7476 | 1172007.5539 | 2628980.9536 | 1172004.8502 | 2628977.8108 | 1172003.1119
97 | 2629115.0385 | 1172164.4686 | 2629129.5521 | 1172185.5831 | 2629144.6835 | 1172207.2939
98 | 2629115.0385 | 1172164.4686 | 2629116.3366 | 1172168.0768 | 2629117.0073 | 1172173.2827 | 2629112.5075 | 1172180.1422 | 2629097.8915 | 1172195.9907 | 2629087.0874 | 1172211.1907
99 | 2628904.3375 | 1172012.9364 | 2628894.9518 | 1172018.0543 | 2628887.4326 | 1172023.2407
100 | 2628886.5489 | 1172023.8502 | 2628887.4326 | 1172023.2407
101 | 2628918.9183 | 1171999.7712 | 2628918.6477 | 1172001.9488 | 2628917.9512 | 1172003.6463 | 2628916.55 | 1172005.5516 | 2628913.8472 | 1172007.7509 | 2628904.3375 | 1172012.9364
102 | 2628867.7102 | 1171988.9307 | 2628873.55 | 1171994.4505 | 2628879.6496 | 1171998.4485 | 2628882.5498 | 1171999.752 | 2628888.2522 | 1172000.4464 | 2628911.6504 | 1172000.1475 | 2628918.9183 | 1171999.7712
103 | 2628918.9183 | 1171999.7712 | 2628929.1542 | 1171999.1877
104 | 2628867.7102 | 1171988.9307 | 2628877.8518 | 1171976.2507 | 2628880.6489 | 1171971.9508 | 2628882.9541 | 1171966.548 | 2628883.2733 | 1171965.5832
105 | 2628867.7102 | 1171988.9307 | 2628866.0484 | 1171990.946 | 2628847.6481 | 1172012.8467 | 2628841.2342 | 1172020.2932
106 | 2628929.1542 | 1171999.1877 | 2628942.0858 | 1171998.4506
107 | 2628841.2342 | 1172020.2932 | 2628820.2518 | 1172044.6539 | 2628818.6234 | 1172046.7445
108 | 2628977.8108 | 1172003.1119 | 2628974.4468 | 1172001.2503 | 2628962.8504 | 1171998.3485 | 2628954.3481 | 1171997.7517 | 2628942.0858 | 1171998.4506
109 | 2628787.8076 | 1172093.2271 | 2628788.6534 | 1172088.3473 | 2628789.9498 | 1172084.3514 | 2628795.2526 | 1172075.8502 | 2628803.3519 | 1172066.3508 | 2628818.6234 | 1172046.7445
110 | 2628977.8108 | 1172003.1119 | 2628982.7132 | 1172001.5792 | 2628990.251 | 1172000.7484 | 2628994.9861 | 1171999.0259 | 2628998.8526 | 1171996.5989 | 2629000.7935 | 1171993.8179 | 2629000.9193 | 1171993.4681
111 | 2628801.5473 | 1172106.1515 | 2628802.6974 | 1172104.3654
112 | 2628836.8473 | 1172078.4508 | 2628813.348 | 1172090.3554 | 2628808.6476 | 1172094.4461 | 2628806.6532 | 1172097.2491 | 2628804.252 | 1172101.9512 | 2628802.6974 | 1172104.3654
113 | 2628788.8233 | 1172124.7223 | 2628792.451 | 1172117.8473 | 2628795.2479 | 1172113.5473 | 2628801.5473 | 1172106.1515 | 2628801.5473 | 1172106.1515
114 | 2628788.8233 | 1172124.7223 | 2628788.9523 | 1172123.3556 | 2628787.0527 | 1172109.5505 | 2628786.451 | 1172101.0544 | 2628787.8076 | 1172093.2271
115 | 2628788.8233 | 1172124.7223 | 2628788.4527 | 1172128.6559 | 2628787.4512 | 1172133.3535 | 2628784.9501 | 1172139.7559 | 2628781 | 1172147.3585
116 | 2628781 | 1172147.3585 | 2628780.9515 | 1172147.4519 | 2628779.6802 | 1172149.4804
117 | 2628779.6802 | 1172149.4804 | 2628777.9326 | 1172152.2689
118 | 2628777.9326 | 1172152.2689 | 2628776.8695 | 1172153.9651
119 | 2629213.296 | 1171980.9108 | 2629218.85 | 1171983.2456 | 2629223.6492 | 1171985.648 | 2629230.1181 | 1171989.5195
120 | 2629224.6284 | 1172034.3778 | 2629223.0033 | 1172032.7173
121 | 2629175.1377 | 1172241.8885 | 2629171.1829 | 1172238.89 | 2629167.3967 | 1172235.8034 | 2629169.7388 | 1172230.7122 | 2629162.9526 | 1172226.4548 | 2629153.8346 | 1172218.84 | 2629149.3685 | 1172214.0159 | 2629144.6835 | 1172207.2939
122 | 2629086.4119 | 1172221.1926 | 2629087.0874 | 1172211.1907 | 2629087.0874 | 1172211.1907
123 | 2629175.1377 | 1172241.8885 | 2629177.1184 | 1172238.7854
124 | 2629175.1377 | 1172241.8885 | 2629176.2046 | 1172242.6941 | 2629181.8638 | 1172245.9344 | 2629191.0085 | 1172250.0122
125 | 2629086.4119 | 1172221.1926 | 2629086.4119 | 1172221.1926 | 2629090.6664 | 1172230.24 | 2629098.6443 | 1172250.6002 | 2629111.7205 | 1172268.328
126 | 2629111.7205 | 1172268.328 | 2629119.8511 | 1172279.3509 | 2629127.5512 | 1172289.1488
127 | 2629147.7746 | 1172336.1043 | 2629145.9487 | 1172330.9483 | 2629140.5537 | 1172320.5502 | 2629136.25 | 1172310.6465 | 2629132.8488 | 1172299.1463 | 2629131.3528 | 1172295.3482 | 2629127.5512 | 1172289.1488
128 | 2629315.1684 | 1172027.9424 | 2629317.8317 | 1172029.1257
129 | 2629321.2541 | 1172030.6461 | 2629317.8317 | 1172029.1257
130 | 2629307.2036 | 1172024.4039 | 2629315.1684 | 1172027.9424
131 | 2629321.2541 | 1172030.6461 | 2629330.5511 | 1172037.6506
132 | 2629321.2541 | 1172030.6461 | 2629335.5207 | 1172030.1932 | 2629332.7916 | 1172023.6321 | 2629326.5199 | 1172018.9325 | 2629316.5431 | 1172010.1682 | 2629309.84 | 1172006.089 | 2629303.3649 | 1172000.7436 | 2629298.2766 | 1171994.8713 | 2629289.2444 | 1171988.4574 | 2629282.967 | 1171984.9139 | 2629281.0545 | 1171983.4149
133 | 2629307.2036 | 1172024.4039 | 2629304.151 | 1172023.0478 | 2629282.3477 | 1172014.1644
134 | 2629330.5511 | 1172037.6506 | 2629329.7492 | 1172040.5482 | 2629329.5527 | 1172044.7494
135 | 2629281.0545 | 1171983.4149 | 2629275.0531 | 1171977.897
136 | 2629244.6812 | 1171996.9338 | 2629269.5492 | 1172008.9498 | 2629282.3477 | 1172014.1644
137 | 2629329.5527 | 1172044.7494 | 2629329.5527 | 1172044.7494 | 2629329.8522 | 1172047.6524 | 2629331.6483 | 1172051.0517 | 2629334.6504 | 1172054.9462 | 2629344.5469 | 1172064.4549 | 2629349.2833 | 1172068.5308
138 | 2629244.6812 | 1171996.9338 | 2629272.7535 | 1172026.3076
139 | 2629244.6812 | 1171996.9338 | 2629233.3499 | 1171991.4536 | 2629230.1971 | 1171989.5668
140 | 2629349.2833 | 1172068.5308 | 2629353.9532 | 1172072.5494 | 2629356.7814 | 1172074.6183
141 | 2629230.1971 | 1171989.5668 | 2629230.1181 | 1171989.5195
142 | 2629356.7814 | 1172074.6183 | 2629358.0534 | 1172075.5487 | 2629363.6649 | 1172078.9357
143 | 2628764.1813 | 1172174.2108 | 2628764.6585 | 1172173.4494
144 | 2628764.6585 | 1172173.4494 | 2628765.4598 | 1172172.1707
145 | 2628749.3102 | 1172197.9395 | 2628764.1813 | 1172174.2108
146 | 2628769.4903 | 1172165.7396 | 2628765.4598 | 1172172.1707
147 | 2628769.4903 | 1172165.7396 | 2628776.8695 | 1172153.9651
148 | 2629144.3738 | 1172337.1328 | 2629144.7262 | 1172337.0122 | 2629147.7746 | 1172336.1043
149 | 2629147.7746 | 1172336.1043 | 2629156.3683 | 1172333.5001 | 2629165.8735 | 1172330.6225 | 2629167.7501 | 1172330.0536 | 2629168.947 | 1172324.5454 | 2629170.354 | 1172319.8498 | 2629171.7496 | 1172315.9546 | 2629173.6533 | 1172312.9512 | 2629176.0526 | 1172310.2503
150 | 2629144.3738 | 1172337.1328 | 2629129.3756 | 1172340.3729 | 2629114.1261 | 1172343.3784 | 2629079.4077 | 1172347.0524
151 | 2629035.8244 | 1172364.4699 | 2629041.2542 | 1172361.0462 | 2629054.3519 | 1172353.8502 | 2629061.5469 | 1172351.0502 | 2629075.652 | 1172347.4499 | 2629079.4077 | 1172347.0524
152 | 2629019.7744 | 1172376.5232 | 2629033.1533 | 1172366.1542 | 2629035.8244 | 1172364.4699
153 | 2629005.4667 | 1172387.5169 | 2629008.6491 | 1172385.1457 | 2629019.7744 | 1172376.5232
154 | 2628994.4788 | 1172395.7039 | 2629005.4667 | 1172387.5169
155 | 2628994.4788 | 1172395.7039 | 2628985.5533 | 1172402.3543 | 2628979.5528 | 1172408.0505 | 2628976.5508 | 1172412.0492 | 2628971.5482 | 1172420.1515 | 2628971.1736 | 1172421.0025
156 | 2628971.1736 | 1172421.0025 | 2628969.5261 | 1172424.7453
157 | 2628961.0832 | 1172446.085 | 2628963.0487 | 1172439.754 | 2628965.2539 | 1172434.4508 | 2628969.5261 | 1172424.7453
158 | 2628310.0095 | 1171427.5143 | 2628306.7506 | 1171432.4459 | 2628306.2502 | 1171434.7558 | 2628306.6515 | 1171437.2479 | 2628308.0491 | 1171439.3555 | 2628313.7468 | 1171446.0525 | 2628315.9521 | 1171452.0548 | 2628315.9507 | 1171458.8472 | 2628315.54 | 1171462.6557
159 | 2628314.247 | 1171474.6472 | 2628315.54 | 1171462.6557
160 | 2628310.0095 | 1171427.5143 | 2628317.9502 | 1171435.4557 | 2628343.152 | 1171458.653 | 2628363.8514 | 1171476.3485 | 2628369.8505 | 1171480.7457 | 2628384.8538 | 1171489.7544 | 2628410.647 | 1171504.2503 | 2628425.3189 | 1171512.8883
161 | 2628489.3473 | 1171628.8531 | 2628488.2531 | 1171619.2541 | 2628485.3496 | 1171602.4539 | 2628481.3514 | 1171587.4495 | 2628478.747 | 1171580.1557 | 2628474.6487 | 1171570.1534 | 2628463.6541 | 1171548.1456 | 2628456.0509 | 1171536.8483 | 2628451.6538 | 1171531.7471 | 2628447.0541 | 1171527.4565 | 2628442.0471 | 1171523.553 | 2628431.5474 | 1171516.5553 | 2628425.3189 | 1171512.8883
162 | 2628489.3473 | 1171628.8531 | 2628532.6445 | 1171621.5323
163 | 2628489.3473 | 1171628.8531 | 2628490.1004 | 1171634.5595 | 2628493.9544 | 1171663.8484 | 2628495.2495 | 1171677.8506 | 2628495.5013 | 1171683.4033
164 | 2628532.6445 | 1171621.5323 | 2628553.5813 | 1171617.9854
165 | 2628532.6445 | 1171621.5323 | 2628562.8985 | 1171630.7139 | 2628574.4518 | 1171633.0235
166 | 2628495.5013 | 1171683.4033 | 2628495.5329 | 1171684.1012
167 | 2628553.5813 | 1171617.9854 | 2628569.7489 | 1171615.2496 | 2628589.6486 | 1171612.654 | 2628606.4514 | 1171609.8547 | 2628617.4482 | 1171607.15 | 2628628.3621 | 1171603.4823
168 | 2628653.9753 | 1171592.2314 | 2628637.2475 | 1171599.9517 | 2628629.3538 | 1171603.1491 | 2628628.3621 | 1171603.4823
169 | 2628708.854 | 1171589.4543 | 2628705.9493 | 1171590.6521 | 2628702.6507 | 1171591.0477 | 2628699.8143 | 1171590.7563 | 2628692.5368 | 1171589.8322 | 2628674.552 | 1171587.0561 | 2628666.6486 | 1171587.452 | 2628661.9469 | 1171588.5524 | 2628653.9753 | 1171592.2314
170 | 2628708.854 | 1171589.4543 | 2628713.5509 | 1171586.1528 | 2628715.2538 | 1171583.5485 | 2628717.0541 | 1171578.1543 | 2628716.8543 | 1171570.3493 | 2628713.4591 | 1171547.5172
171 | 2628483.026 | 1171789.3721 | 2628483.026 | 1171789.3721 | 2628481.5252 | 1171801.0265 | 2628479.9265 | 1171804.2762

## bus_geodata
| x | y | coords
0 | 2628540.2636 | 1171926.1525
1 | 2628544.9368 | 1171930.9122
2 | 2628413.0914 | 1171882.0556
3 | 2628549.9184 | 1171935.0862
4 | 2628457.4533 | 1171827.1482
5 | 2628360.2096 | 1171828.3785
6 | 2628568.1291 | 1171958.4488
7 | 2628386.1476 | 1171766.5469
8 | 2628404.7834 | 1171793.3597
9 | 2628409.6887 | 1171775.029
10 | 2628459.108 | 1171784.2249
11 | 2628569.3526 | 1171960.0184
12 | 2628474.7664 | 1171730.3302
13 | 2628471.3431 | 1171783.9255
14 | 2628584.4108 | 1171974.2257
15 | 2628608.9509 | 1171949.3518
16 | 2628600.3635 | 1171984.0717
17 | 2628631.3669 | 1172004.3645
18 | 2628639.6376 | 1171994.6824
19 | 2628622.2496 | 1172014.4184
20 | 2628653.2517 | 1171979.7561
21 | 2628614.0814 | 1172023.7034
22 | 2628583.1482 | 1172067.6565
23 | 2628547.5535 | 1172065.8532
24 | 2628584.4479 | 1172006.6536
25 | 2628666.8152 | 1171977.1125
26 | 2628651.7534 | 1171969.955
27 | 2628714.2538 | 1171888.3181
28 | 2628756.9586 | 1171849.1599
29 | 2628845.2186 | 1171805.8359
30 | 2628851.7726 | 1171802.6303
31 | 2628769.831 | 1171955.477
32 | 2628865.3136 | 1171950.9387
33 | 2628906.7373 | 1171790.7609
34 | 2628887.2538 | 1171953.5508
35 | 2628928.2007 | 1171795.2338
36 | 2628927.4239 | 1171794.7043
37 | 2628934.91 | 1171799.801
38 | 2628945.7915 | 1171763.8126
39 | 2628932.8038 | 1171806.2462
40 | 2628941.8934 | 1171760.5826
41 | 2628992.7765 | 1171811.1113
42 | 2628960.3134 | 1171897.8513
43 | 2628939.773 | 1171758.8256
44 | 2628912.1959 | 1171732.4461
45 | 2628915.3934 | 1171722.9289
46 | 2629045.4674 | 1171877.2058
47 | 2628962.765 | 1171901.7763
48 | 2628765.3253 | 1171664.8628
49 | 2628716.4135 | 1171635.4028
50 | 2628922.4682 | 1171701.1637
51 | 2629052.9052 | 1171893.9133
52 | 2628961.8549 | 1171909.5875
53 | 2629053.8482 | 1171896.0317
54 | 2628878.5915 | 1171893.4754
55 | 2628947.878 | 1171905.6096
56 | 2628875.2192 | 1171892.1615
57 | 2628961.2344 | 1171914.6422
58 | 2628959.899 | 1171926.7086
59 | 2628941.9556 | 1171928.2564
60 | 2629024.032 | 1171944.948
61 | 2628922.2744 | 1171922.1919
62 | 2628909.3477 | 1171935.0475
63 | 2628962.0476 | 1171937.947
64 | 2629059.5493 | 1171954.2478
65 | 2629131.4272 | 1171969.9059
66 | 2629144.3365 | 1171971.1803
67 | 2629129.2842 | 1171969.661
68 | 2629161.1124 | 1171972.2074
69 | 2629066.5487 | 1171954.0482
70 | 2629175.0418 | 1171973.2612
71 | 2629051.9116 | 1171940.9263
72 | 2629179.5891 | 1171973.6756
73 | 2629198.633 | 1172003.7816
74 | 2629074.9837 | 1171966.9623
75 | 2629195.5239 | 1171975.7379
76 | 2629210.995 | 1172012.1425
77 | 2628884.1329 | 1171929.7347
78 | 2628888.0653 | 1171951.7983
79 | 2628970.9536 | 1171946.85
80 | 2629015.8728 | 1172087.5808
81 | 2629005.5854 | 1172083.0802
82 | 2629035.1497 | 1172099.2271
83 | 2628987.6206 | 1172057.0914
84 | 2629045.534 | 1172104.6306
85 | 2628984.3219 | 1172047.0658
86 | 2629088.2172 | 1172130.1135
87 | 2628986.2843 | 1172033.849
88 | 2629108.5445 | 1172155.4596
89 | 2628990.5696 | 1172020.3155
90 | 2629115.0385 | 1172164.4686
91 | 2628887.4326 | 1172023.2407
92 | 2628904.3375 | 1172012.9364
93 | 2628886.5489 | 1172023.8502
94 | 2628918.9183 | 1171999.7712
95 | 2628867.7102 | 1171988.9307
96 | 2628929.1542 | 1171999.1877
97 | 2628883.2733 | 1171965.5832
98 | 2628841.2342 | 1172020.2932
99 | 2628942.0858 | 1171998.4506
100 | 2628818.6234 | 1172046.7445
101 | 2628977.8108 | 1172003.1119
102 | 2628802.6974 | 1172104.3654
103 | 2628801.5473 | 1172106.1515
104 | 2628836.8473 | 1172078.4508
105 | 2628788.8233 | 1172124.7223
106 | 2628787.8076 | 1172093.2271
107 | 2628781 | 1172147.3585
108 | 2628779.6802 | 1172149.4804
109 | 2628777.9326 | 1172152.2689
110 | 2629213.296 | 1171980.9108
111 | 2629223.0033 | 1172032.7173
112 | 2629000.9193 | 1171993.4681
113 | 2629043.5518 | 1172048.5523
114 | 2629144.6835 | 1172207.2939
115 | 2629087.0874 | 1172211.1907
116 | 2629175.1377 | 1172241.8885
117 | 2629086.4119 | 1172221.1926
118 | 2629177.1184 | 1172238.7854
119 | 2629191.0085 | 1172250.0122
120 | 2629111.7205 | 1172268.328
121 | 2628925.9499 | 1171962.6526
122 | 2629127.5512 | 1172289.1488
123 | 2629317.8317 | 1172029.1257
124 | 2629315.1684 | 1172027.9424
125 | 2629321.2541 | 1172030.6461
126 | 2629307.2036 | 1172024.4039
127 | 2629330.5511 | 1172037.6506
128 | 2629281.0545 | 1171983.4149
129 | 2629282.3477 | 1172014.1644
130 | 2629329.5527 | 1172044.7494
131 | 2629275.0531 | 1171977.897
132 | 2629244.6812 | 1171996.9338
133 | 2629349.2833 | 1172068.5308
134 | 2629272.7535 | 1172026.3076
135 | 2629230.1971 | 1171989.5668
136 | 2629356.7814 | 1172074.6183
137 | 2629230.1181 | 1171989.5195
138 | 2629224.6284 | 1172034.3778
139 | 2629363.6649 | 1172078.9357
140 | 2628764.6585 | 1172173.4494
141 | 2628764.1813 | 1172174.2108
142 | 2628765.4598 | 1172172.1707
143 | 2628749.3102 | 1172197.9395
144 | 2628769.4903 | 1172165.7396
145 | 2628776.8695 | 1172153.9651
146 | 2629147.7746 | 1172336.1043
147 | 2629144.3738 | 1172337.1328
148 | 2629176.0526 | 1172310.2503
149 | 2629079.4077 | 1172347.0524
150 | 2629035.8244 | 1172364.4699
151 | 2629019.7744 | 1172376.5232
152 | 2629005.4667 | 1172387.5169
153 | 2628994.4788 | 1172395.7039
154 | 2628971.1736 | 1172421.0025
155 | 2628969.5261 | 1172424.7453
156 | 2628961.0832 | 1172446.085
157 | 2628315.54 | 1171462.6557
158 | 2628310.0095 | 1171427.5143
159 | 2628314.247 | 1171474.6472
160 | 2628425.3189 | 1171512.8883
161 | 2628489.3473 | 1171628.8531
162 | 2628532.6445 | 1171621.5323
163 | 2628495.5013 | 1171683.4033
164 | 2628553.5813 | 1171617.9854
165 | 2628574.4518 | 1171633.0235
166 | 2628495.5329 | 1171684.1012
167 | 2628628.3621 | 1171603.4823
168 | 2628653.9753 | 1171592.2314
169 | 2628708.854 | 1171589.4543
170 | 2628483.026 | 1171789.3721
171 | 2628479.9265 | 1171804.2762
172 | 2628713.4591 | 1171547.5172
173 | 2628918.9183 | 1171999.7712

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1