## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_576-15_1_3_node_21 | 0.4 | n |  | TRUE
1 | bus_LV_576-15_1_3_node_22 | 0.4 | n |  | TRUE
2 | bus_LV_576-15_1_3_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_576-15_1_3_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_576-15_1_3_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_576-15_1_3_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_576-15_1_3_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_576-15_1_3_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_576-15_1_3_node_243 | 0.4 | n |  | TRUE
9 | bus_LV_576-15_1_3_node_46 | 0.4 | n |  | TRUE
10 | bus_LV_576-15_1_3_node_217 | 0.4 | n |  | TRUE
11 | bus_LV_576-15_1_3_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_576-15_1_3_node_230 | 0.4 | n |  | TRUE
13 | bus_LV_576-15_1_3_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_576-15_1_3_node_218 | 0.4 | n |  | TRUE
15 | bus_LV_576-15_1_3_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_576-15_1_3_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_576-15_1_3_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_576-15_1_3_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_576-15_1_3_node_253 | 0.4 | n |  | TRUE
20 | bus_LV_576-15_1_3_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_576-15_1_3_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_576-15_1_3_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_576-15_1_3_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_576-15_1_3_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_576-15_1_3_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_576-15_1_3_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_576-15_1_3_node_62 | 0.4 | n |  | TRUE
28 | bus_LV_576-15_1_3_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_576-15_1_3_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_576-15_1_3_node_95 | 0.4 | n |  | TRUE
31 | bus_LV_576-15_1_3_node_211 | 0.4 | n |  | TRUE
32 | bus_LV_576-15_1_3_node_61 | 0.4 | n |  | TRUE
33 | bus_LV_576-15_1_3_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_576-15_1_3_node_65 | 0.4 | n |  | TRUE
35 | bus_LV_576-15_1_3_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_576-15_1_3_node_210 | 0.4 | n |  | TRUE
37 | bus_LV_576-15_1_3_node_213 | 0.4 | n |  | TRUE
38 | bus_LV_576-15_1_3_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_576-15_1_3_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_576-15_1_3_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_576-15_1_3_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_576-15_1_3_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_576-15_1_3_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_576-15_1_3_node_48 | 0.4 | n |  | TRUE
45 | bus_LV_576-15_1_3_node_240 | 0.4 | n |  | TRUE
46 | bus_LV_576-15_1_3_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_576-15_1_3_node_238 | 0.4 | n |  | TRUE
48 | bus_LV_576-15_1_3_node_239 | 0.4 | n |  | TRUE
49 | bus_LV_576-15_1_3_node_244 | 0.4 | n |  | TRUE
50 | bus_LV_576-15_1_3_node_224 | 0.4 | n |  | TRUE
51 | bus_LV_576-15_1_3_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_576-15_1_3_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_576-15_1_3_node_53 | 0.4 | n |  | TRUE
54 | bus_LV_576-15_1_3_node_241 | 0.4 | n |  | TRUE
55 | bus_LV_576-15_1_3_node_237 | 0.4 | n |  | TRUE
56 | bus_LV_576-15_1_3_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_576-15_1_3_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_576-15_1_3_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_576-15_1_3_node_228 | 0.4 | n |  | TRUE
60 | bus_LV_576-15_1_3_node_232 | 0.4 | n |  | TRUE
61 | bus_LV_576-15_1_3_node_117 | 0.4 | n |  | TRUE
62 | bus_LV_576-15_1_3_node_231 | 0.4 | n |  | TRUE
63 | bus_LV_576-15_1_3_node_223 | 0.4 | n |  | TRUE
64 | bus_LV_576-15_1_3_node_233 | 0.4 | n |  | TRUE
65 | bus_LV_576-15_1_3_node_115 | 0.4 | n |  | TRUE
66 | bus_LV_576-15_1_3_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_576-15_1_3_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_576-15_1_3_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_576-15_1_3_node_97 | 0.4 | n |  | TRUE
70 | bus_LV_576-15_1_3_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_576-15_1_3_node_96 | 0.4 | n |  | TRUE
72 | bus_LV_576-15_1_3_node_196 | 0.4 | n |  | TRUE
73 | bus_LV_576-15_1_3_node_198 | 0.4 | n |  | TRUE
74 | bus_LV_576-15_1_3_node_91 | 0.4 | n |  | TRUE
75 | bus_LV_576-15_1_3_node_90 | 0.4 | n |  | TRUE
76 | bus_LV_576-15_1_3_node_98 | 0.4 | n |  | TRUE
77 | bus_LV_576-15_1_3_node_99 | 0.4 | n |  | TRUE
78 | bus_LV_576-15_1_3_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_576-15_1_3_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_576-15_1_3_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_576-15_1_3_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_576-15_1_3_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_576-15_1_3_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_576-15_1_3_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_576-15_1_3_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_576-15_1_3_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_576-15_1_3_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_576-15_1_3_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_576-15_1_3_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_576-15_1_3_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_576-15_1_3_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_576-15_1_3_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_576-15_1_3_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_576-15_1_3_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_576-15_1_3_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_576-15_1_3_node_86 | 0.4 | n |  | TRUE
97 | bus_LV_576-15_1_3_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_576-15_1_3_node_89 | 0.4 | n |  | TRUE
99 | bus_LV_576-15_1_3_node_195 | 0.4 | n |  | TRUE
100 | bus_LV_576-15_1_3_node_188 | 0.4 | n |  | TRUE
101 | bus_LV_576-15_1_3_node_194 | 0.4 | n |  | TRUE
102 | bus_LV_576-15_1_3_node_197 | 0.4 | n |  | TRUE
103 | bus_LV_576-15_1_3_node_189 | 0.4 | n |  | TRUE
104 | bus_LV_576-15_1_3_node_187 | 0.4 | n |  | TRUE
105 | bus_LV_576-15_1_3_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_576-15_1_3_node_94 | 0.4 | n |  | TRUE
107 | bus_LV_576-15_1_3_node_209 | 0.4 | n |  | TRUE
108 | bus_LV_576-15_1_3_node_199 | 0.4 | n |  | TRUE
109 | bus_LV_576-15_1_3_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_576-15_1_3_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_576-15_1_3_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_576-15_1_3_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_576-15_1_3_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_576-15_1_3_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_576-15_1_3_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_576-15_1_3_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_576-15_1_3_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_576-15_1_3_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_576-15_1_3_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_576-15_1_3_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_576-15_1_3_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_576-15_1_3_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_576-15_1_3_node_215 | 0.4 | n |  | TRUE
124 | bus_LV_576-15_1_3_node_234 | 0.4 | n |  | TRUE
125 | bus_LV_576-15_1_3_node_236 | 0.4 | n |  | TRUE
126 | bus_LV_576-15_1_3_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_576-15_1_3_node_116 | 0.4 | n |  | TRUE
128 | bus_LV_576-15_1_3_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_576-15_1_3_node_119 | 0.4 | n |  | TRUE
130 | bus_LV_576-15_1_3_node_120 | 0.4 | n |  | TRUE
131 | bus_LV_576-15_1_3_node_149 | 0.4 | n |  | TRUE
132 | bus_LV_576-15_1_3_node_150 | 0.4 | n |  | TRUE
133 | bus_LV_576-15_1_3_node_165 | 0.4 | n |  | TRUE
134 | bus_LV_576-15_1_3_node_167 | 0.4 | n |  | TRUE
135 | bus_LV_576-15_1_3_node_169 | 0.4 | n |  | TRUE
136 | bus_LV_576-15_1_3_node_166 | 0.4 | n |  | TRUE
137 | bus_LV_576-15_1_3_node_168 | 0.4 | n |  | TRUE
138 | bus_LV_576-15_1_3_node_170 | 0.4 | n |  | TRUE
139 | bus_LV_576-15_1_3_node_171 | 0.4 | n |  | TRUE
140 | bus_LV_576-15_1_3_node_172 | 0.4 | n |  | TRUE
141 | bus_LV_576-15_1_3_node_173 | 0.4 | n |  | TRUE
142 | bus_LV_576-15_1_3_node_190 | 0.4 | n |  | TRUE
143 | bus_LV_576-15_1_3_node_193 | 0.4 | n |  | TRUE
144 | bus_LV_576-15_1_3_node_191 | 0.4 | n |  | TRUE
145 | bus_LV_576-15_1_3_node_185 | 0.4 | n |  | TRUE
146 | bus_LV_576-15_1_3_node_183 | 0.4 | n |  | TRUE
147 | bus_LV_576-15_1_3_node_254 | 0.4 | n |  | TRUE
148 | bus_LV_576-15_1_3_node_186 | 0.4 | n |  | TRUE
149 | bus_LV_576-15_1_3_node_200 | 0.4 | n |  | TRUE
150 | bus_LV_576-15_1_3_node_202 | 0.4 | n |  | TRUE
151 | bus_LV_576-15_1_3_node_203 | 0.4 | n |  | TRUE
152 | bus_LV_576-15_1_3_node_204 | 0.4 | n |  | TRUE
153 | bus_LV_576-15_1_3_node_205 | 0.4 | n |  | TRUE
154 | bus_LV_576-15_1_3_node_207 | 0.4 | n |  | TRUE
155 | bus_LV_576-15_1_3_node_235 | 0.4 | n |  | TRUE
156 | bus_LV_576-15_1_3_node_208 | 0.4 | n |  | TRUE
157 | bus_LV_576-15_1_3_node_214 | 0.4 | n |  | TRUE
158 | bus_LV_576-15_1_3_node_212 | 0.4 | n |  | TRUE
159 | bus_LV_576-15_1_3_node_216 | 0.4 | n |  | TRUE
160 | bus_LV_576-15_1_3_node_222 | 0.4 | n |  | TRUE
161 | bus_LV_576-15_1_3_node_226 | 0.4 | n |  | TRUE
162 | bus_LV_576-15_1_3_node_220 | 0.4 | n |  | TRUE
163 | bus_LV_576-15_1_3_node_227 | 0.4 | n |  | TRUE
164 | bus_LV_576-15_1_3_node_219 | 0.4 | n |  | TRUE
165 | bus_LV_576-15_1_3_node_221 | 0.4 | n |  | TRUE
166 | bus_LV_576-15_1_3_node_225 | 0.4 | n |  | TRUE
167 | bus_LV_576-15_1_3_node_229 | 0.4 | n |  | TRUE
168 | bus_LV_576-15_1_3_node_242 | 0.4 | n |  | TRUE
169 | bus_MV_195_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_576-15_1_3_load_21 | 0 | 0.00078687 | 0.00019721 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_576-15_1_3_load_24 | 3 | 0.00039792 | 9.9728e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_576-15_1_3_load_25 | 4 | 0.0052621 | 0.0013188 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_576-15_1_3_load_28 | 6 | 0.00042316 | 0.00010605 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_576-15_1_3_load_243 | 8 | 0.0034283 | 0.00085921 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_576-15_1_3_load_217 | 10 | 0.0018882 | 0.00047323 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_576-15_1_3_load_230 | 12 | 0.0028585 | 0.0007164 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_576-15_1_3_load_218 | 14 | 0.0021615 | 0.00054172 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_576-15_1_3_load_31 | 16 | 0.00066113 | 0.0001657 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_576-15_1_3_load_40 | 17 | 0.00037334 | 9.3568e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_576-15_1_3_load_32 | 18 | 0.00059956 | 0.00015026 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_576-15_1_3_load_253 | 19 | 0.00037105 | 9.2995e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_576-15_1_3_load_37 | 23 | 0.0028211 | 0.00070704 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_576-15_1_3_load_39 | 26 | 0.00090628 | 0.00022714 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_576-15_1_3_load_63 | 28 | 0.0021813 | 0.00054668 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_576-15_1_3_load_60 | 29 | 0.0010325 | 0.00025876 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_576-15_1_3_load_211 | 31 | 0.0014846 | 0.00037208 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_576-15_1_3_load_61 | 32 | 0.0014801 | 0.00037096 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_576-15_1_3_load_64 | 33 | 0.0038824 | 0.00097302 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_576-15_1_3_load_58 | 35 | 0.0016623 | 0.0004166 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_576-15_1_3_load_210 | 36 | 0.0016585 | 0.00041565 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_576-15_1_3_load_59 | 38 | 0.0016123 | 0.00040409 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_576-15_1_3_load_42 | 39 | 0.0011101 | 0.00027822 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_576-15_1_3_load_45 | 41 | 0.0016206 | 0.00040617 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_576-15_1_3_load_47 | 42 | 0.0012348 | 0.00030947 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_576-15_1_3_load_240 | 45 | 0.0015152 | 0.00037975 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_576-15_1_3_load_238 | 47 | 0.0011838 | 0.00029668 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_576-15_1_3_load_239 | 48 | 0.00078496 | 0.00019673 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_576-15_1_3_load_244 | 49 | 0.0011325 | 0.00028382 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_576-15_1_3_load_53 | 53 | 0.0037824 | 0.00094796 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_576-15_1_3_load_241 | 54 | 0.0012873 | 0.00032263 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_576-15_1_3_load_237 | 55 | 0.0021136 | 0.00052971 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_576-15_1_3_load_55 | 57 | 0.0020235 | 0.00050713 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_576-15_1_3_load_56 | 58 | 0.001749 | 0.00043834 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_576-15_1_3_load_228 | 59 | 0.0042347 | 0.0010613 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_576-15_1_3_load_232 | 60 | 0.0042419 | 0.0010631 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_576-15_1_3_load_117 | 61 | 0.0024632 | 0.00061734 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_576-15_1_3_load_231 | 62 | 0.0066263 | 0.0016607 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_576-15_1_3_load_233 | 64 | 0.0028444 | 0.00071287 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_576-15_1_3_load_115 | 65 | 0.0012959 | 0.00032478 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_576-15_1_3_load_57 | 66 | 0.0015847 | 0.00039716 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_576-15_1_3_load_66 | 67 | 0.0021969 | 0.0005506 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_576-15_1_3_load_78 | 70 | 0.00094492 | 0.00023682 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_576-15_1_3_load_198 | 73 | 0.00041447 | 0.00010388 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_576-15_1_3_load_91 | 74 | 0.00060336 | 0.00015122 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_576-15_1_3_load_98 | 76 | 0.0019712 | 0.00049403 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_576-15_1_3_load_99 | 77 | 0.0010231 | 0.00025641 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_576-15_1_3_load_69 | 79 | 0.00018995 | 4.7606e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_576-15_1_3_load_72 | 81 | 0.00072289 | 0.00018117 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_576-15_1_3_load_73 | 82 | 0.0011914 | 0.00029859 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_576-15_1_3_load_77 | 86 | 0.00016672 | 4.1785e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_576-15_1_3_load_79 | 87 | 0.00055836 | 0.00013994 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_576-15_1_3_load_80 | 88 | 0.0038036 | 0.00095326 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_576-15_1_3_load_82 | 89 | 0.00024278 | 6.0847e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_576-15_1_3_load_83 | 90 | 0.00038516 | 9.653e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_576-15_1_3_load_84 | 91 | 0.00015753 | 3.948e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_576-15_1_3_load_87 | 93 | 0.00015973 | 4.0033e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_576-15_1_3_load_85 | 94 | 0.000202 | 5.0626e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_576-15_1_3_load_89 | 98 | 0.00015609 | 3.912e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_576-15_1_3_load_195 | 99 | 0.00018424 | 4.6175e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_576-15_1_3_load_194 | 101 | 0.00024874 | 6.234e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_576-15_1_3_load_197 | 102 | 0.00023351 | 5.8523e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_576-15_1_3_load_189 | 103 | 0.00024733 | 6.1986e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_576-15_1_3_load_93 | 105 | 0.0013292 | 0.00033314 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_576-15_1_3_load_94 | 106 | 0.00095667 | 0.00023976 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_576-15_1_3_load_199 | 108 | 0.00023665 | 5.9311e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_576-15_1_3_load_103 | 110 | 0.00093692 | 0.00023481 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_576-15_1_3_load_100 | 111 | 0.0013102 | 0.00032837 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_576-15_1_3_load_102 | 112 | 0.0013287 | 0.000333 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_576-15_1_3_load_104 | 113 | 0.005319 | 0.0013331 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_576-15_1_3_load_105 | 114 | 0.0028771 | 0.00072106 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_576-15_1_3_load_107 | 116 | 0.0055555 | 0.0013923 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_576-15_1_3_load_108 | 117 | 0.0026548 | 0.00066536 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_576-15_1_3_load_109 | 118 | 0.002741 | 0.00068696 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_576-15_1_3_load_110 | 119 | 0.0017258 | 0.00043253 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_576-15_1_3_load_112 | 121 | 0.0026516 | 0.00066454 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_576-15_1_3_load_113 | 122 | 0.0015265 | 0.00038257 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_576-15_1_3_load_215 | 123 | 0.0022058 | 0.00055283 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_576-15_1_3_load_234 | 124 | 0.0017197 | 0.000431 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_576-15_1_3_load_114 | 126 | 0.0028148 | 0.00070547 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_576-15_1_3_load_119 | 129 | 0.0040494 | 0.0010149 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_576-15_1_3_load_120 | 130 | 0.0038708 | 0.00097011 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_576-15_1_3_load_149 | 131 | 0.00028403 | 7.1184e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_576-15_1_3_load_150 | 132 | 0.00022164 | 5.5548e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_576-15_1_3_load_165 | 133 | 0.00018766 | 4.7033e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_576-15_1_3_load_166 | 136 | 0.00024393 | 6.1135e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_576-15_1_3_load_172 | 140 | 0.00038952 | 9.7623e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_576-15_1_3_load_173 | 141 | 0.00061436 | 0.00015397 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_576-15_1_3_load_190 | 142 | 0.00067 | 0.00016792 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_576-15_1_3_load_191 | 144 | 0.00044046 | 0.00011039 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_576-15_1_3_load_185 | 145 | 0.0008217 | 0.00020594 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_576-15_1_3_load_183 | 146 | 0.00019796 | 4.9614e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_576-15_1_3_load_254 | 147 | 0.00025989 | 6.5134e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_576-15_1_3_load_186 | 148 | 0.00060112 | 0.00015066 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_576-15_1_3_load_200 | 149 | 0.00014167 | 3.5506e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_576-15_1_3_load_202 | 150 | 0.0019198 | 0.00048115 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_576-15_1_3_load_203 | 151 | 0.0033014 | 0.00082741 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_576-15_1_3_load_205 | 153 | 0.0018738 | 0.00046963 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_576-15_1_3_load_207 | 154 | 0.0025761 | 0.00064564 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_576-15_1_3_load_235 | 155 | 0.0014441 | 0.00036192 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_576-15_1_3_load_208 | 156 | 0.0027928 | 0.00069994 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_576-15_1_3_load_214 | 157 | 0.0028645 | 0.00071791 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_576-15_1_3_load_212 | 158 | 0.0023164 | 0.00058054 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_576-15_1_3_load_226 | 161 | 0.0033795 | 0.00084697 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_576-15_1_3_load_227 | 163 | 0.0013645 | 0.00034197 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_576-15_1_3_load_219 | 164 | 0.0018456 | 0.00046254 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_576-15_1_3_load_225 | 166 | 0.002183 | 0.00054711 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_576-15_1_3_load_229 | 167 | 0.0033521 | 0.00084011 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_576-15_1_3_load_242 | 168 | 0.0019546 | 0.00048987 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 158 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_576-15_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.012267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_576-15_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.006474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_576-15_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0061705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_576-15_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.043638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_576-15_1_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.042384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_576-15_1_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0058161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_576-15_1_3_line_6 | NAYY 4x150 SE | 5 | 10 | 0.033299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_576-15_1_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.094231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_576-15_1_3_line_8 | NAYY 4x150 SE | 6 | 11 | 0.016369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_576-15_1_3_line_9 | NAYY 4x150 SE | 7 | 8 | 0.025528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_576-15_1_3_line_10 | NAYY 4x150 SE | 7 | 9 | 0.034781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_576-15_1_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.029474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_576-15_1_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.063819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_576-15_1_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.010378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_576-15_1_3_line_14 | NAYY 4x150 SE | 11 | 15 | 0.067132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_576-15_1_3_line_15 | NAYY 4x150 SE | 11 | 16 | 0.0038655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_576-15_1_3_line_16 | NAYY 4x150 SE | 12 | 50 | 0.026019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_576-15_1_3_line_17 | NAYY 4x150 SE | 13 | 41 | 0.021085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_576-15_1_3_line_18 | NAYY 4x150 SE | 13 | 39 | 0.059201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_576-15_1_3_line_19 | NAYY 4x150 SE | 15 | 17 | 0.014712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_576-15_1_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.015522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_576-15_1_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.007009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_576-15_1_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.026115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_576-15_1_3_line_23 | NAYY 4x150 SE | 20 | 21 | 0.098181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_576-15_1_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.014014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_576-15_1_3_line_25 | NAYY 4x150 SE | 21 | 23 | 0.016388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_576-15_1_3_line_26 | NAYY 4x150 SE | 22 | 27 | 0.015382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_576-15_1_3_line_27 | NAYY 4x150 SE | 22 | 28 | 0.053183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_576-15_1_3_line_28 | NAYY 4x150 SE | 23 | 29 | 0.001951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_576-15_1_3_line_29 | NAYY 4x150 SE | 24 | 25 | 0.008337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_576-15_1_3_line_30 | NAYY 4x150 SE | 24 | 26 | 0.01432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_576-15_1_3_line_31 | NAYY 4x150 SE | 25 | 30 | 0.006397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_576-15_1_3_line_32 | NAYY 4x150 SE | 25 | 31 | 0.018826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_576-15_1_3_line_33 | NAYY 4x150 SE | 26 | 32 | 0.0079537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_576-15_1_3_line_34 | NAYY 4x150 SE | 27 | 33 | 0.0037176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_576-15_1_3_line_35 | NAYY 4x150 SE | 28 | 34 | 0.01803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_576-15_1_3_line_36 | NAYY 4x150 SE | 29 | 35 | 0.021508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_576-15_1_3_line_37 | NAYY 4x150 SE | 30 | 36 | 0.040246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_576-15_1_3_line_38 | NAYY 4x150 SE | 31 | 37 | 0.052792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_576-15_1_3_line_39 | NAYY 4x150 SE | 32 | 38 | 0.010053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_576-15_1_3_line_40 | NAYY 4x150 SE | 34 | 67 | 0.022806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_576-15_1_3_line_41 | NAYY 4x150 SE | 34 | 68 | 0.034176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_576-15_1_3_line_42 | NAYY 4x150 SE | 35 | 66 | 0.019346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_576-15_1_3_line_43 | NAYY 4x150 SE | 36 | 107 | 0.01858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_576-15_1_3_line_44 | NAYY 4x150 SE | 37 | 157 | 0.051922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_576-15_1_3_line_45 | NAYY 4x150 SE | 37 | 158 | 0.039682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_576-15_1_3_line_46 | NAYY 4x150 SE | 37 | 123 | 0.01656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_576-15_1_3_line_47 | NAYY 4x150 SE | 39 | 40 | 0.015745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_576-15_1_3_line_48 | NAYY 4x150 SE | 40 | 42 | 0.022462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_576-15_1_3_line_49 | NAYY 4x150 SE | 40 | 43 | 0.023163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_576-15_1_3_line_50 | NAYY 4x150 SE | 43 | 48 | 0.01171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_576-15_1_3_line_51 | NAYY 4x150 SE | 44 | 45 | 0.003098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_576-15_1_3_line_52 | NAYY 4x150 SE | 44 | 46 | 0.1127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_576-15_1_3_line_53 | NAYY 4x150 SE | 44 | 47 | 0.010657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_576-15_1_3_line_54 | NAYY 4x150 SE | 45 | 54 | 0.018785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_576-15_1_3_line_55 | NAYY 4x150 SE | 46 | 49 | 0.17368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_576-15_1_3_line_56 | NAYY 4x150 SE | 47 | 55 | 0.014554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_576-15_1_3_line_57 | NAYY 4x150 SE | 48 | 55 | 0.058386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_576-15_1_3_line_58 | NAYY 4x150 SE | 50 | 167 | 0.010805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_576-15_1_3_line_59 | NAYY 4x150 SE | 50 | 165 | 0.010745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_576-15_1_3_line_60 | NAYY 4x150 SE | 51 | 52 | 0.01868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_576-15_1_3_line_61 | NAYY 4x150 SE | 51 | 53 | 0.01879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_576-15_1_3_line_62 | NAYY 4x150 SE | 52 | 56 | 0.018847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_576-15_1_3_line_63 | NAYY 4x150 SE | 52 | 57 | 0.01296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_576-15_1_3_line_64 | NAYY 4x150 SE | 53 | 58 | 0.011252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_576-15_1_3_line_65 | NAYY 4x150 SE | 54 | 168 | 0.015915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_576-15_1_3_line_66 | NAYY 4x150 SE | 56 | 59 | 0.01365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_576-15_1_3_line_67 | NAYY 4x150 SE | 56 | 60 | 0.0061141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_576-15_1_3_line_68 | NAYY 4x150 SE | 57 | 61 | 0.044641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_576-15_1_3_line_69 | NAYY 4x150 SE | 58 | 62 | 0.010982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_576-15_1_3_line_70 | NAYY 4x150 SE | 59 | 63 | 0.061355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_576-15_1_3_line_71 | NAYY 4x150 SE | 60 | 64 | 0.014701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_576-15_1_3_line_72 | NAYY 4x150 SE | 61 | 65 | 0.011854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_576-15_1_3_line_73 | NAYY 4x150 SE | 63 | 163 | 0.015211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_576-15_1_3_line_74 | NAYY 4x150 SE | 63 | 159 | 0.020221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_576-15_1_3_line_75 | NAYY 4x150 SE | 65 | 126 | 0.034681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_576-15_1_3_line_76 | NAYY 4x150 SE | 68 | 69 | 0.039569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_576-15_1_3_line_77 | NAYY 4x150 SE | 68 | 70 | 0.046556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_576-15_1_3_line_78 | NAYY 4x150 SE | 69 | 76 | 0.015056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_576-15_1_3_line_79 | NAYY 4x150 SE | 69 | 77 | 0.0070808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_576-15_1_3_line_80 | NAYY 4x150 SE | 70 | 78 | 0.099346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_576-15_1_3_line_81 | NAYY 4x150 SE | 71 | 72 | 0.027285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_576-15_1_3_line_82 | NAYY 4x150 SE | 71 | 73 | 0.018149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_576-15_1_3_line_83 | NAYY 4x150 SE | 72 | 92 | 0.019983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_576-15_1_3_line_84 | NAYY 4x150 SE | 73 | 108 | 0.021344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_576-15_1_3_line_85 | NAYY 4x150 SE | 74 | 75 | 0.010866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_576-15_1_3_line_86 | NAYY 4x150 SE | 75 | 95 | 0.016566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_576-15_1_3_line_87 | NAYY 4x150 SE | 75 | 87 | 0.010323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_576-15_1_3_line_88 | NAYY 4x150 SE | 77 | 109 | 0.0062854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_576-15_1_3_line_89 | NAYY 4x150 SE | 78 | 84 | 0.083615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_576-15_1_3_line_90 | NAYY 4x150 SE | 78 | 85 | 0.008043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_576-15_1_3_line_91 | NAYY 4x150 SE | 78 | 86 | 0.033165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
92 | LV_576-15_1_3_line_92 | NAYY 4x150 SE | 78 | 79 | 0.031174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_576-15_1_3_line_93 | NAYY 4x150 SE | 79 | 80 | 0.0423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_576-15_1_3_line_94 | NAYY 4x150 SE | 80 | 81 | 0.02629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_576-15_1_3_line_95 | NAYY 4x150 SE | 80 | 82 | 0.015276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_576-15_1_3_line_96 | NAYY 4x150 SE | 80 | 83 | 0.077279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_576-15_1_3_line_97 | NAYY 4x150 SE | 83 | 87 | 0.012179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_576-15_1_3_line_98 | NAYY 4x150 SE | 84 | 88 | 0.048006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_576-15_1_3_line_99 | NAYY 4x150 SE | 85 | 89 | 0.004634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_576-15_1_3_line_100 | NAYY 4x150 SE | 85 | 90 | 0.05587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_576-15_1_3_line_101 | NAYY 4x150 SE | 86 | 91 | 0.015232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_576-15_1_3_line_102 | NAYY 4x150 SE | 91 | 94 | 0.079083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_576-15_1_3_line_103 | NAYY 4x150 SE | 92 | 93 | 0.0065625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_576-15_1_3_line_104 | NAYY 4x150 SE | 93 | 96 | 0.06623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_576-15_1_3_line_105 | NAYY 4x150 SE | 94 | 96 | 0.078385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_576-15_1_3_line_106 | NAYY 4x150 SE | 95 | 105 | 0.010136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_576-15_1_3_line_107 | NAYY 4x150 SE | 95 | 106 | 0.009864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_576-15_1_3_line_108 | NAYY 4x150 SE | 96 | 97 | 0.082093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_576-15_1_3_line_109 | NAYY 4x150 SE | 96 | 98 | 0.015647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_576-15_1_3_line_110 | NAYY 4x150 SE | 97 | 99 | 0.023727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_576-15_1_3_line_111 | NAYY 4x150 SE | 97 | 100 | 0.032581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_576-15_1_3_line_112 | NAYY 4x150 SE | 98 | 101 | 0.012558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_576-15_1_3_line_113 | NAYY 4x150 SE | 99 | 102 | 0.019695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_576-15_1_3_line_114 | NAYY 4x150 SE | 100 | 103 | 0.032291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_576-15_1_3_line_115 | NAYY 4x150 SE | 100 | 104 | 0.072907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_576-15_1_3_line_116 | NAYY 4x150 SE | 104 | 138 | 0.018078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
117 | LV_576-15_1_3_line_117 | NAYY 4x150 SE | 107 | 156 | 0.066393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_576-15_1_3_line_118 | NAYY 4x150 SE | 107 | 154 | 0.015896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_576-15_1_3_line_119 | NAYY 4x150 SE | 108 | 149 | 0.020139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_576-15_1_3_line_120 | NAYY 4x150 SE | 109 | 110 | 0.013016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_576-15_1_3_line_121 | NAYY 4x150 SE | 109 | 111 | 0.0042872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_576-15_1_3_line_122 | NAYY 4x150 SE | 111 | 112 | 0.020035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_576-15_1_3_line_123 | NAYY 4x150 SE | 113 | 114 | 0.007515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_576-15_1_3_line_124 | NAYY 4x150 SE | 113 | 115 | 0.0069476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_576-15_1_3_line_125 | NAYY 4x150 SE | 115 | 116 | 0.015829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_576-15_1_3_line_126 | NAYY 4x150 SE | 115 | 117 | 0.015226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_576-15_1_3_line_127 | NAYY 4x150 SE | 116 | 118 | 0.012678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_576-15_1_3_line_128 | NAYY 4x150 SE | 118 | 119 | 0.039249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_576-15_1_3_line_129 | NAYY 4x150 SE | 119 | 120 | 0.0068534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_576-15_1_3_line_130 | NAYY 4x150 SE | 120 | 121 | 0.015644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_576-15_1_3_line_131 | NAYY 4x150 SE | 120 | 122 | 0.012869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_576-15_1_3_line_132 | NAYY 4x150 SE | 121 | 123 | 0.00061606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_576-15_1_3_line_133 | NAYY 4x150 SE | 122 | 124 | 0.022857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_576-15_1_3_line_134 | NAYY 4x150 SE | 124 | 125 | 0.0076067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_576-15_1_3_line_135 | NAYY 4x150 SE | 125 | 155 | 0.019877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_576-15_1_3_line_136 | NAYY 4x150 SE | 126 | 127 | 0.021049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_576-15_1_3_line_137 | NAYY 4x150 SE | 127 | 128 | 0.024724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_576-15_1_3_line_138 | NAYY 4x150 SE | 128 | 129 | 0.006024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_576-15_1_3_line_139 | NAYY 4x150 SE | 128 | 130 | 0.006631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_576-15_1_3_line_140 | NAYY 4x150 SE | 131 | 132 | 0.026873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_576-15_1_3_line_141 | NAYY 4x150 SE | 132 | 133 | 0.14148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_576-15_1_3_line_142 | NAYY 4x150 SE | 133 | 136 | 0.12505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
143 | LV_576-15_1_3_line_143 | NAYY 4x150 SE | 133 | 134 | 0.068412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_576-15_1_3_line_144 | NAYY 4x150 SE | 134 | 135 | 0.074728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_576-15_1_3_line_145 | NAYY 4x150 SE | 135 | 140 | 0.020034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_576-15_1_3_line_146 | NAYY 4x150 SE | 135 | 141 | 0.12673 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_576-15_1_3_line_147 | NAYY 4x150 SE | 136 | 137 | 0.044775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
148 | LV_576-15_1_3_line_148 | NAYY 4x150 SE | 137 | 138 | 0.10927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
149 | LV_576-15_1_3_line_149 | NAYY 4x150 SE | 137 | 139 | 0.098961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_576-15_1_3_line_150 | NAYY 4x150 SE | 138 | 142 | 0.015942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_576-15_1_3_line_151 | NAYY 4x150 SE | 139 | 143 | 0.058451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_576-15_1_3_line_152 | NAYY 4x150 SE | 139 | 144 | 0.032068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_576-15_1_3_line_153 | NAYY 4x150 SE | 140 | 145 | 0.052542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_576-15_1_3_line_154 | NAYY 4x150 SE | 141 | 146 | 0.032516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_576-15_1_3_line_155 | NAYY 4x150 SE | 143 | 147 | 0.047993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_576-15_1_3_line_156 | NAYY 4x150 SE | 145 | 148 | 0.014658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_576-15_1_3_line_157 | NAYY 4x150 SE | 150 | 151 | 0.040528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_576-15_1_3_line_158 | NAYY 4x150 SE | 150 | 152 | 0.018188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_576-15_1_3_line_159 | NAYY 4x150 SE | 152 | 153 | 0.02269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_576-15_1_3_line_160 | NAYY 4x150 SE | 153 | 154 | 0.021279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
161 | LV_576-15_1_3_line_161 | NAYY 4x150 SE | 157 | 159 | 0.011865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
162 | LV_576-15_1_3_line_162 | NAYY 4x150 SE | 159 | 160 | 0.042645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
163 | LV_576-15_1_3_line_163 | NAYY 4x150 SE | 160 | 161 | 0.020538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
164 | LV_576-15_1_3_line_164 | NAYY 4x150 SE | 160 | 162 | 0.010282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
165 | LV_576-15_1_3_line_165 | NAYY 4x150 SE | 162 | 164 | 0.045612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
166 | LV_576-15_1_3_line_166 | NAYY 4x150 SE | 164 | 165 | 0.019538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
167 | LV_576-15_1_3_line_167 | NAYY 4x150 SE | 165 | 166 | 0.0164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_576-15_1_3_trafo_212 | 0.25 MVA 20/0.4 kV | 169 | 158 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2644865.0304 | 1163309.4513 | 2644868.8699 | 1163312.2703 | 2644875.0281 | 1163313.339 | 2644876.2733 | 1163313.1961
1 | 2644865.0304 | 1163309.4513 | 2644860.1575 | 1163313.7283
2 | 2644865.0304 | 1163309.4513 | 2644866.7768 | 1163303.5331
3 | 2644893.8684 | 1163338.3482 | 2644875.1717 | 1163332.0721 | 2644870.6221 | 1163328.9588 | 2644860.1575 | 1163313.7283
4 | 2644828.2996 | 1163335.4023 | 2644832.6483 | 1163336.7131 | 2644834.4999 | 1163332.8805 | 2644839.4276 | 1163324.3238 | 2644847.2354 | 1163317.8342 | 2644860.1575 | 1163313.7283
5 | 2644866.7768 | 1163303.5331 | 2644868.423 | 1163297.9549
6 | 2644828.2996 | 1163335.4023 | 2644795.9358 | 1163343.2383
7 | 2644828.2996 | 1163335.4023 | 2644832.6483 | 1163336.7131 | 2644855.0971 | 1163351.3659 | 2644856.5615 | 1163355.2788 | 2644856.5743 | 1163359.7257 | 2644847.8718 | 1163376.3028 | 2644840.3723 | 1163396.9355 | 2644837.3476 | 1163410.1754
8 | 2644874.6527 | 1163283.5651 | 2644875.2007 | 1163286.0927 | 2644869.384 | 1163294.6983 | 2644868.423 | 1163297.9549
9 | 2644855.9807 | 1163425.9781 | 2644847.795 | 1163414.3444 | 2644841.6529 | 1163411.1302 | 2644837.3476 | 1163410.1754
10 | 2644829.849 | 1163444.0484 | 2644830.9584 | 1163433.9514 | 2644837.3476 | 1163410.1754
11 | 2644829.849 | 1163444.0484 | 2644814.4194 | 1163441.3876 | 2644800.6429 | 1163440.332
12 | 2644829.849 | 1163444.0484 | 2644831.257 | 1163449.3728 | 2644841.6571 | 1163462.9574 | 2644849.3713 | 1163466.9391 | 2644854.4375 | 1163472.6799 | 2644853.943 | 1163480.4358 | 2644845.0486 | 1163495.0327
13 | 2644785.8492 | 1163345.6805 | 2644795.9358 | 1163343.2383
14 | 2644914.8687 | 1163234.0948 | 2644905.4845 | 1163241.3841 | 2644899.453 | 1163252.0669 | 2644896.3624 | 1163265.8956 | 2644890.9602 | 1163274.3819 | 2644883.3979 | 1163279.7839 | 2644874.6527 | 1163283.5651
15 | 2644874.6527 | 1163283.5651 | 2644870.8047 | 1163283.9314
16 | 2644778.3334 | 1163430.2465 | 2644780.0644 | 1163433.3499 | 2644783.2278 | 1163436.4417 | 2644787.2198 | 1163438.3169 | 2644792.242 | 1163439.6883 | 2644800.6429 | 1163440.332
17 | 2644828.1427 | 1163507.5355 | 2644839.5117 | 1163497.993 | 2644845.0486 | 1163495.0327
18 | 2644845.0486 | 1163495.0327 | 2644819.4023 | 1163533.3395 | 2644809.7691 | 1163542.22
19 | 2644914.8687 | 1163234.0948 | 2644917.0267 | 1163242.582 | 2644913.8752 | 1163247.6342
20 | 2644870.8047 | 1163283.9314 | 2644866.9644 | 1163284.297 | 2644857.8483 | 1163283.3953 | 2644855.5545 | 1163282.3923
21 | 2644910.1656 | 1163253.581 | 2644913.8752 | 1163247.6342
22 | 2644830.4478 | 1163276.3652 | 2644839.147 | 1163276.6857 | 2644848.8467 | 1163279.4595 | 2644855.5545 | 1163282.3923
23 | 2644830.4478 | 1163276.3652 | 2644829.6453 | 1163267.8992 | 2644832.3388 | 1163263.139 | 2644836.892 | 1163258.5928 | 2644861.666 | 1163252.1741 | 2644869.7101 | 1163245.8419 | 2644874.2276 | 1163237.8825 | 2644874.4806 | 1163205.0005
24 | 2644873.5661 | 1163191.0197 | 2644874.4806 | 1163205.0005
25 | 2644874.4806 | 1163205.0005 | 2644870.3078 | 1163205.7698 | 2644860.2184 | 1163212.5305
26 | 2644873.5661 | 1163191.0197 | 2644881.2698 | 1163188.2424 | 2644888.2544 | 1163186.3602
27 | 2644873.5661 | 1163191.0197 | 2644869.3882 | 1163184.2628 | 2644864.4296 | 1163177.4223 | 2644836.8361 | 1163153.089
28 | 2644858.5976 | 1163213.6165 | 2644860.2184 | 1163212.5305
29 | 2644658.9063 | 1163267.9631 | 2644665.8577 | 1163272.5949
30 | 2644665.8577 | 1163272.5949 | 2644671.5274 | 1163268.2903 | 2644678.6468 | 1163267.2082
31 | 2644658.9063 | 1163267.9631 | 2644652.7536 | 1163266.1499
32 | 2644658.9063 | 1163267.9631 | 2644655.1525 | 1163274.2163 | 2644653.3485 | 1163285.607
33 | 2644678.6468 | 1163267.2082 | 2644686.5102 | 1163266.0129
34 | 2644888.2544 | 1163186.3602 | 2644891.5073 | 1163184.5604
35 | 2644823.3129 | 1163141.1636 | 2644836.8361 | 1163153.089
36 | 2644858.5976 | 1163213.6165 | 2644852.817 | 1163217.49 | 2644838.5024 | 1163220.0934
37 | 2644652.7536 | 1163266.1499 | 2644650.2695 | 1163265.42 | 2644643.9099 | 1163265.684 | 2644613.2853 | 1163272.1113
38 | 2644651.8009 | 1163337.7246 | 2644648.3697 | 1163317.0439 | 2644653.3485 | 1163285.607
39 | 2644686.5102 | 1163266.0129 | 2644696.4494 | 1163264.5022
40 | 2644823.3129 | 1163141.1636 | 2644835.948 | 1163122.1589
41 | 2644796.4236 | 1163122.9984 | 2644800.9135 | 1163131.0693 | 2644810.7332 | 1163133.188 | 2644823.3129 | 1163141.1636
42 | 2644820.3578 | 1163226.6642 | 2644835.6124 | 1163220.619 | 2644838.5024 | 1163220.0934
43 | 2644595.1018 | 1163275.9275 | 2644613.2853 | 1163272.1113
44 | 2644651.8009 | 1163337.7246 | 2644659.2751 | 1163361.6926 | 2644662.3514 | 1163366.2178 | 2644677.3919 | 1163381.3626
45 | 2644651.8009 | 1163337.7246 | 2644677.7367 | 1163331.5695 | 2644690.2789 | 1163328.0541
46 | 2644651.8009 | 1163337.7246 | 2644642.3805 | 1163340.6785 | 2644635.7704 | 1163341.6888
47 | 2644798.193 | 1163552.8918 | 2644809.7691 | 1163542.22
48 | 2644798.193 | 1163552.8918 | 2644791.2447 | 1163550.9835 | 2644782.6022 | 1163549.2738 | 2644776.6655 | 1163546.7607
49 | 2644778.0581 | 1163562.9138 | 2644793.5514 | 1163558.0155 | 2644798.193 | 1163552.8918
50 | 2644778.0581 | 1163562.9138 | 2644767.1162 | 1163567.0838
51 | 2644689.7689 | 1163598.754 | 2644686.9202 | 1163599.9719
52 | 2644689.7689 | 1163598.754 | 2644694.0689 | 1163612.771 | 2644698.6704 | 1163647.0231 | 2644707.0876 | 1163664.606 | 2644713.9058 | 1163672.6608 | 2644723.3343 | 1163682.9919 | 2644729.5699 | 1163688.0186 | 2644736.6569 | 1163696.9982
53 | 2644689.7689 | 1163598.754 | 2644699.5651 | 1163594.5586
54 | 2644686.9202 | 1163599.9719 | 2644679.9797 | 1163602.9391 | 2644669.2328 | 1163606.2207
55 | 2644736.6569 | 1163696.9982 | 2644741.0229 | 1163686.6808 | 2644785.7481 | 1163625.6705 | 2644787.7605 | 1163622.8618 | 2644802.1274 | 1163603.6142 | 2644818.6759 | 1163581.4815 | 2644834.0659 | 1163567.8445 | 2644844.0152 | 1163564.806 | 2644844.772 | 1163564.7973
56 | 2644712.9436 | 1163588.8289 | 2644699.5651 | 1163594.5586
57 | 2644712.9436 | 1163588.8289 | 2644736.2566 | 1163578.8446 | 2644767.1162 | 1163567.0838
58 | 2644773.0726 | 1163420.8024 | 2644778.3334 | 1163430.2465
59 | 2644768.1431 | 1163433.7392 | 2644778.3334 | 1163430.2465
60 | 2644713.7474 | 1163510.586 | 2644701.8482 | 1163503.8941 | 2644696.9323 | 1163502.6459
61 | 2644713.7474 | 1163510.586 | 2644730.9368 | 1163502.998
62 | 2644696.9323 | 1163502.6459 | 2644696.4519 | 1163483.8102
63 | 2644696.9323 | 1163502.6459 | 2644684.4478 | 1163499.4737 | 2644684.3699 | 1163499.463
64 | 2644741.2304 | 1163498.4541 | 2644730.9368 | 1163502.998
65 | 2644654.0115 | 1163610.8686 | 2644669.2328 | 1163606.2207
66 | 2644696.4519 | 1163483.8102 | 2644694.5213 | 1163470.2977
67 | 2644696.4519 | 1163483.8102 | 2644699.9293 | 1163478.7813
68 | 2644684.3699 | 1163499.463 | 2644640.145 | 1163493.3853
69 | 2644751.2768 | 1163494.0192 | 2644741.2304 | 1163498.4541
70 | 2644685.8435 | 1163409.5593 | 2644694.5213 | 1163470.2977
71 | 2644708.2907 | 1163466.6892 | 2644699.9293 | 1163478.7813
72 | 2644628.3228 | 1163492.7013 | 2644637.2441 | 1163492.9867 | 2644640.145 | 1163493.3853
73 | 2644670.7673 | 1163411.8819 | 2644685.8435 | 1163409.5593
74 | 2644685.8435 | 1163409.5593 | 2644684.2691 | 1163392.5943 | 2644685.753 | 1163389.7816
75 | 2644628.3228 | 1163492.7013 | 2644603.7643 | 1163491.9156 | 2644593.887 | 1163489.7573
76 | 2644796.4236 | 1163122.9984 | 2644786.4495 | 1163120.0003 | 2644757.5116 | 1163115.6383
77 | 2644796.4236 | 1163122.9984 | 2644791.7583 | 1163107.6 | 2644789.758 | 1163077.199
78 | 2644749.3056 | 1163128.2728 | 2644757.5116 | 1163115.6383
79 | 2644757.5116 | 1163115.6383 | 2644750.748 | 1163113.5425
80 | 2644771.3459 | 1162981.8269 | 2644776.6802 | 1162985.5685 | 2644778.9408 | 1162990.5991 | 2644788.4966 | 1163058.0276 | 2644789.758 | 1163077.199
81 | 2644572.4034 | 1162897.8841 | 2644561.625 | 1162905.1748 | 2644557.5319 | 1162911.7035 | 2644555.7307 | 1162918.049
82 | 2644555.7307 | 1162918.049 | 2644550.7538 | 1162935.5018
83 | 2644592.2373 | 1162899.7876 | 2644582.7914 | 1162897.8055 | 2644572.4034 | 1162897.8841
84 | 2644550.7538 | 1162935.5018 | 2644550.084 | 1162937.8509 | 2644545.4567 | 1162945.1538 | 2644538.0811 | 1162952.28
85 | 2644662.9588 | 1163102.8514 | 2644653.4972 | 1163108.1951
86 | 2644669.9713 | 1163117.8557 | 2644667.0203 | 1163110.8746 | 2644662.9588 | 1163102.8514
87 | 2644662.9588 | 1163102.8514 | 2644672.439 | 1163098.7652
88 | 2644748.1479 | 1163107.8202 | 2644750.748 | 1163113.5425
89 | 2644771.3459 | 1162981.8269 | 2644768.0297 | 1162979.6678 | 2644762.684 | 1162978.494 | 2644707.3532 | 1162984.7972 | 2644697.9683 | 1162983.9159 | 2644689.5328 | 1162979.9956
90 | 2644778.2405 | 1162977.6538 | 2644771.3459 | 1162981.8269
91 | 2644771.3459 | 1162981.8269 | 2644768.7413 | 1162972.5805 | 2644758.7537 | 1162951.2434
92 | 2644771.3459 | 1162981.8269 | 2644773.039 | 1162986.9421 | 2644771.7561 | 1162996.6933 | 2644766.9837 | 1163004.9398 | 2644762.2419 | 1163009.2712
93 | 2644727.7948 | 1163033.6857 | 2644756.1552 | 1163014.8311 | 2644762.2419 | 1163009.2712
94 | 2644702.3877 | 1163040.6784 | 2644716.391 | 1163036.4802 | 2644727.7948 | 1163033.6857
95 | 2644742.7204 | 1163032.1736 | 2644734.2764 | 1163034.5677 | 2644727.7948 | 1163033.6857
96 | 2644683.6229 | 1163093.9446 | 2644700.0291 | 1163082.8384 | 2644705.6682 | 1163072.3637 | 2644710.6215 | 1163055.2249 | 2644715.0811 | 1163046.787 | 2644727.7948 | 1163033.6857
97 | 2644683.6229 | 1163093.9446 | 2644672.439 | 1163098.7652
98 | 2644692.7122 | 1163016.027 | 2644685.7554 | 1163012.0843 | 2644679.635 | 1163005.8912 | 2644676.8969 | 1162998.1002 | 2644678.0931 | 1162991.7502 | 2644681.6255 | 1162986.4514 | 2644685.7692 | 1162982.3912 | 2644689.5328 | 1162979.9956
99 | 2644778.7038 | 1162973.0437 | 2644778.2405 | 1162977.6538
100 | 2644778.2405 | 1162977.6538 | 2644787.2336 | 1162970.4503 | 2644791.1904 | 1162962.6979 | 2644791.0675 | 1162952.4583 | 2644788.0706 | 1162940.3519 | 2644782.5842 | 1162928.6418
101 | 2644748.6448 | 1162940.114 | 2644748.6448 | 1162940.114 | 2644757.2949 | 1162948.127 | 2644758.7537 | 1162951.2434
102 | 2644748.6448 | 1162940.114 | 2644741.0547 | 1162930.686 | 2644729.5344 | 1162914.0917 | 2644724.0865 | 1162910.1603 | 2644696.161 | 1162898.28 | 2644687.9404 | 1162893.1087
103 | 2644592.2373 | 1162899.7876 | 2644595.4862 | 1162894.0857
104 | 2644631.8545 | 1162839.1496 | 2644618.4397 | 1162853.8023 | 2644595.4862 | 1162894.0857
105 | 2644631.8545 | 1162839.1496 | 2644671.0528 | 1162882.4853 | 2644687.9404 | 1162893.1087
106 | 2644669.9713 | 1163117.8557 | 2644678.2464 | 1163123.7425
107 | 2644670.7179 | 1163127.6886 | 2644669.9713 | 1163117.8557
108 | 2644573.9373 | 1162781.8572 | 2644581.0032 | 1162785.6003 | 2644590.7592 | 1162792.265 | 2644617.9667 | 1162821.5263 | 2644631.8545 | 1162839.1496
109 | 2644631.8545 | 1162839.1496 | 2644644.2282 | 1162829.5724
110 | 2644573.9373 | 1162781.8572 | 2644570.4429 | 1162789.2574 | 2644559.8284 | 1162800.6119
111 | 2644573.9373 | 1162781.8572 | 2644569.8418 | 1162781.4711 | 2644560.3167 | 1162783.9574 | 2644551.2774 | 1162783.946 | 2644542.3655 | 1162780.1892
112 | 2644654.1592 | 1162821.8859 | 2644644.2282 | 1162829.5724
113 | 2644543.3256 | 1162809.8451 | 2644553.6715 | 1162807.1981 | 2644559.8284 | 1162800.6119
114 | 2644542.3655 | 1162780.1892 | 2644522.8713 | 1162799.6218 | 2644521.1394 | 1162804.062
115 | 2644495.5118 | 1162724.558 | 2644504.337 | 1162733.8393 | 2644522.938 | 1162760.5908 | 2644542.3655 | 1162780.1892
116 | 2644512.4885 | 1162718.2136 | 2644495.5118 | 1162724.558
117 | 2644595.1018 | 1163275.9275 | 2644592.943 | 1163268.5299 | 2644594.6232 | 1163263.0061 | 2644603.6574 | 1163250.1775 | 2644608.0979 | 1163219.4832 | 2644607.224 | 1163213.3363
118 | 2644595.1018 | 1163275.9275 | 2644579.6214 | 1163279.5381
119 | 2644518.7489 | 1162953.948 | 2644523.6557 | 1162955.4867 | 2644531.1578 | 1162955.1198 | 2644538.0576 | 1162952.3027 | 2644538.0811 | 1162952.28
120 | 2644757.2214 | 1163099.0497 | 2644751.5289 | 1163102.2869 | 2644748.1479 | 1163107.8202
121 | 2644748.1479 | 1163107.8202 | 2644747.5208 | 1163103.579
122 | 2644749.3222 | 1163083.8275 | 2644746.7476 | 1163098.3493 | 2644747.5208 | 1163103.579
123 | 2644569.8796 | 1163398.7159 | 2644576.1038 | 1163394.5047
124 | 2644581.8582 | 1163390.6115 | 2644576.1038 | 1163394.5047
125 | 2644581.8582 | 1163390.6115 | 2644580.666 | 1163385.0776 | 2644581.4189 | 1163374.9378
126 | 2644596.8338 | 1163393.5907 | 2644581.8582 | 1163390.6115
127 | 2644581.4189 | 1163374.9378 | 2644581.8062 | 1163369.7224 | 2644580.7118 | 1163362.3549
128 | 2644613.1633 | 1163346.2139 | 2644600.2416 | 1163350.3044 | 2644587.6935 | 1163351.5343 | 2644583.5562 | 1163355.8059 | 2644580.7118 | 1163362.3549 | 2644580.7118 | 1163362.3549
129 | 2644619.6971 | 1163344.1454 | 2644613.1633 | 1163346.2139
130 | 2644619.6971 | 1163344.1454 | 2644635.1614 | 1163341.7819
131 | 2644619.6971 | 1163344.1454 | 2644606.8696 | 1163343.1112
132 | 2644635.1614 | 1163341.7819 | 2644635.7704 | 1163341.6888
133 | 2644606.8696 | 1163343.1112 | 2644593.7307 | 1163342.0519 | 2644584.3304 | 1163339.7603
134 | 2644576.9402 | 1163337.9587 | 2644584.3304 | 1163339.7603
135 | 2644576.9402 | 1163337.9587 | 2644558.3898 | 1163330.8192
136 | 2644573.1256 | 1163487.8309 | 2644582.4363 | 1163487.2552 | 2644593.887 | 1163489.7573
137 | 2644573.1256 | 1163487.8309 | 2644573.9907 | 1163481.6897 | 2644580.991 | 1163479.6961 | 2644592.1779 | 1163478.1448
138 | 2644592.1779 | 1163478.1448 | 2644593.1717 | 1163472.2046
139 | 2644592.1779 | 1163478.1448 | 2644598.6623 | 1163479.6158
140 | 2644535.4768 | 1162402.5472 | 2644526.0344 | 1162405.3839 | 2644509.4827 | 1162409.3207
141 | 2644412.0724 | 1162511.9197 | 2644509.4827 | 1162409.3207
142 | 2644513.8315 | 1162582.1744 | 2644506.7814 | 1162571.1836 | 2644487.6426 | 1162558.0241 | 2644448.7653 | 1162538.1709 | 2644412.0724 | 1162511.9197 | 2644412.0724 | 1162511.9197
143 | 2644344.1572 | 1162513.2196 | 2644398.4353 | 1162508.9175 | 2644412.0724 | 1162511.9197
144 | 2644344.1572 | 1162513.2196 | 2644336.7886 | 1162536.9777 | 2644337.6498 | 1162545.8999 | 2644347.0754 | 1162576.6965 | 2644350.6636 | 1162584.6048
145 | 2644350.6636 | 1162584.6048 | 2644357.1785 | 1162584.1637 | 2644363.1295 | 1162587.4648 | 2644366.3343 | 1162593.3471 | 2644366.3343 | 1162593.3471
146 | 2644350.6636 | 1162584.6048 | 2644345.5654 | 1162589.2808 | 2644335.561 | 1162611.0407 | 2644325.3787 | 1162619.5256 | 2644288.6401 | 1162629.6382 | 2644280.4193 | 1162629.7667 | 2644272.4307 | 1162626.4395 | 2644251.6587 | 1162608.2217
147 | 2644538.0063 | 1162619.8622 | 2644513.8315 | 1162582.1744
148 | 2644512.4885 | 1162718.2136 | 2644508.0246 | 1162701.3607 | 2644508.7086 | 1162691.7385 | 2644511.9183 | 1162674.1531 | 2644519.5803 | 1162638.769 | 2644523.9733 | 1162627.9514 | 2644532.033 | 1162621.6634 | 2644538.0063 | 1162619.8622
149 | 2644538.0063 | 1162619.8622 | 2644542.0563 | 1162619.1696 | 2644549.2894 | 1162617.9447 | 2644549.834 | 1162617.8487 | 2644563.4862 | 1162634.2805 | 2644593.6454 | 1162651.9687 | 2644623.8758 | 1162656.9398
150 | 2644512.4885 | 1162718.2136 | 2644528.248 | 1162720.6184
151 | 2644623.8758 | 1162656.9398 | 2644634.4991 | 1162651.0155 | 2644645.6419 | 1162652.51 | 2644657.7515 | 1162661.0265 | 2644665.3418 | 1162675.6571 | 2644669.0465 | 1162675.0288
152 | 2644623.8758 | 1162656.9398 | 2644621.3891 | 1162659.6228 | 2644618.0048 | 1162665.6008 | 2644615.7102 | 1162677.5011 | 2644618.4683 | 1162686.5088
153 | 2644366.3343 | 1162593.3471 | 2644363.7217 | 1162618.3075 | 2644364.9678 | 1162632.1684 | 2644369.9158 | 1162644.7598
154 | 2644220.3259 | 1162600.9988 | 2644227.199 | 1162603.9286 | 2644244.4399 | 1162605.4339 | 2644251.6587 | 1162608.2217
155 | 2644655.8194 | 1162630.285 | 2644654.4196 | 1162639.2904 | 2644656.6118 | 1162648.4115 | 2644667.6551 | 1162669.4933 | 2644669.0465 | 1162675.0288
156 | 2644369.9158 | 1162644.7598 | 2644375.2771 | 1162658.4025
157 | 2644547.6927 | 1163232.6425 | 2644545.6167 | 1163235.9179 | 2644538.6165 | 1163271.8931
158 | 2644536.8016 | 1163289.5251 | 2644535.4931 | 1163285.202 | 2644538.3546 | 1163273.2392 | 2644538.6165 | 1163271.8931
159 | 2644536.8016 | 1163289.5251 | 2644558.8983 | 1163284.3714
160 | 2644579.6214 | 1163279.5381 | 2644558.8983 | 1163284.3714
161 | 2644685.753 | 1163389.7816 | 2644677.3919 | 1163381.3626
162 | 2644685.753 | 1163389.7816 | 2644689.9161 | 1163392.3472 | 2644696.587 | 1163393.4751 | 2644704.911 | 1163392.7255 | 2644718.0477 | 1163387.5426 | 2644722.58 | 1163386.8092 | 2644726.3612 | 1163388.2047
163 | 2644745.731 | 1163381.2228 | 2644726.3612 | 1163388.2047
164 | 2644727.1163 | 1163397.9043 | 2644728.3212 | 1163394.5115 | 2644727.7801 | 1163391.0501 | 2644726.3612 | 1163388.2047
165 | 2644727.1163 | 1163397.9043 | 2644726.4464 | 1163404.5583 | 2644729.8537 | 1163416.0563 | 2644733.6899 | 1163425.5009 | 2644736.9529 | 1163428.5934 | 2644741.4596 | 1163430.2723 | 2644748.8569 | 1163431.0034
166 | 2644768.1431 | 1163433.7392 | 2644763.84 | 1163432.4843 | 2644748.8569 | 1163431.0034
167 | 2644758.0148 | 1163442.2683 | 2644763.9737 | 1163442.3127 | 2644766.8611 | 1163440.2886 | 2644768.5353 | 1163436.6103 | 2644768.1431 | 1163433.7392

## bus_geodata
| x | y | coords
0 | 2644876.2733 | 1163313.1961
1 | 2644865.0304 | 1163309.4513
2 | 2644860.1575 | 1163313.7283
3 | 2644866.7768 | 1163303.5331
4 | 2644893.8684 | 1163338.3482
5 | 2644828.2996 | 1163335.4023
6 | 2644868.423 | 1163297.9549
7 | 2644837.3476 | 1163410.1754
8 | 2644855.9807 | 1163425.9781
9 | 2644829.849 | 1163444.0484
10 | 2644795.9358 | 1163343.2383
11 | 2644874.6527 | 1163283.5651
12 | 2644800.6429 | 1163440.332
13 | 2644845.0486 | 1163495.0327
14 | 2644785.8492 | 1163345.6805
15 | 2644914.8687 | 1163234.0948
16 | 2644870.8047 | 1163283.9314
17 | 2644913.8752 | 1163247.6342
18 | 2644855.5545 | 1163282.3923
19 | 2644910.1656 | 1163253.581
20 | 2644830.4478 | 1163276.3652
21 | 2644874.4806 | 1163205.0005
22 | 2644873.5661 | 1163191.0197
23 | 2644860.2184 | 1163212.5305
24 | 2644665.8577 | 1163272.5949
25 | 2644658.9063 | 1163267.9631
26 | 2644678.6468 | 1163267.2082
27 | 2644888.2544 | 1163186.3602
28 | 2644836.8361 | 1163153.089
29 | 2644858.5976 | 1163213.6165
30 | 2644652.7536 | 1163266.1499
31 | 2644653.3485 | 1163285.607
32 | 2644686.5102 | 1163266.0129
33 | 2644891.5073 | 1163184.5604
34 | 2644823.3129 | 1163141.1636
35 | 2644838.5024 | 1163220.0934
36 | 2644613.2853 | 1163272.1113
37 | 2644651.8009 | 1163337.7246
38 | 2644696.4494 | 1163264.5022
39 | 2644809.7691 | 1163542.22
40 | 2644798.193 | 1163552.8918
41 | 2644828.1427 | 1163507.5355
42 | 2644776.6655 | 1163546.7607
43 | 2644778.0581 | 1163562.9138
44 | 2644689.7689 | 1163598.754
45 | 2644686.9202 | 1163599.9718
46 | 2644736.6569 | 1163696.9982
47 | 2644699.5651 | 1163594.5586
48 | 2644767.1162 | 1163567.0838
49 | 2644844.772 | 1163564.7973
50 | 2644778.3334 | 1163430.2465
51 | 2644713.7474 | 1163510.586
52 | 2644696.9323 | 1163502.6459
53 | 2644730.9368 | 1163502.998
54 | 2644669.2328 | 1163606.2207
55 | 2644712.9436 | 1163588.8289
56 | 2644696.4519 | 1163483.8102
57 | 2644684.3699 | 1163499.463
58 | 2644741.2304 | 1163498.4541
59 | 2644694.5213 | 1163470.2977
60 | 2644699.9293 | 1163478.7813
61 | 2644640.145 | 1163493.3853
62 | 2644751.2768 | 1163494.0192
63 | 2644685.8435 | 1163409.5593
64 | 2644708.2907 | 1163466.6892
65 | 2644628.3228 | 1163492.7013
66 | 2644820.3578 | 1163226.6642
67 | 2644835.948 | 1163122.1589
68 | 2644796.4236 | 1163122.9984
69 | 2644757.5116 | 1163115.6383
70 | 2644789.758 | 1163077.199
71 | 2644555.7307 | 1162918.049
72 | 2644572.4034 | 1162897.8841
73 | 2644550.7538 | 1162935.5018
74 | 2644653.4972 | 1163108.1951
75 | 2644662.9588 | 1163102.8514
76 | 2644749.3056 | 1163128.2728
77 | 2644750.748 | 1163113.5425
78 | 2644771.3459 | 1162981.8269
79 | 2644762.2419 | 1163009.2712
80 | 2644727.7948 | 1163033.6857
81 | 2644702.3877 | 1163040.6784
82 | 2644742.7204 | 1163032.1736
83 | 2644683.6229 | 1163093.9446
84 | 2644689.5328 | 1162979.9956
85 | 2644778.2405 | 1162977.6538
86 | 2644758.7537 | 1162951.2434
87 | 2644672.439 | 1163098.7652
88 | 2644692.7122 | 1163016.0269
89 | 2644778.7038 | 1162973.0437
90 | 2644782.5842 | 1162928.6418
91 | 2644748.6448 | 1162940.114
92 | 2644592.2373 | 1162899.7876
93 | 2644595.4862 | 1162894.0857
94 | 2644687.9404 | 1162893.1087
95 | 2644669.9713 | 1163117.8557
96 | 2644631.8545 | 1162839.1496
97 | 2644573.9373 | 1162781.8572
98 | 2644644.2282 | 1162829.5724
99 | 2644559.8284 | 1162800.6119
100 | 2644542.3655 | 1162780.1892
101 | 2644654.1592 | 1162821.8859
102 | 2644543.3256 | 1162809.8451
103 | 2644521.1394 | 1162804.062
104 | 2644495.5118 | 1162724.558
105 | 2644678.2464 | 1163123.7425
106 | 2644670.7179 | 1163127.6886
107 | 2644595.1018 | 1163275.9275
108 | 2644538.0811 | 1162952.28
109 | 2644748.1479 | 1163107.8202
110 | 2644757.2214 | 1163099.0497
111 | 2644747.5208 | 1163103.579
112 | 2644749.3222 | 1163083.8275
113 | 2644576.1038 | 1163394.5047
114 | 2644569.8796 | 1163398.7159
115 | 2644581.8582 | 1163390.6115
116 | 2644581.4189 | 1163374.9378
117 | 2644596.8338 | 1163393.5907
118 | 2644580.7118 | 1163362.3549
119 | 2644613.1633 | 1163346.2139
120 | 2644619.6971 | 1163344.1454
121 | 2644635.1614 | 1163341.7819
122 | 2644606.8696 | 1163343.1112
123 | 2644635.7704 | 1163341.6888
124 | 2644584.3304 | 1163339.7603
125 | 2644576.9402 | 1163337.9587
126 | 2644593.887 | 1163489.7573
127 | 2644573.1256 | 1163487.8309
128 | 2644592.1779 | 1163478.1448
129 | 2644593.1717 | 1163472.2046
130 | 2644598.6623 | 1163479.6158
131 | 2644535.4768 | 1162402.5472
132 | 2644509.4827 | 1162409.3207
133 | 2644412.0724 | 1162511.9197
134 | 2644344.1572 | 1162513.2196
135 | 2644350.6636 | 1162584.6048
136 | 2644513.8315 | 1162582.1744
137 | 2644538.0063 | 1162619.8622
138 | 2644512.4885 | 1162718.2136
139 | 2644623.8758 | 1162656.9398
140 | 2644366.3343 | 1162593.3471
141 | 2644251.6587 | 1162608.2217
142 | 2644528.248 | 1162720.6184
143 | 2644669.0465 | 1162675.0288
144 | 2644618.4683 | 1162686.5088
145 | 2644369.9158 | 1162644.7598
146 | 2644220.3259 | 1162600.9988
147 | 2644655.8194 | 1162630.285
148 | 2644375.2771 | 1162658.4025
149 | 2644518.7489 | 1162953.948
150 | 2644538.6165 | 1163271.8931
151 | 2644547.6927 | 1163232.6425
152 | 2644536.8016 | 1163289.5251
153 | 2644558.8983 | 1163284.3714
154 | 2644579.6214 | 1163279.5381
155 | 2644558.3898 | 1163330.8192
156 | 2644607.224 | 1163213.3363
157 | 2644677.3919 | 1163381.3626
158 | 2644690.2789 | 1163328.0541
159 | 2644685.753 | 1163389.7816
160 | 2644726.3612 | 1163388.2047
161 | 2644745.731 | 1163381.2228
162 | 2644727.1163 | 1163397.9043
163 | 2644670.7673 | 1163411.8819
164 | 2644748.8569 | 1163431.0034
165 | 2644768.1431 | 1163433.7392
166 | 2644758.0148 | 1163442.2683
167 | 2644773.0726 | 1163420.8024
168 | 2644654.0115 | 1163610.8686
169 | 2644706.2248 | 1163320.0528

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1