## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5841-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5841-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5841-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5841-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5841-12_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5841-12_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5841-12_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_5841-12_0_3_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_5841-12_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_5841-12_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_5841-12_0_3_node_66 | 0.4 | n |  | TRUE
11 | bus_LV_5841-12_0_3_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_5841-12_0_3_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_5841-12_0_3_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_5841-12_0_3_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_5841-12_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_5841-12_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5841-12_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_5841-12_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_5841-12_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_5841-12_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_5841-12_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_5841-12_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_5841-12_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_5841-12_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_5841-12_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_5841-12_0_3_node_56 | 0.4 | n |  | TRUE
27 | bus_LV_5841-12_0_3_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_5841-12_0_3_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_5841-12_0_3_node_57 | 0.4 | n |  | TRUE
30 | bus_LV_5841-12_0_3_node_58 | 0.4 | n |  | TRUE
31 | bus_LV_5841-12_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_5841-12_0_3_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_5841-12_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_5841-12_0_3_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_5841-12_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_5841-12_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_5841-12_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_5841-12_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_5841-12_0_3_node_62 | 0.4 | n |  | TRUE
40 | bus_LV_5841-12_0_3_node_63 | 0.4 | n |  | TRUE
41 | bus_LV_5841-12_0_3_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_5841-12_0_3_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_5841-12_0_3_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_5841-12_0_3_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_5841-12_0_3_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_5841-12_0_3_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_5841-12_0_3_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_5841-12_0_3_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_5841-12_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_5841-12_0_3_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_5841-12_0_3_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_5841-12_0_3_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_5841-12_0_3_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_5841-12_0_3_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_5841-12_0_3_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_5841-12_0_3_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_5841-12_0_3_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_5841-12_0_3_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_5841-12_0_3_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_5841-12_0_3_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_5841-12_0_3_node_69 | 0.4 | n |  | TRUE
62 | bus_LV_5841-12_0_3_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_5841-12_0_3_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_5841-12_0_3_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_5841-12_0_3_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_5841-12_0_3_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_5841-12_0_3_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_5841-12_0_3_node_68 | 0.4 | n |  | TRUE
69 | bus_MV_146_0_node_9 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5841-12_0_3_load_0 | 0 | 0.0030897 | 0.00077434 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5841-12_0_3_load_2 | 2 | 0.0028261 | 0.00070829 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5841-12_0_3_load_3 | 3 | 0.0015341 | 0.00038449 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5841-12_0_3_load_67 | 7 | 0.001387 | 0.00034761 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5841-12_0_3_load_7 | 9 | 0.0082458 | 0.0020666 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5841-12_0_3_load_66 | 10 | 0.00082024 | 0.00020557 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5841-12_0_3_load_21 | 11 | 0.00039797 | 9.974e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5841-12_0_3_load_23 | 12 | 0.00051037 | 0.00012791 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5841-12_0_3_load_20 | 13 | 0.0022966 | 0.00057559 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5841-12_0_3_load_22 | 14 | 0.00044108 | 0.00011054 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5841-12_0_3_load_9 | 15 | 0.0080801 | 0.0020251 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5841-12_0_3_load_10 | 16 | 0.008192 | 0.0020531 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5841-12_0_3_load_11 | 17 | 0.030009 | 0.007521 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5841-12_0_3_load_12 | 18 | 0.0081446 | 0.0020412 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5841-12_0_3_load_13 | 19 | 0.0097512 | 0.0024439 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5841-12_0_3_load_14 | 20 | 0.0089832 | 0.0022514 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5841-12_0_3_load_19 | 22 | 0.0086547 | 0.0021691 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5841-12_0_3_load_17 | 23 | 0.0016844 | 0.00042214 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5841-12_0_3_load_16 | 24 | 0.011071 | 0.0027746 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5841-12_0_3_load_54 | 27 | 0.00086519 | 0.00021684 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5841-12_0_3_load_57 | 29 | 0.00065879 | 0.00016511 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5841-12_0_3_load_58 | 30 | 0.0012806 | 0.00032094 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5841-12_0_3_load_24 | 31 | 0.0004565 | 0.00011441 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5841-12_0_3_load_25 | 32 | 0.00075291 | 0.0001887 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5841-12_0_3_load_28 | 33 | 0.0026589 | 0.00066639 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5841-12_0_3_load_26 | 34 | 0.0043327 | 0.0010859 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5841-12_0_3_load_27 | 35 | 0.0077146 | 0.0019335 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5841-12_0_3_load_29 | 36 | 0.0092072 | 0.0023075 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5841-12_0_3_load_63 | 40 | 0.0048936 | 0.0012264 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5841-12_0_3_load_32 | 41 | 0.00046112 | 0.00011557 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5841-12_0_3_load_33 | 42 | 0.00010807 | 2.7086e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5841-12_0_3_load_35 | 44 | 0.00038241 | 9.5842e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5841-12_0_3_load_36 | 45 | 0.00037369 | 9.3655e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5841-12_0_3_load_37 | 46 | 0.00015887 | 3.9816e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5841-12_0_3_load_65 | 47 | 0.00017411 | 4.3636e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5841-12_0_3_load_53 | 48 | 0.0003957 | 9.9171e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5841-12_0_3_load_45 | 50 | 0.00036941 | 9.2583e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5841-12_0_3_load_41 | 51 | 0.0003443 | 8.6289e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5841-12_0_3_load_38 | 53 | 0.00020618 | 5.1674e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5841-12_0_3_load_39 | 54 | 0.00022216 | 5.5679e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5841-12_0_3_load_40 | 55 | 0.0002615 | 6.5538e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5841-12_0_3_load_42 | 56 | 0.00039039 | 9.7841e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5841-12_0_3_load_51 | 57 | 0.00069221 | 0.00017348 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5841-12_0_3_load_52 | 58 | 0.0015105 | 0.00037857 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5841-12_0_3_load_50 | 60 | 0.00023738 | 5.9492e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5841-12_0_3_load_69 | 61 | 0.00019395 | 4.8609e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5841-12_0_3_load_47 | 63 | 0.0005974 | 0.00014972 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5841-12_0_3_load_48 | 64 | 0.00061522 | 0.00015419 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5841-12_0_3_load_59 | 65 | 0.0014578 | 0.00036536 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5841-12_0_3_load_60 | 66 | 0.0030292 | 0.00075918 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5841-12_0_3_load_61 | 67 | 0.0008421 | 0.00021105 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5841-12_0_3_load_68 | 68 | 0.0007145 | 0.00017907 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5841-12_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5841-12_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.012232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5841-12_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.012569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5841-12_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.048234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5841-12_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.15162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5841-12_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.017971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5841-12_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.037627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5841-12_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.08168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5841-12_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.022212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5841-12_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.023801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5841-12_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.016124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5841-12_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.073264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5841-12_0_3_line_12 | NAYY 4x150 SE | 10 | 68 | 0.0040146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5841-12_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.027619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5841-12_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.017077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5841-12_0_3_line_15 | NAYY 4x150 SE | 13 | 22 | 0.032625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_5841-12_0_3_line_16 | NAYY 4x150 SE | 14 | 31 | 0.007004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5841-12_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.028821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5841-12_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.009149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5841-12_0_3_line_19 | NAYY 4x150 SE | 16 | 18 | 0.0055094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5841-12_0_3_line_20 | NAYY 4x150 SE | 18 | 19 | 0.031364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_5841-12_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.06625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_5841-12_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.018068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_5841-12_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.058476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_5841-12_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.063958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5841-12_0_3_line_25 | NAYY 4x150 SE | 23 | 24 | 0.0020201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5841-12_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.097212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5841-12_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.24462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5841-12_0_3_line_28 | NAYY 4x150 SE | 26 | 29 | 0.022284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5841-12_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.016095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5841-12_0_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.21198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5841-12_0_3_line_31 | NAYY 4x150 SE | 28 | 58 | 0.077443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5841-12_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.068393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5841-12_0_3_line_33 | NAYY 4x150 SE | 30 | 65 | 0.029718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5841-12_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.021936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5841-12_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.022512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5841-12_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.023494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5841-12_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.00026626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5841-12_0_3_line_38 | NAYY 4x150 SE | 35 | 36 | 0.042308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5841-12_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.057076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5841-12_0_3_line_40 | NAYY 4x150 SE | 37 | 38 | 0.20025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5841-12_0_3_line_41 | NAYY 4x150 SE | 38 | 39 | 0.20267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5841-12_0_3_line_42 | NAYY 4x150 SE | 39 | 40 | 0.12123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5841-12_0_3_line_43 | NAYY 4x150 SE | 40 | 67 | 0.10418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5841-12_0_3_line_44 | NAYY 4x150 SE | 41 | 42 | 0.0066391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_5841-12_0_3_line_45 | NAYY 4x150 SE | 41 | 43 | 0.00016359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_5841-12_0_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.0079114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_5841-12_0_3_line_47 | NAYY 4x150 SE | 43 | 45 | 0.026092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_5841-12_0_3_line_48 | NAYY 4x150 SE | 43 | 46 | 0.011816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_5841-12_0_3_line_49 | NAYY 4x150 SE | 43 | 47 | 0.32981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_5841-12_0_3_line_50 | NAYY 4x150 SE | 44 | 48 | 0.032567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_5841-12_0_3_line_51 | NAYY 4x150 SE | 45 | 49 | 0.13975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_5841-12_0_3_line_52 | NAYY 4x150 SE | 46 | 50 | 0.011348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_5841-12_0_3_line_53 | NAYY 4x150 SE | 48 | 51 | 0.097999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_5841-12_0_3_line_54 | NAYY 4x150 SE | 49 | 52 | 0.057022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_5841-12_0_3_line_55 | NAYY 4x150 SE | 51 | 54 | 0.015014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_5841-12_0_3_line_56 | NAYY 4x150 SE | 52 | 59 | 0.011445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_5841-12_0_3_line_57 | NAYY 4x150 SE | 52 | 60 | 0.032306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_5841-12_0_3_line_58 | NAYY 4x150 SE | 53 | 54 | 0.0043246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_5841-12_0_3_line_59 | NAYY 4x150 SE | 53 | 55 | 0.019728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_5841-12_0_3_line_60 | NAYY 4x150 SE | 55 | 56 | 0.016962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_5841-12_0_3_line_61 | NAYY 4x150 SE | 56 | 57 | 0.016701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_5841-12_0_3_line_62 | NAYY 4x150 SE | 57 | 58 | 0.036915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_5841-12_0_3_line_63 | NAYY 4x150 SE | 59 | 61 | 0.021779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_5841-12_0_3_line_64 | NAYY 4x150 SE | 60 | 62 | 0.018383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_5841-12_0_3_line_65 | NAYY 4x150 SE | 62 | 63 | 0.074059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_5841-12_0_3_line_66 | NAYY 4x150 SE | 63 | 64 | 0.011219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_5841-12_0_3_line_67 | NAYY 4x150 SE | 65 | 66 | 0.053789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5841-12_0_3_trafo_12 | 0.25 MVA 20/0.4 kV | 69 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2575613.7266 | 1146965.8041 | 2575623.8639 | 1146954.2794 | 2575633.9258 | 1146958.4183
1 | 2575613.7266 | 1146965.8041 | 2575601.6197 | 1146964.0602
2 | 2575613.7266 | 1146965.8041 | 2575625.3229 | 1146970.6512
3 | 2575555.0935 | 1146971.1784 | 2575564.0828 | 1146966.3394 | 2575578.1165 | 1146962.9696 | 2575593.085 | 1146962.8309 | 2575601.6197 | 1146964.0602
4 | 2575555.0935 | 1146971.1784 | 2575557.9085 | 1146977.8258 | 2575554.0768 | 1146989.336 | 2575548.9497 | 1146999.5841 | 2575552.7917 | 1147011.3632 | 2575566.3541 | 1147041.3118 | 2575570.7084 | 1147063.8386 | 2575577.1076 | 1147086.8795 | 2575574.5451 | 1147104.5432 | 2575570.9617 | 1147114.785
5 | 2575555.0935 | 1146971.1784 | 2575547.1555 | 1146970.1546 | 2575538.2418 | 1146974.7154
6 | 2575570.9617 | 1147114.785 | 2575570.191 | 1147138.6444 | 2575568.4073 | 1147141.9533 | 2575560.4221 | 1147147.9663
7 | 2575511.5757 | 1147038.7558 | 2575527.705 | 1147035.1661 | 2575533.0778 | 1147030.5641 | 2575535.8925 | 1147018.2799 | 2575532.5677 | 1146988.323 | 2575536.1494 | 1146975.78 | 2575538.2418 | 1146974.7154
8 | 2575538.2418 | 1146974.7154 | 2575539.1006 | 1146952.5198
9 | 2575541.4088 | 1147162.2837 | 2575560.4221 | 1147147.9663
10 | 2575511.5757 | 1147038.7558 | 2575506.2655 | 1147023.5314
11 | 2575511.5757 | 1147038.7558 | 2575507.8464 | 1147056.5243 | 2575496.6443 | 1147066.7639 | 2575483.8454 | 1147069.6398 | 2575474.8845 | 1147062.5951 | 2575470.5871 | 1147047.7914
12 | 2575538.2018 | 1147164.6987 | 2575541.4088 | 1147162.2837
13 | 2575499.6653 | 1146996.757 | 2575503.8978 | 1147016.7429 | 2575506.2655 | 1147023.5314
14 | 2575461.49 | 1147033.7148 | 2575469.1278 | 1147042.7643 | 2575470.5871 | 1147047.7914
15 | 2575498.4978 | 1146964.5436 | 2575496.646 | 1146982.4999 | 2575499.6653 | 1146996.757
16 | 2575461.49 | 1147033.7148 | 2575456.9725 | 1147028.3624
17 | 2575400.6101 | 1146879.4986 | 2575372.127 | 1146883.9007
18 | 2575363.0853 | 1146885.298 | 2575372.127 | 1146883.9007
19 | 2575400.6101 | 1146879.4986 | 2575406.0549 | 1146878.6571
20 | 2575406.0549 | 1146878.6571 | 2575428.5506 | 1146875.1804 | 2575437.1039 | 1146874.2719
21 | 2575437.1039 | 1146874.2719 | 2575464.7945 | 1146871.3304 | 2575478.0051 | 1146877.0237 | 2575480.5151 | 1146886.0513 | 2575487.01 | 1146899.1813
22 | 2575501.2975 | 1146906.5211 | 2575494.1948 | 1146906.9391 | 2575489.2353 | 1146903.68 | 2575487.01 | 1146899.1813
23 | 2575501.2975 | 1146906.5211 | 2575503.3839 | 1146917.1623 | 2575498.4978 | 1146964.5436
24 | 2575501.2975 | 1146906.5211 | 2575500.3171 | 1146901.5448 | 2575494.4286 | 1146879.5357 | 2575493.8601 | 1146870.1 | 2575495.8278 | 1146862.944 | 2575501.2184 | 1146844.4868
25 | 2575501.2184 | 1146844.4868 | 2575501.7847 | 1146842.5476
26 | 2575533.3975 | 1146750.9353 | 2575521.5593 | 1146774.8398 | 2575501.7847 | 1146842.5476
27 | 2575533.3975 | 1146750.9353 | 2575519.3677 | 1146506.7159
28 | 2575519.3677 | 1146506.7159 | 2575516.5839 | 1146504.0148 | 2575508.8743 | 1146502.6455 | 2575498.4424 | 1146504.3784
29 | 2575519.3677 | 1146506.7159 | 2575519.4716 | 1146502.0576 | 2575519.7348 | 1146490.6246
30 | 2575461.84 | 1146302.4938 | 2575466.0291 | 1146314.4715 | 2575477.6219 | 1146328.0865 | 2575491.6864 | 1146343.2032 | 2575514.1427 | 1146366.8567 | 2575522.425 | 1146376.7834 | 2575525.122 | 1146380.7744 | 2575526.38 | 1146386.0052 | 2575526.4143 | 1146394.4204 | 2575524.7073 | 1146412.8253 | 2575523.6242 | 1146427.8817 | 2575520.8484 | 1146442.2334 | 2575519.7348 | 1146490.6246
31 | 2575486.8211 | 1146229.1904 | 2575461.84 | 1146302.4938
32 | 2575431.2522 | 1146516.9771 | 2575452.2043 | 1146512.0593 | 2575498.4424 | 1146504.3784
33 | 2575431.2522 | 1146516.9771 | 2575404.7739 | 1146523.1921 | 2575402.3913 | 1146524.0117
34 | 2575438.5581 | 1147016.4423 | 2575456.9725 | 1147028.3624 | 2575456.9725 | 1147028.3624
35 | 2575438.5581 | 1147016.4423 | 2575419.6603 | 1147004.2093
36 | 2575400.1234 | 1146991.1681 | 2575407.0565 | 1146996.0506 | 2575419.6603 | 1147004.2093
37 | 2575400.1234 | 1146991.1681 | 2575399.9057 | 1146991.0148
38 | 2575399.9057 | 1146991.0148 | 2575375.6993 | 1146973.9681 | 2575366.4296 | 1146965.2847
39 | 2575324.7745 | 1146926.2645 | 2575366.4296 | 1146965.2847
40 | 2575176.0329 | 1146791.8996 | 2575245.785 | 1146850.7743 | 2575314.8978 | 1146917.0116 | 2575324.7745 | 1146926.2645
41 | 2575176.0329 | 1146791.8996 | 2575136.6738 | 1146765.0268 | 2575079.7167 | 1146730.4679 | 2575021.8021 | 1146683.7519 | 2575009.4441 | 1146676.433
42 | 2575009.4441 | 1146676.433 | 2574980.2081 | 1146659.1128 | 2574928.3703 | 1146627.7578 | 2574909.3699 | 1146609.0427
43 | 2574909.3699 | 1146609.0427 | 2574929.396 | 1146506.8056
44 | 2575305.5028 | 1146060.5538 | 2575308.1315 | 1146066.6503
45 | 2575305.438 | 1146060.4035 | 2575305.5028 | 1146060.5538
46 | 2575308.1315 | 1146066.6503 | 2575311.2639 | 1146073.9152
47 | 2575305.438 | 1146060.4035 | 2575289.4614 | 1146066.2277 | 2575280.4897 | 1146067.6675
48 | 2575305.438 | 1146060.4035 | 2575295.7431 | 1146053.6483
49 | 2575305.438 | 1146060.4035 | 2575511.8654 | 1145803.1774
50 | 2575324.1584 | 1146103.8207 | 2575311.2639 | 1146073.9152
51 | 2575208.4959 | 1146173.5811 | 2575217.0214 | 1146141.7413 | 2575225.7204 | 1146105.3985 | 2575238.0095 | 1146086.4607 | 2575258.745 | 1146074.1692 | 2575276.6648 | 1146068.2814 | 2575280.4897 | 1146067.6675
52 | 2575295.7431 | 1146053.6483 | 2575286.4324 | 1146047.1607
53 | 2575324.1584 | 1146103.8207 | 2575328.0219 | 1146112.7812 | 2575347.8347 | 1146130.1862 | 2575400.6578 | 1146162.3975
54 | 2575212.6706 | 1146230.3143 | 2575209.3435 | 1146209.5844 | 2575208.4959 | 1146173.5811
55 | 2575400.6578 | 1146162.3975 | 2575413.4766 | 1146170.2143
56 | 2575212.6706 | 1146230.3143 | 2575202.8554 | 1146236.2466
57 | 2575212.6706 | 1146230.3143 | 2575227.7721 | 1146250.7955 | 2575232.9899 | 1146255.2478
58 | 2575417.1689 | 1146172.4659 | 2575413.4766 | 1146170.2143
59 | 2575417.1689 | 1146172.4659 | 2575434.0126 | 1146182.7371 | 2575434.0126 | 1146182.7371
60 | 2575446.5122 | 1146194.2031 | 2575434.0126 | 1146182.7371
61 | 2575446.5122 | 1146194.2031 | 2575458.8192 | 1146205.4923
62 | 2575486.8211 | 1146229.1904 | 2575482.8879 | 1146227.5707 | 2575458.8192 | 1146205.4923
63 | 2575181.6387 | 1146236.023 | 2575190.1988 | 1146238.6556 | 2575202.8554 | 1146236.2466
64 | 2575246.9737 | 1146267.18 | 2575232.9899 | 1146255.2478
65 | 2575246.9737 | 1146267.18 | 2575252.4478 | 1146285.1664 | 2575263.4799 | 1146309.8665 | 2575271.6386 | 1146319.4821 | 2575282.8875 | 1146320.3696 | 2575287.1958 | 1146320.2038
66 | 2575287.1958 | 1146320.2038 | 2575298.4066 | 1146319.7723
67 | 2575351.5281 | 1146541.5083 | 2575402.3913 | 1146524.0117

## bus_geodata
| x | y | coords
0 | 2575633.9258 | 1146958.4183
1 | 2575613.7266 | 1146965.8041
2 | 2575601.6197 | 1146964.0602
3 | 2575625.3229 | 1146970.6512
4 | 2575555.0935 | 1146971.1784
5 | 2575570.9617 | 1147114.785
6 | 2575538.2418 | 1146974.7154
7 | 2575560.4221 | 1147147.9663
8 | 2575511.5757 | 1147038.7558
9 | 2575539.1006 | 1146952.5198
10 | 2575541.4088 | 1147162.2837
11 | 2575506.2655 | 1147023.5314
12 | 2575470.5871 | 1147047.7914
13 | 2575499.6653 | 1146996.757
14 | 2575461.49 | 1147033.7148
15 | 2575372.127 | 1146883.9007
16 | 2575400.6101 | 1146879.4986
17 | 2575363.0853 | 1146885.298
18 | 2575406.0549 | 1146878.6571
19 | 2575437.1039 | 1146874.2719
20 | 2575487.01 | 1146899.1813
21 | 2575501.2975 | 1146906.5211
22 | 2575498.4978 | 1146964.5436
23 | 2575501.2184 | 1146844.4868
24 | 2575501.7847 | 1146842.5476
25 | 2575533.3975 | 1146750.9353
26 | 2575519.3677 | 1146506.7159
27 | 2575519.7348 | 1146490.6246
28 | 2575461.84 | 1146302.4938
29 | 2575498.4424 | 1146504.3784
30 | 2575431.2522 | 1146516.9771
31 | 2575456.9725 | 1147028.3624
32 | 2575438.5581 | 1147016.4423
33 | 2575419.6603 | 1147004.2093
34 | 2575400.1234 | 1146991.1681
35 | 2575399.9057 | 1146991.0148
36 | 2575366.4296 | 1146965.2847
37 | 2575324.7745 | 1146926.2645
38 | 2575176.0329 | 1146791.8996
39 | 2575009.4441 | 1146676.433
40 | 2574909.3699 | 1146609.0427
41 | 2575305.5028 | 1146060.5538
42 | 2575308.1315 | 1146066.6503
43 | 2575305.438 | 1146060.4036
44 | 2575311.2639 | 1146073.9152
45 | 2575280.4897 | 1146067.6675
46 | 2575295.7431 | 1146053.6483
47 | 2575511.8654 | 1145803.1774
48 | 2575324.1584 | 1146103.8207
49 | 2575208.4959 | 1146173.5811
50 | 2575286.4324 | 1146047.1607
51 | 2575400.6578 | 1146162.3975
52 | 2575212.6706 | 1146230.3143
53 | 2575417.1689 | 1146172.4659
54 | 2575413.4766 | 1146170.2143
55 | 2575434.0126 | 1146182.7371
56 | 2575446.5122 | 1146194.2031
57 | 2575458.8192 | 1146205.4923
58 | 2575486.8211 | 1146229.1904
59 | 2575202.8554 | 1146236.2466
60 | 2575232.9899 | 1146255.2478
61 | 2575181.6387 | 1146236.023
62 | 2575246.9737 | 1146267.18
63 | 2575287.1958 | 1146320.2038
64 | 2575298.4066 | 1146319.7723
65 | 2575402.3913 | 1146524.0117
66 | 2575351.5281 | 1146541.5083
67 | 2574929.396 | 1146506.8056
68 | 2575538.2018 | 1147164.6987
69 | 2575406.0549 | 1146878.6571

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1