## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5841-21_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5841-21_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5841-21_0_1_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_5841-21_0_1_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_5841-21_0_1_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_5841-21_0_1_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_5841-21_0_1_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_5841-21_0_1_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5841-21_0_1_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5841-21_0_1_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_5841-21_0_1_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_5841-21_0_1_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_5841-21_0_1_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_5841-21_0_1_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_5841-21_0_1_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_5841-21_0_1_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_5841-21_0_1_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_5841-21_0_1_node_134 | 0.4 | n |  | TRUE
18 | bus_LV_5841-21_0_1_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_5841-21_0_1_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_5841-21_0_1_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_5841-21_0_1_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_5841-21_0_1_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_5841-21_0_1_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_5841-21_0_1_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_5841-21_0_1_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_5841-21_0_1_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_5841-21_0_1_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_5841-21_0_1_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_5841-21_0_1_node_136 | 0.4 | n |  | TRUE
30 | bus_LV_5841-21_0_1_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_5841-21_0_1_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_5841-21_0_1_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_5841-21_0_1_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_5841-21_0_1_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_5841-21_0_1_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_5841-21_0_1_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_5841-21_0_1_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_5841-21_0_1_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_5841-21_0_1_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_5841-21_0_1_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_5841-21_0_1_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_5841-21_0_1_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_5841-21_0_1_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_5841-21_0_1_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_5841-21_0_1_node_133 | 0.4 | n |  | TRUE
46 | bus_MV_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5841-21_0_1_load_0 | 0 | 0.0011171 | 0.00027997 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5841-21_0_1_load_1 | 1 | 0.00089748 | 0.00022493 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5841-21_0_1_load_9 | 2 | 0.00095387 | 0.00023906 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5841-21_0_1_load_2 | 3 | 0.0021412 | 0.00053663 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5841-21_0_1_load_3 | 4 | 0.00052249 | 0.00013095 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5841-21_0_1_load_20 | 5 | 0.00054762 | 0.00013725 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5841-21_0_1_load_4 | 6 | 0.00044208 | 0.0001108 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5841-21_0_1_load_5 | 7 | 0.00015174 | 3.803e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5841-21_0_1_load_22 | 9 | 0.00027854 | 6.9808e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5841-21_0_1_load_10 | 12 | 0.0002109 | 5.2858e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5841-21_0_1_load_11 | 13 | 0.00017278 | 4.3302e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5841-21_0_1_load_12 | 15 | 8.952e-05 | 2.2436e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5841-21_0_1_load_13 | 16 | 9.6233e-05 | 2.4118e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5841-21_0_1_load_15 | 19 | 0.00031801 | 7.9701e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5841-21_0_1_load_16 | 20 | 0.00044822 | 0.00011234 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5841-21_0_1_load_17 | 21 | 0.00018585 | 4.6579e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5841-21_0_1_load_33 | 22 | 0.00012078 | 3.0269e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5841-21_0_1_load_27 | 23 | 0.00017271 | 4.3286e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5841-21_0_1_load_21 | 24 | 0.00046356 | 0.00011618 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5841-21_0_1_load_24 | 26 | 0.0034387 | 0.00086183 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5841-21_0_1_load_25 | 27 | 0.00017823 | 4.4668e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5841-21_0_1_load_26 | 28 | 0.0008397 | 0.00021045 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5841-21_0_1_load_136 | 29 | 0.00054021 | 0.00013539 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5841-21_0_1_load_37 | 30 | 0.00022414 | 5.6174e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5841-21_0_1_load_31 | 31 | 0.00016769 | 4.2027e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5841-21_0_1_load_32 | 32 | 0.00039101 | 9.7996e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5841-21_0_1_load_34 | 33 | 0.00033839 | 8.4808e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5841-21_0_1_load_35 | 34 | 0.00032943 | 8.2564e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5841-21_0_1_load_36 | 35 | 0.00027717 | 6.9466e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5841-21_0_1_load_40 | 36 | 0.00025423 | 6.3717e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5841-21_0_1_load_46 | 37 | 8.5682e-05 | 2.1474e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5841-21_0_1_load_43 | 38 | 0.0011359 | 0.00028467 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5841-21_0_1_load_38 | 39 | 0.0003564 | 8.9322e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5841-21_0_1_load_41 | 41 | 0.00016048 | 4.0219e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5841-21_0_1_load_42 | 42 | 0.00034058 | 8.5357e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5841-21_0_1_load_45 | 43 | 0.00034769 | 8.7138e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5841-21_0_1_load_44 | 44 | 0.0001868 | 4.6817e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5841-21_0_1_load_133 | 45 | 0.0017376 | 0.00043549 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5841-21_0_1_line_0 | NAYY 4x150 SE | 0 | 1 | 0.057936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_5841-21_0_1_line_1 | NAYY 4x150 SE | 0 | 2 | 0.19403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_5841-21_0_1_line_2 | NAYY 4x150 SE | 1 | 3 | 0.020201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_5841-21_0_1_line_3 | NAYY 4x150 SE | 2 | 10 | 0.13743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_5841-21_0_1_line_4 | NAYY 4x150 SE | 3 | 4 | 0.036871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_5841-21_0_1_line_5 | NAYY 4x150 SE | 4 | 5 | 0.01062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_5841-21_0_1_line_6 | NAYY 4x150 SE | 6 | 7 | 0.022049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_5841-21_0_1_line_7 | NAYY 4x150 SE | 6 | 8 | 0.1194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_5841-21_0_1_line_8 | NAYY 4x150 SE | 6 | 9 | 0.12077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_5841-21_0_1_line_9 | NAYY 4x150 SE | 7 | 10 | 0.013914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_5841-21_0_1_line_10 | NAYY 4x150 SE | 8 | 11 | 0.083228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_5841-21_0_1_line_11 | NAYY 4x150 SE | 9 | 24 | 0.082273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_5841-21_0_1_line_12 | NAYY 4x150 SE | 10 | 12 | 0.016385 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_5841-21_0_1_line_13 | NAYY 4x150 SE | 11 | 13 | 0.029109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_5841-21_0_1_line_14 | NAYY 4x150 SE | 13 | 14 | 0.029203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_5841-21_0_1_line_15 | NAYY 4x150 SE | 14 | 30 | 0.010192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_5841-21_0_1_line_16 | NAYY 4x150 SE | 14 | 28 | 0.025127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_5841-21_0_1_line_17 | NAYY 4x150 SE | 15 | 16 | 0.010906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_5841-21_0_1_line_18 | NAYY 4x150 SE | 16 | 17 | 0.42781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_5841-21_0_1_line_19 | NAYY 4x150 SE | 17 | 45 | 0.10972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_5841-21_0_1_line_20 | NAYY 4x150 SE | 18 | 19 | 0.11818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_5841-21_0_1_line_21 | NAYY 4x150 SE | 18 | 20 | 0.061804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_5841-21_0_1_line_22 | NAYY 4x150 SE | 19 | 21 | 0.013663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_5841-21_0_1_line_23 | NAYY 4x150 SE | 20 | 22 | 0.17206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_5841-21_0_1_line_24 | NAYY 4x150 SE | 21 | 23 | 0.038556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_5841-21_0_1_line_25 | NAYY 4x150 SE | 22 | 34 | 0.029559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_5841-21_0_1_line_26 | NAYY 4x150 SE | 22 | 31 | 0.036295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_5841-21_0_1_line_27 | NAYY 4x150 SE | 23 | 29 | 0.15905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_5841-21_0_1_line_28 | NAYY 4x150 SE | 24 | 25 | 0.029783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_5841-21_0_1_line_29 | NAYY 4x150 SE | 25 | 26 | 0.088302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_5841-21_0_1_line_30 | NAYY 4x150 SE | 27 | 28 | 0.040244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_5841-21_0_1_line_31 | NAYY 4x150 SE | 29 | 45 | 0.43642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_5841-21_0_1_line_32 | NAYY 4x150 SE | 30 | 38 | 0.0096448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_5841-21_0_1_line_33 | NAYY 4x150 SE | 31 | 32 | 0.022353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_5841-21_0_1_line_34 | NAYY 4x150 SE | 32 | 33 | 0.0049125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_5841-21_0_1_line_35 | NAYY 4x150 SE | 33 | 35 | 0.018365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_5841-21_0_1_line_36 | NAYY 4x150 SE | 34 | 36 | 0.17146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_5841-21_0_1_line_37 | NAYY 4x150 SE | 35 | 37 | 0.028745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_5841-21_0_1_line_38 | NAYY 4x150 SE | 36 | 39 | 0.0090424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_5841-21_0_1_line_39 | NAYY 4x150 SE | 38 | 44 | 0.0053828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_5841-21_0_1_line_40 | NAYY 4x150 SE | 39 | 40 | 0.033328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_5841-21_0_1_line_41 | NAYY 4x150 SE | 40 | 41 | 0.021611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_5841-21_0_1_line_42 | NAYY 4x150 SE | 41 | 42 | 0.09742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_5841-21_0_1_line_43 | NAYY 4x150 SE | 42 | 43 | 0.011374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_5841-21_0_1_line_44 | NAYY 4x150 SE | 43 | 44 | 0.02068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5841-21_0_1_trafo_10 | 0.25 MVA 20/0.4 kV | 46 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2579825.0919 | 1147832.1614 | 2579841.8943 | 1147820.0766 | 2579853.4187 | 1147817.1587 | 2579860.1877 | 1147820.5043 | 2579863.3384 | 1147825.7518 | 2579863.3591 | 1147831.9104 | 2579861.0645 | 1147836.9317
1 | 2579734.6385 | 1147660.5038 | 2579825.0919 | 1147832.1614
2 | 2579846.6977 | 1147850.9423 | 2579857.2119 | 1147842.2027 | 2579861.0645 | 1147836.9317 | 2579861.0645 | 1147836.9317
3 | 2579658.1151 | 1147561.9915 | 2579656.682 | 1147576.4479 | 2579656.5734 | 1147591.9782 | 2579659.255 | 1147606.0093 | 2579670.2425 | 1147614.5096 | 2579697.6566 | 1147632.1589 | 2579734.6385 | 1147660.5038
4 | 2579872.8478 | 1147874.7853 | 2579855.6333 | 1147861.5065 | 2579848.2015 | 1147857.4183 | 2579846.6977 | 1147850.9423 | 2579846.6977 | 1147850.9423
5 | 2579881.2571 | 1147881.272 | 2579872.8478 | 1147874.7853
6 | 2579658.9947 | 1147529.2168 | 2579663.4128 | 1147543.4977 | 2579664.6544 | 1147550.4883
7 | 2579613.9098 | 1147421.3721 | 2579611.1211 | 1147432.387 | 2579634.7769 | 1147482.8093 | 2579658.9947 | 1147529.2168
8 | 2579658.9947 | 1147529.2168 | 2579753.7747 | 1147454.3759
9 | 2579658.1151 | 1147561.9915 | 2579665.0882 | 1147552.9301 | 2579664.6544 | 1147550.4883
10 | 2579534.4907 | 1147395.763 | 2579613.9098 | 1147421.3721
11 | 2579824.1214 | 1147496.9277 | 2579817.9546 | 1147492.5955 | 2579756.2996 | 1147455.3625 | 2579753.7747 | 1147454.3759
12 | 2579658.1151 | 1147561.9915 | 2579648.233 | 1147562.4363 | 2579643.7976 | 1147557.6952
13 | 2579534.4907 | 1147395.763 | 2579534.9356 | 1147386.6237 | 2579534.6822 | 1147379.8545 | 2579530.0166 | 1147367.5222
14 | 2579524.8505 | 1147338.9012 | 2579527.9787 | 1147362.1353 | 2579530.0166 | 1147367.5222
15 | 2579524.8505 | 1147338.9012 | 2579517.4038 | 1147331.9423
16 | 2579524.8505 | 1147338.9012 | 2579543.4457 | 1147355.7997
17 | 2579034.5139 | 1147318.3531 | 2579044.8748 | 1147321.7574
18 | 2579034.5139 | 1147318.3531 | 2578779.5797 | 1147661.9044
19 | 2578779.5797 | 1147661.9044 | 2578792.9778 | 1147674.2187 | 2578819.1332 | 1147684.8872 | 2578840.018 | 1147697.0529 | 2578855.6993 | 1147703.5675 | 2578864.0115 | 1147724.0706
20 | 2579232.3819 | 1147366.5084 | 2579244.8591 | 1147379.1048 | 2579286.1501 | 1147404.8304 | 2579333.5982 | 1147425.6104 | 2579333.5982 | 1147425.6104
21 | 2579212.321 | 1147308.5158 | 2579229.3994 | 1147363.495 | 2579232.3819 | 1147366.5084
22 | 2579333.5982 | 1147425.6104 | 2579344.4309 | 1147433.9373
23 | 2579212.321 | 1147308.5158 | 2579247.0358 | 1147139.9988
24 | 2579375.8176 | 1147456.0017 | 2579370.1967 | 1147453.7429 | 2579344.4309 | 1147433.9373
25 | 2579275.9471 | 1147145.1887 | 2579268.3476 | 1147142.329 | 2579247.0358 | 1147139.9988
26 | 2579210.9559 | 1147136.054 | 2579247.0358 | 1147139.9988
27 | 2579375.8176 | 1147456.0017 | 2579275.872 | 1147579.73
28 | 2579848.4919 | 1147514.0479 | 2579824.1214 | 1147496.9277
29 | 2579848.4919 | 1147514.0479 | 2579847.0208 | 1147505.9155 | 2579842.0199 | 1147489.502 | 2579834.9678 | 1147475.1519 | 2579830.8558 | 1147428.4427
30 | 2579573.5406 | 1147382.5012 | 2579567.2979 | 1147377.4756 | 2579543.4457 | 1147355.7997
31 | 2579275.872 | 1147579.73 | 2578864.0115 | 1147724.0706
32 | 2579517.4038 | 1147331.9423 | 2579510.357 | 1147325.3571
33 | 2579210.9559 | 1147136.054 | 2579204.8782 | 1147135.3895 | 2579188.9475 | 1147132.2377
34 | 2579188.9475 | 1147132.2377 | 2579184.1284 | 1147131.2843
35 | 2579166.1131 | 1147127.7201 | 2579184.1284 | 1147131.2843
36 | 2579446.8739 | 1147158.6565 | 2579275.9471 | 1147145.1887
37 | 2579166.1131 | 1147127.7201 | 2579137.9153 | 1147122.1375
38 | 2579446.8739 | 1147158.6565 | 2579451.9453 | 1147166.1428
39 | 2579510.357 | 1147325.3571 | 2579508.648 | 1147323.7601 | 2579507.5613 | 1147320.9169
40 | 2579449.2225 | 1147198.5904 | 2579447.7878 | 1147192.2922 | 2579447.1594 | 1147185.9467 | 2579451.5205 | 1147172.1472 | 2579451.9453 | 1147166.1428
41 | 2579449.2225 | 1147198.5904 | 2579451.327 | 1147203.1076 | 2579457.3601 | 1147213.3365 | 2579460.3657 | 1147217.0167
42 | 2579460.3657 | 1147217.0167 | 2579476.155 | 1147236.3502 | 2579483.8691 | 1147250.8198 | 2579486.0155 | 1147263.1186 | 2579485.955 | 1147283.6289 | 2579480.0948 | 1147305.9377 | 2579480.0948 | 1147305.9377
43 | 2579490.4162 | 1147310.7154 | 2579480.0948 | 1147305.9377
44 | 2579490.4162 | 1147310.7154 | 2579506.5093 | 1147318.1646 | 2579507.5613 | 1147320.9169

## bus_geodata
| x | y | coords
0 | 2579825.0919 | 1147832.1614
1 | 2579861.0645 | 1147836.9317
2 | 2579734.6385 | 1147660.5038
3 | 2579846.6977 | 1147850.9423
4 | 2579872.8478 | 1147874.7853
5 | 2579881.2571 | 1147881.272
6 | 2579658.9947 | 1147529.2168
7 | 2579664.6544 | 1147550.4883
8 | 2579613.9098 | 1147421.3721
9 | 2579753.7747 | 1147454.3759
10 | 2579658.1151 | 1147561.9915
11 | 2579534.4907 | 1147395.763
12 | 2579643.7976 | 1147557.6952
13 | 2579530.0166 | 1147367.5222
14 | 2579524.8505 | 1147338.9012
15 | 2579044.8748 | 1147321.7574
16 | 2579034.5139 | 1147318.3531
17 | 2578779.5797 | 1147661.9044
18 | 2579232.3819 | 1147366.5084
19 | 2579333.5982 | 1147425.6104
20 | 2579212.321 | 1147308.5158
21 | 2579344.4309 | 1147433.9373
22 | 2579247.0358 | 1147139.9988
23 | 2579375.8176 | 1147456.0017
24 | 2579824.1214 | 1147496.9277
25 | 2579848.4919 | 1147514.0479
26 | 2579830.8558 | 1147428.4427
27 | 2579573.5406 | 1147382.5012
28 | 2579543.4457 | 1147355.7997
29 | 2579275.872 | 1147579.73
30 | 2579517.4038 | 1147331.9423
31 | 2579210.9559 | 1147136.054
32 | 2579188.9475 | 1147132.2377
33 | 2579184.1284 | 1147131.2843
34 | 2579275.9471 | 1147145.1887
35 | 2579166.1131 | 1147127.7201
36 | 2579446.8739 | 1147158.6565
37 | 2579137.9153 | 1147122.1375
38 | 2579510.357 | 1147325.3571
39 | 2579451.9453 | 1147166.1428
40 | 2579449.2225 | 1147198.5904
41 | 2579460.3657 | 1147217.0167
42 | 2579480.0948 | 1147305.9377
43 | 2579490.4162 | 1147310.7154
44 | 2579507.5613 | 1147320.9169
45 | 2578864.0115 | 1147724.0706
46 | 2579643.7976 | 1147557.6952

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1