## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_602-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_602-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_602-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_602-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_602-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_602-1_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_602-1_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_602-1_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_602-1_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_602-1_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_602-1_0_4_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_602-1_0_4_node_316 | 0.4 | n |  | TRUE
12 | bus_LV_602-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_602-1_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_602-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_602-1_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_602-1_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_602-1_0_4_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_602-1_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_602-1_0_4_node_325 | 0.4 | n |  | TRUE
20 | bus_LV_602-1_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_602-1_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_602-1_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_602-1_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_602-1_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_602-1_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_602-1_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_602-1_0_4_node_295 | 0.4 | n |  | TRUE
28 | bus_LV_602-1_0_4_node_324 | 0.4 | n |  | TRUE
29 | bus_LV_602-1_0_4_node_301 | 0.4 | n |  | TRUE
30 | bus_LV_602-1_0_4_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_602-1_0_4_node_64 | 0.4 | n |  | TRUE
32 | bus_LV_602-1_0_4_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_602-1_0_4_node_71 | 0.4 | n |  | TRUE
34 | bus_LV_602-1_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_602-1_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_602-1_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_602-1_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_602-1_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_602-1_0_4_node_56 | 0.4 | n |  | TRUE
40 | bus_LV_602-1_0_4_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_602-1_0_4_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_602-1_0_4_node_29 | 0.4 | n |  | TRUE
43 | bus_LV_602-1_0_4_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_602-1_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_602-1_0_4_node_269 | 0.4 | n |  | TRUE
46 | bus_LV_602-1_0_4_node_267 | 0.4 | n |  | TRUE
47 | bus_LV_602-1_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_602-1_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_602-1_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_602-1_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_602-1_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_602-1_0_4_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_602-1_0_4_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_602-1_0_4_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_602-1_0_4_node_54 | 0.4 | n |  | TRUE
56 | bus_LV_602-1_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_602-1_0_4_node_67 | 0.4 | n |  | TRUE
58 | bus_LV_602-1_0_4_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_602-1_0_4_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_602-1_0_4_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_602-1_0_4_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_602-1_0_4_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_602-1_0_4_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_602-1_0_4_node_299 | 0.4 | n |  | TRUE
65 | bus_LV_602-1_0_4_node_244 | 0.4 | n |  | TRUE
66 | bus_LV_602-1_0_4_node_318 | 0.4 | n |  | TRUE
67 | bus_LV_602-1_0_4_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_602-1_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_602-1_0_4_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_602-1_0_4_node_72 | 0.4 | n |  | TRUE
71 | bus_LV_602-1_0_4_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_602-1_0_4_node_250 | 0.4 | n |  | TRUE
73 | bus_LV_602-1_0_4_node_75 | 0.4 | n |  | TRUE
74 | bus_LV_602-1_0_4_node_207 | 0.4 | n |  | TRUE
75 | bus_LV_602-1_0_4_node_208 | 0.4 | n |  | TRUE
76 | bus_LV_602-1_0_4_node_209 | 0.4 | n |  | TRUE
77 | bus_LV_602-1_0_4_node_210 | 0.4 | n |  | TRUE
78 | bus_LV_602-1_0_4_node_211 | 0.4 | n |  | TRUE
79 | bus_LV_602-1_0_4_node_296 | 0.4 | n |  | TRUE
80 | bus_LV_602-1_0_4_node_238 | 0.4 | n |  | TRUE
81 | bus_LV_602-1_0_4_node_239 | 0.4 | n |  | TRUE
82 | bus_LV_602-1_0_4_node_240 | 0.4 | n |  | TRUE
83 | bus_LV_602-1_0_4_node_242 | 0.4 | n |  | TRUE
84 | bus_LV_602-1_0_4_node_243 | 0.4 | n |  | TRUE
85 | bus_LV_602-1_0_4_node_246 | 0.4 | n |  | TRUE
86 | bus_LV_602-1_0_4_node_245 | 0.4 | n |  | TRUE
87 | bus_LV_602-1_0_4_node_306 | 0.4 | n |  | TRUE
88 | bus_LV_602-1_0_4_node_298 | 0.4 | n |  | TRUE
89 | bus_LV_602-1_0_4_node_247 | 0.4 | n |  | TRUE
90 | bus_LV_602-1_0_4_node_248 | 0.4 | n |  | TRUE
91 | bus_LV_602-1_0_4_node_251 | 0.4 | n |  | TRUE
92 | bus_LV_602-1_0_4_node_252 | 0.4 | n |  | TRUE
93 | bus_LV_602-1_0_4_node_253 | 0.4 | n |  | TRUE
94 | bus_LV_602-1_0_4_node_321 | 0.4 | n |  | TRUE
95 | bus_LV_602-1_0_4_node_257 | 0.4 | n |  | TRUE
96 | bus_LV_602-1_0_4_node_254 | 0.4 | n |  | TRUE
97 | bus_LV_602-1_0_4_node_255 | 0.4 | n |  | TRUE
98 | bus_LV_602-1_0_4_node_256 | 0.4 | n |  | TRUE
99 | bus_LV_602-1_0_4_node_258 | 0.4 | n |  | TRUE
100 | bus_LV_602-1_0_4_node_259 | 0.4 | n |  | TRUE
101 | bus_LV_602-1_0_4_node_260 | 0.4 | n |  | TRUE
102 | bus_LV_602-1_0_4_node_272 | 0.4 | n |  | TRUE
103 | bus_LV_602-1_0_4_node_261 | 0.4 | n |  | TRUE
104 | bus_LV_602-1_0_4_node_262 | 0.4 | n |  | TRUE
105 | bus_LV_602-1_0_4_node_263 | 0.4 | n |  | TRUE
106 | bus_LV_602-1_0_4_node_265 | 0.4 | n |  | TRUE
107 | bus_LV_602-1_0_4_node_266 | 0.4 | n |  | TRUE
108 | bus_LV_602-1_0_4_node_270 | 0.4 | n |  | TRUE
109 | bus_LV_602-1_0_4_node_268 | 0.4 | n |  | TRUE
110 | bus_LV_602-1_0_4_node_275 | 0.4 | n |  | TRUE
111 | bus_LV_602-1_0_4_node_276 | 0.4 | n |  | TRUE
112 | bus_LV_602-1_0_4_node_271 | 0.4 | n |  | TRUE
113 | bus_LV_602-1_0_4_node_273 | 0.4 | n |  | TRUE
114 | bus_LV_602-1_0_4_node_274 | 0.4 | n |  | TRUE
115 | bus_LV_602-1_0_4_node_277 | 0.4 | n |  | TRUE
116 | bus_LV_602-1_0_4_node_278 | 0.4 | n |  | TRUE
117 | bus_LV_602-1_0_4_node_279 | 0.4 | n |  | TRUE
118 | bus_LV_602-1_0_4_node_281 | 0.4 | n |  | TRUE
119 | bus_LV_602-1_0_4_node_280 | 0.4 | n |  | TRUE
120 | bus_LV_602-1_0_4_node_302 | 0.4 | n |  | TRUE
121 | bus_LV_602-1_0_4_node_282 | 0.4 | n |  | TRUE
122 | bus_LV_602-1_0_4_node_283 | 0.4 | n |  | TRUE
123 | bus_LV_602-1_0_4_node_291 | 0.4 | n |  | TRUE
124 | bus_LV_602-1_0_4_node_323 | 0.4 | n |  | TRUE
125 | bus_LV_602-1_0_4_node_284 | 0.4 | n |  | TRUE
126 | bus_LV_602-1_0_4_node_285 | 0.4 | n |  | TRUE
127 | bus_LV_602-1_0_4_node_286 | 0.4 | n |  | TRUE
128 | bus_LV_602-1_0_4_node_288 | 0.4 | n |  | TRUE
129 | bus_LV_602-1_0_4_node_287 | 0.4 | n |  | TRUE
130 | bus_LV_602-1_0_4_node_290 | 0.4 | n |  | TRUE
131 | bus_LV_602-1_0_4_node_292 | 0.4 | n |  | TRUE
132 | bus_LV_602-1_0_4_node_289 | 0.4 | n |  | TRUE
133 | bus_LV_602-1_0_4_node_293 | 0.4 | n |  | TRUE
134 | bus_LV_602-1_0_4_node_294 | 0.4 | n |  | TRUE
135 | bus_LV_602-1_0_4_node_297 | 0.4 | n |  | TRUE
136 | bus_LV_602-1_0_4_node_300 | 0.4 | n |  | TRUE
137 | bus_LV_602-1_0_4_node_304 | 0.4 | n |  | TRUE
138 | bus_LV_602-1_0_4_node_305 | 0.4 | n |  | TRUE
139 | bus_LV_602-1_0_4_node_303 | 0.4 | n |  | TRUE
140 | bus_LV_602-1_0_4_node_317 | 0.4 | n |  | TRUE
141 | bus_LV_602-1_0_4_node_307 | 0.4 | n |  | TRUE
142 | bus_LV_602-1_0_4_node_308 | 0.4 | n |  | TRUE
143 | bus_LV_602-1_0_4_node_311 | 0.4 | n |  | TRUE
144 | bus_LV_602-1_0_4_node_312 | 0.4 | n |  | TRUE
145 | bus_LV_602-1_0_4_node_313 | 0.4 | n |  | TRUE
146 | bus_LV_602-1_0_4_node_314 | 0.4 | n |  | TRUE
147 | bus_LV_602-1_0_4_node_315 | 0.4 | n |  | TRUE
148 | bus_LV_602-1_0_4_node_319 | 0.4 | n |  | TRUE
149 | bus_MV_94_0_node_157 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_602-1_0_4_load_0 | 0 | 0.00038308 | 9.601e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_602-1_0_4_load_1 | 1 | 0.00037492 | 9.3964e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_602-1_0_4_load_2 | 2 | 0.001017 | 0.00025489 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_602-1_0_4_load_4 | 4 | 0.00041864 | 0.00010492 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_602-1_0_4_load_5 | 5 | 0.00020195 | 5.0614e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_602-1_0_4_load_23 | 7 | 0.00047948 | 0.00012017 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_602-1_0_4_load_13 | 10 | 0.00059801 | 0.00014988 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_602-1_0_4_load_316 | 11 | 0.00042569 | 0.00010669 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_602-1_0_4_load_8 | 12 | 0.0014235 | 0.00035676 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_602-1_0_4_load_9 | 13 | 0.0006967 | 0.00017461 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_602-1_0_4_load_22 | 18 | 0.0013978 | 0.00035032 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_602-1_0_4_load_325 | 19 | 0.00041562 | 0.00010416 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_602-1_0_4_load_14 | 20 | 0.0014346 | 0.00035955 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_602-1_0_4_load_15 | 21 | 0.00072202 | 0.00018096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_602-1_0_4_load_16 | 22 | 0.00041111 | 0.00010303 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_602-1_0_4_load_31 | 26 | 0.00040567 | 0.00010167 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_602-1_0_4_load_295 | 27 | 0.00042156 | 0.00010565 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_602-1_0_4_load_324 | 28 | 0.0013077 | 0.00032775 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_602-1_0_4_load_64 | 31 | 0.0014279 | 0.00035785 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_602-1_0_4_load_53 | 32 | 0.0043041 | 0.0010787 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_602-1_0_4_load_71 | 33 | 0.00072528 | 0.00018177 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_602-1_0_4_load_24 | 34 | 0.00071354 | 0.00017883 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_602-1_0_4_load_26 | 36 | 0.00010685 | 2.6779e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_602-1_0_4_load_27 | 37 | 0.001389 | 0.00034813 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_602-1_0_4_load_56 | 39 | 0.0011475 | 0.0002876 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_602-1_0_4_load_74 | 41 | 0.0010593 | 0.00026548 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_602-1_0_4_load_29 | 42 | 0.0003867 | 9.6915e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_602-1_0_4_load_30 | 43 | 0.00038118 | 9.5532e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_602-1_0_4_load_269 | 45 | 0.0027627 | 0.0006924 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_602-1_0_4_load_267 | 46 | 0.00041883 | 0.00010497 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_602-1_0_4_load_33 | 47 | 0.0015061 | 0.00037746 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_602-1_0_4_load_34 | 48 | 0.00059498 | 0.00014912 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_602-1_0_4_load_38 | 51 | 0.00073911 | 0.00018524 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_602-1_0_4_load_66 | 54 | 0.00096937 | 0.00024295 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_602-1_0_4_load_54 | 55 | 0.00049934 | 0.00012515 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_602-1_0_4_load_55 | 56 | 0.0016862 | 0.0004226 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_602-1_0_4_load_58 | 58 | 0.0017103 | 0.00042864 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_602-1_0_4_load_59 | 59 | 0.00063936 | 0.00016024 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_602-1_0_4_load_299 | 64 | 0.00061619 | 0.00015443 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_602-1_0_4_load_318 | 66 | 0.0031238 | 0.00078289 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_602-1_0_4_load_76 | 67 | 0.002043 | 0.00051203 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_602-1_0_4_load_68 | 68 | 0.00018139 | 4.546e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_602-1_0_4_load_69 | 69 | 0.00033674 | 8.4394e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_602-1_0_4_load_73 | 71 | 0.0038208 | 0.00095759 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_602-1_0_4_load_250 | 72 | 0.00030394 | 7.6174e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_602-1_0_4_load_75 | 73 | 0.00026212 | 6.5695e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_602-1_0_4_load_207 | 74 | 0.00033135 | 8.3045e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_602-1_0_4_load_208 | 75 | 0.0012077 | 0.00030268 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_602-1_0_4_load_210 | 77 | 0.00024827 | 6.2221e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_602-1_0_4_load_211 | 78 | 0.00074321 | 0.00018627 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_602-1_0_4_load_296 | 79 | 0.0002325 | 5.827e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_602-1_0_4_load_238 | 80 | 0.00021054 | 5.2766e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_602-1_0_4_load_239 | 81 | 0.00048479 | 0.0001215 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_602-1_0_4_load_242 | 83 | 0.00066548 | 0.00016679 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_602-1_0_4_load_243 | 84 | 0.00048215 | 0.00012084 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_602-1_0_4_load_246 | 85 | 0.00047539 | 0.00011914 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_602-1_0_4_load_306 | 87 | 0.00050651 | 0.00012694 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_602-1_0_4_load_298 | 88 | 0.00028651 | 7.1807e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_602-1_0_4_load_248 | 90 | 0.0018159 | 0.00045511 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_602-1_0_4_load_251 | 91 | 0.0012638 | 0.00031673 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_602-1_0_4_load_321 | 94 | 0.00017883 | 4.482e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_602-1_0_4_load_257 | 95 | 0.0028091 | 0.00070403 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_602-1_0_4_load_254 | 96 | 0.0011629 | 0.00029145 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_602-1_0_4_load_255 | 97 | 0.0003439 | 8.619e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_602-1_0_4_load_256 | 98 | 0.00012208 | 3.0596e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_602-1_0_4_load_258 | 99 | 0.00045811 | 0.00011481 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_602-1_0_4_load_272 | 102 | 0.0021628 | 0.00054204 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_602-1_0_4_load_261 | 103 | 0.00069888 | 0.00017515 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_602-1_0_4_load_268 | 109 | 0.0022584 | 0.00056601 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_602-1_0_4_load_275 | 110 | 0.0011575 | 0.00029009 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_602-1_0_4_load_271 | 112 | 0.0021108 | 0.00052902 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_602-1_0_4_load_273 | 113 | 0.00052276 | 0.00013101 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_602-1_0_4_load_274 | 114 | 0.00084409 | 0.00021155 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_602-1_0_4_load_277 | 115 | 0.0001876 | 4.7017e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_602-1_0_4_load_278 | 116 | 0.00089828 | 0.00022513 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_602-1_0_4_load_279 | 117 | 0.00059087 | 0.00014809 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_602-1_0_4_load_291 | 123 | 0.00090832 | 0.00022765 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_602-1_0_4_load_323 | 124 | 0.00062099 | 0.00015563 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_602-1_0_4_load_284 | 125 | 0.00182 | 0.00045613 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_602-1_0_4_load_285 | 126 | 0.0002322 | 5.8196e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_602-1_0_4_load_288 | 128 | 0.0016266 | 0.00040765 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_602-1_0_4_load_292 | 131 | 0.00057988 | 0.00014533 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_602-1_0_4_load_289 | 132 | 0.00044853 | 0.00011241 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_602-1_0_4_load_293 | 133 | 0.00044114 | 0.00011056 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_602-1_0_4_load_294 | 134 | 0.00049188 | 0.00012328 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_602-1_0_4_load_300 | 136 | 0.00017524 | 4.392e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_602-1_0_4_load_304 | 137 | 0.0010023 | 0.00025121 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_602-1_0_4_load_305 | 138 | 0.00053756 | 0.00013473 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_602-1_0_4_load_303 | 139 | 0.001151 | 0.00028846 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_602-1_0_4_load_317 | 140 | 0.00064624 | 0.00016196 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_602-1_0_4_load_308 | 142 | 9.1856e-05 | 2.3021e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_602-1_0_4_load_311 | 143 | 0.0013236 | 0.00033173 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_602-1_0_4_load_313 | 145 | 0.00047379 | 0.00011874 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_602-1_0_4_load_314 | 146 | 0.00044091 | 0.0001105 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_602-1_0_4_load_315 | 147 | 0.0006352 | 0.0001592 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_602-1_0_4_load_319 | 148 | 0.00069985 | 0.0001754 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_602-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.016752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_602-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.023953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_602-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0042049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_602-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0033071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_602-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.006676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_602-1_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.035711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_602-1_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.005929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_602-1_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0097422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_602-1_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.01521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_602-1_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0090577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_602-1_0_4_line_10 | NAYY 4x150 SE | 7 | 33 | 0.012363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_602-1_0_4_line_11 | NAYY 4x150 SE | 8 | 23 | 0.022498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_602-1_0_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.010527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_602-1_0_4_line_13 | NAYY 4x150 SE | 10 | 20 | 0.023867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_602-1_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.015891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_602-1_0_4_line_15 | NAYY 4x150 SE | 12 | 14 | 0.0015491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_602-1_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.026534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_602-1_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.4245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_602-1_0_4_line_18 | NAYY 4x150 SE | 15 | 17 | 0.036081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_602-1_0_4_line_19 | NAYY 4x150 SE | 15 | 18 | 0.031654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_602-1_0_4_line_20 | NAYY 4x150 SE | 16 | 19 | 0.11696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_602-1_0_4_line_21 | NAYY 4x150 SE | 17 | 30 | 0.008263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_602-1_0_4_line_22 | NAYY 4x150 SE | 17 | 31 | 0.0075348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_602-1_0_4_line_23 | NAYY 4x150 SE | 18 | 32 | 0.0074001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_602-1_0_4_line_24 | NAYY 4x150 SE | 21 | 22 | 0.025319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_602-1_0_4_line_25 | NAYY 4x150 SE | 21 | 23 | 0.034858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_602-1_0_4_line_26 | NAYY 4x150 SE | 22 | 24 | 0.020016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_602-1_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.053238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_602-1_0_4_line_28 | NAYY 4x150 SE | 24 | 26 | 0.012541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_602-1_0_4_line_29 | NAYY 4x150 SE | 24 | 27 | 0.010954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_602-1_0_4_line_30 | NAYY 4x150 SE | 25 | 28 | 0.030355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_602-1_0_4_line_31 | NAYY 4x150 SE | 25 | 29 | 0.058278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_602-1_0_4_line_32 | NAYY 4x150 SE | 26 | 42 | 0.0025676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_602-1_0_4_line_33 | NAYY 4x150 SE | 27 | 134 | 0.01847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_602-1_0_4_line_34 | NAYY 4x150 SE | 29 | 137 | 0.047965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_602-1_0_4_line_35 | NAYY 4x150 SE | 29 | 63 | 0.15259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_602-1_0_4_line_36 | NAYY 4x150 SE | 30 | 52 | 0.016551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_602-1_0_4_line_37 | NAYY 4x150 SE | 31 | 61 | 0.010831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_602-1_0_4_line_38 | NAYY 4x150 SE | 32 | 55 | 0.01044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_602-1_0_4_line_39 | NAYY 4x150 SE | 33 | 71 | 0.016043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_602-1_0_4_line_40 | NAYY 4x150 SE | 34 | 35 | 0.045423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_602-1_0_4_line_41 | NAYY 4x150 SE | 34 | 36 | 0.0051106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_602-1_0_4_line_42 | NAYY 4x150 SE | 35 | 37 | 0.0053842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_602-1_0_4_line_43 | NAYY 4x150 SE | 35 | 38 | 0.020149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_602-1_0_4_line_44 | NAYY 4x150 SE | 37 | 39 | 0.028569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_602-1_0_4_line_45 | NAYY 4x150 SE | 38 | 40 | 0.005604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_602-1_0_4_line_46 | NAYY 4x150 SE | 38 | 41 | 0.018228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_602-1_0_4_line_47 | NAYY 4x150 SE | 39 | 53 | 0.022069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_602-1_0_4_line_48 | NAYY 4x150 SE | 40 | 70 | 0.1047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_602-1_0_4_line_49 | NAYY 4x150 SE | 40 | 69 | 0.015231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_602-1_0_4_line_50 | NAYY 4x150 SE | 41 | 73 | 0.019168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_602-1_0_4_line_51 | NAYY 4x150 SE | 43 | 44 | 0.010219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_602-1_0_4_line_52 | NAYY 4x150 SE | 44 | 45 | 0.03703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_602-1_0_4_line_53 | NAYY 4x150 SE | 44 | 46 | 0.26978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_602-1_0_4_line_54 | NAYY 4x150 SE | 45 | 111 | 0.025962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_602-1_0_4_line_55 | NAYY 4x150 SE | 46 | 109 | 0.037218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_602-1_0_4_line_56 | NAYY 4x150 SE | 47 | 48 | 0.0083102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_602-1_0_4_line_57 | NAYY 4x150 SE | 47 | 49 | 0.0069756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_602-1_0_4_line_58 | NAYY 4x150 SE | 49 | 50 | 0.006852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_602-1_0_4_line_59 | NAYY 4x150 SE | 49 | 51 | 0.013287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_602-1_0_4_line_60 | NAYY 4x150 SE | 50 | 53 | 0.019611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_602-1_0_4_line_61 | NAYY 4x150 SE | 51 | 54 | 0.0078729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_602-1_0_4_line_62 | NAYY 4x150 SE | 52 | 57 | 0.047773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_602-1_0_4_line_63 | NAYY 4x150 SE | 52 | 67 | 0.0083113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_602-1_0_4_line_64 | NAYY 4x150 SE | 53 | 57 | 0.016319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_602-1_0_4_line_65 | NAYY 4x150 SE | 55 | 56 | 0.025912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_602-1_0_4_line_66 | NAYY 4x150 SE | 58 | 59 | 0.0020564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_602-1_0_4_line_67 | NAYY 4x150 SE | 58 | 60 | 0.037531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_602-1_0_4_line_68 | NAYY 4x150 SE | 59 | 61 | 0.015006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_602-1_0_4_line_69 | NAYY 4x150 SE | 60 | 62 | 0.26517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_602-1_0_4_line_70 | NAYY 4x150 SE | 62 | 65 | 0.38421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_602-1_0_4_line_71 | NAYY 4x150 SE | 62 | 66 | 0.2301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_602-1_0_4_line_72 | NAYY 4x150 SE | 63 | 64 | 0.02571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_602-1_0_4_line_73 | NAYY 4x150 SE | 64 | 136 | 0.011109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_602-1_0_4_line_74 | NAYY 4x150 SE | 65 | 86 | 0.015174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_602-1_0_4_line_75 | NAYY 4x150 SE | 65 | 83 | 0.28197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_602-1_0_4_line_76 | NAYY 4x150 SE | 66 | 148 | 0.020679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_602-1_0_4_line_77 | NAYY 4x150 SE | 67 | 71 | 0.019245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_602-1_0_4_line_78 | NAYY 4x150 SE | 68 | 69 | 0.041258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_602-1_0_4_line_79 | NAYY 4x150 SE | 70 | 72 | 0.04041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_602-1_0_4_line_80 | NAYY 4x150 SE | 72 | 91 | 0.022972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_602-1_0_4_line_81 | NAYY 4x150 SE | 74 | 75 | 0.0012056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_602-1_0_4_line_82 | NAYY 4x150 SE | 74 | 76 | 0.012896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_602-1_0_4_line_83 | NAYY 4x150 SE | 75 | 77 | 0.027428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_602-1_0_4_line_84 | NAYY 4x150 SE | 76 | 78 | 0.21699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_602-1_0_4_line_85 | NAYY 4x150 SE | 78 | 79 | 0.0043597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_602-1_0_4_line_86 | NAYY 4x150 SE | 79 | 135 | 0.21865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_602-1_0_4_line_87 | NAYY 4x150 SE | 80 | 81 | 0.011563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_602-1_0_4_line_88 | NAYY 4x150 SE | 80 | 82 | 0.017107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_602-1_0_4_line_89 | NAYY 4x150 SE | 82 | 83 | 0.032699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_602-1_0_4_line_90 | NAYY 4x150 SE | 82 | 84 | 0.1184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_602-1_0_4_line_91 | NAYY 4x150 SE | 84 | 85 | 0.001366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_602-1_0_4_line_92 | NAYY 4x150 SE | 85 | 89 | 0.016946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_602-1_0_4_line_93 | NAYY 4x150 SE | 86 | 87 | 0.18001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_602-1_0_4_line_94 | NAYY 4x150 SE | 86 | 88 | 0.11535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_602-1_0_4_line_95 | NAYY 4x150 SE | 87 | 141 | 0.05629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_602-1_0_4_line_96 | NAYY 4x150 SE | 88 | 135 | 0.10607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_602-1_0_4_line_97 | NAYY 4x150 SE | 89 | 90 | 0.023554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_602-1_0_4_line_98 | NAYY 4x150 SE | 92 | 93 | 0.3577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_602-1_0_4_line_99 | NAYY 4x150 SE | 92 | 94 | 0.037907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_602-1_0_4_line_100 | NAYY 4x150 SE | 93 | 95 | 0.083488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_602-1_0_4_line_101 | NAYY 4x150 SE | 93 | 96 | 0.22773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_602-1_0_4_line_102 | NAYY 4x150 SE | 95 | 99 | 0.0071033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_602-1_0_4_line_103 | NAYY 4x150 SE | 96 | 97 | 0.040065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_602-1_0_4_line_104 | NAYY 4x150 SE | 97 | 98 | 0.00070119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_602-1_0_4_line_105 | NAYY 4x150 SE | 99 | 100 | 0.24502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_602-1_0_4_line_106 | NAYY 4x150 SE | 100 | 101 | 0.18905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_602-1_0_4_line_107 | NAYY 4x150 SE | 101 | 102 | 0.30065 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_602-1_0_4_line_108 | NAYY 4x150 SE | 102 | 113 | 0.039568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_602-1_0_4_line_109 | NAYY 4x150 SE | 103 | 104 | 0.091333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_602-1_0_4_line_110 | NAYY 4x150 SE | 103 | 105 | 0.082314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_602-1_0_4_line_111 | NAYY 4x150 SE | 104 | 106 | 0.045524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_602-1_0_4_line_112 | NAYY 4x150 SE | 105 | 107 | 0.10162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_602-1_0_4_line_113 | NAYY 4x150 SE | 106 | 108 | 0.049384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_602-1_0_4_line_114 | NAYY 4x150 SE | 106 | 109 | 0.047558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_602-1_0_4_line_115 | NAYY 4x150 SE | 107 | 110 | 0.089102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_602-1_0_4_line_116 | NAYY 4x150 SE | 108 | 112 | 0.022999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_602-1_0_4_line_117 | NAYY 4x150 SE | 110 | 114 | 0.039546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_602-1_0_4_line_118 | NAYY 4x150 SE | 111 | 115 | 0.044128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
119 | LV_602-1_0_4_line_119 | NAYY 4x150 SE | 111 | 116 | 0.013719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_602-1_0_4_line_120 | NAYY 4x150 SE | 113 | 114 | 0.047759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_602-1_0_4_line_121 | NAYY 4x150 SE | 115 | 117 | 0.00064758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
122 | LV_602-1_0_4_line_122 | NAYY 4x150 SE | 116 | 118 | 0.21866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_602-1_0_4_line_123 | NAYY 4x150 SE | 117 | 119 | 0.095282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
124 | LV_602-1_0_4_line_124 | NAYY 4x150 SE | 118 | 121 | 0.10604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_602-1_0_4_line_125 | NAYY 4x150 SE | 118 | 122 | 0.17455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_602-1_0_4_line_126 | NAYY 4x150 SE | 119 | 120 | 0.096174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
127 | LV_602-1_0_4_line_127 | NAYY 4x150 SE | 120 | 138 | 0.014556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_602-1_0_4_line_128 | NAYY 4x150 SE | 120 | 139 | 0.020861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
129 | LV_602-1_0_4_line_129 | NAYY 4x150 SE | 121 | 123 | 0.02208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_602-1_0_4_line_130 | NAYY 4x150 SE | 122 | 124 | 0.13909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_602-1_0_4_line_131 | NAYY 4x150 SE | 123 | 130 | 0.16995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_602-1_0_4_line_132 | NAYY 4x150 SE | 125 | 126 | 0.016684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_602-1_0_4_line_133 | NAYY 4x150 SE | 125 | 127 | 0.010013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_602-1_0_4_line_134 | NAYY 4x150 SE | 127 | 128 | 0.014805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_602-1_0_4_line_135 | NAYY 4x150 SE | 128 | 132 | 0.018048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_602-1_0_4_line_136 | NAYY 4x150 SE | 129 | 130 | 0.054609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_602-1_0_4_line_137 | NAYY 4x150 SE | 129 | 131 | 0.0082652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_602-1_0_4_line_138 | NAYY 4x150 SE | 130 | 132 | 0.023857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_602-1_0_4_line_139 | NAYY 4x150 SE | 133 | 134 | 0.00069477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_602-1_0_4_line_140 | NAYY 4x150 SE | 137 | 139 | 0.057198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
141 | LV_602-1_0_4_line_141 | NAYY 4x150 SE | 138 | 140 | 0.31164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_602-1_0_4_line_142 | NAYY 4x150 SE | 140 | 147 | 0.030571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_602-1_0_4_line_143 | NAYY 4x150 SE | 141 | 142 | 0.34439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_602-1_0_4_line_144 | NAYY 4x150 SE | 143 | 144 | 0.016362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_602-1_0_4_line_145 | NAYY 4x150 SE | 143 | 145 | 0.021333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_602-1_0_4_line_146 | NAYY 4x150 SE | 144 | 146 | 0.010113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_602-1_0_4_line_147 | NAYY 4x150 SE | 144 | 147 | 0.0224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_602-1_0_4_trafo_20 | 0.25 MVA 20/0.4 kV | 149 | 25 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32
0 | 2617318.6127 | 1198268.3095 | 2617320.8233 | 1198268.68 | 2617330.9468 | 1198270.1323 | 2617335.2109 | 1198270.5373
1 | 2617318.6127 | 1198268.3095 | 2617310.297 | 1198266.9154 | 2617302.3074 | 1198264.8134 | 2617295.5269 | 1198262.2188
2 | 2617339.397 | 1198270.9349 | 2617335.2109 | 1198270.5373
3 | 2617292.5295 | 1198260.8295 | 2617294.5793 | 1198261.8562 | 2617295.5269 | 1198262.2188
4 | 2617339.397 | 1198270.9349 | 2617346.0624 | 1198271.3113
5 | 2617339.397 | 1198270.9349 | 2617335.6069 | 1198278.1278 | 2617332.4863 | 1198282.8547 | 2617329.575 | 1198286.337 | 2617327.9946 | 1198287.7666 | 2617326.2549 | 1198288.9955 | 2617322.2553 | 1198300.1678 | 2617321.9928 | 1198301.3899
6 | 2617292.5295 | 1198260.8295 | 2617289.3554 | 1198259.2397 | 2617287.3225 | 1198258.004
7 | 2617355.7891 | 1198271.8606 | 2617346.0624 | 1198271.3113
8 | 2617309.4373 | 1198293.0269 | 2617316.0527 | 1198296.3033 | 2617318.6899 | 1198298.0897 | 2617320.6264 | 1198299.9185 | 2617321.9928 | 1198301.3899
9 | 2617321.9928 | 1198301.3899 | 2617321.159 | 1198305.3341 | 2617320.6572 | 1198310.3353
10 | 2617287.3225 | 1198258.004 | 2617276.758 | 1198251.582
11 | 2617377.7026 | 1198267.3438 | 2617370.7805 | 1198270.0252 | 2617364.1899 | 1198271.3291 | 2617355.7891 | 1198271.8606
12 | 2617309.4373 | 1198293.0269 | 2617306.6897 | 1198292.5298 | 2617299.2672 | 1198290.3536
13 | 2617323.3606 | 1198334.0114 | 2617321.1774 | 1198320.042 | 2617320.7056 | 1198314.6933 | 2617320.6572 | 1198310.3353
14 | 2617138.1727 | 1198228.9133 | 2617153.3428 | 1198224.1818
15 | 2617136.6939 | 1198229.3745 | 2617138.1727 | 1198228.9133
16 | 2617179.2761 | 1198218.8795 | 2617170.2951 | 1198219.9099 | 2617158.4158 | 1198222.5996 | 2617153.3428 | 1198224.1818
17 | 2616725.2389 | 1198141.366 | 2616734.4211 | 1198141.9141 | 2616745.1929 | 1198143.1448 | 2616759.4024 | 1198145.9082 | 2616770.1224 | 1198149.3511 | 2616823.2221 | 1198168.2544 | 2616842.3121 | 1198173.9888 | 2616861.9233 | 1198178.4685 | 2616881.7428 | 1198181.9706 | 2616990.7432 | 1198195.5634 | 2617006.1557 | 1198198.3085 | 2617018.8167 | 1198201.9242 | 2617029.8851 | 1198205.9133 | 2617043.1329 | 1198212.0431 | 2617070.7519 | 1198225.5511 | 2617087.1462 | 1198231.123 | 2617096.7278 | 1198233.0847 | 2617107.1123 | 1198233.8814 | 2617116.0834 | 1198233.6068 | 2617124.562 | 1198232.486 | 2617136.6939 | 1198229.3745
18 | 2617179.2761 | 1198218.8795 | 2617188.6191 | 1198219.062 | 2617199.1718 | 1198219.6036 | 2617208.1614 | 1198220.8856 | 2617215.2551 | 1198222.0733
19 | 2617179.2761 | 1198218.8795 | 2617180.859 | 1198229.8566 | 2617181.5908 | 1198232.2489 | 2617183.4027 | 1198235.0667 | 2617187.7038 | 1198238.1807 | 2617189.9427 | 1198240.7774 | 2617190.7093 | 1198244.326 | 2617190.8657 | 1198246.6629
20 | 2616725.2389 | 1198141.366 | 2616721.756 | 1198134.1857 | 2616716.7563 | 1198127.5015 | 2616709.7495 | 1198119.6445 | 2616697.3977 | 1198108.7709 | 2616691.7218 | 1198104.2527 | 2616689.0573 | 1198101.2437 | 2616687.0576 | 1198097.4027 | 2616685.7352 | 1198093.7304 | 2616678.5208 | 1198040.0148
21 | 2617215.2551 | 1198222.0733 | 2617223.1676 | 1198224.5307
22 | 2617215.2551 | 1198222.0733 | 2617218.7062 | 1198218.8704 | 2617220.9339 | 1198217.1308
23 | 2617191.342 | 1198254.0474 | 2617191.33 | 1198253.5994 | 2617190.8657 | 1198246.6629
24 | 2617435.7616 | 1198283.1496 | 2617423.0366 | 1198279.5152 | 2617411.3983 | 1198276.2612
25 | 2617377.7026 | 1198267.3438 | 2617396.5584 | 1198272.1122 | 2617411.3983 | 1198276.2612
26 | 2617455.0077 | 1198288.6464 | 2617435.7616 | 1198283.1496
27 | 2617377.7026 | 1198267.3438 | 2617383.1179 | 1198264.3134 | 2617389.1939 | 1198259.3173 | 2617394.4942 | 1198253.9408 | 2617404.1702 | 1198241.6845 | 2617412.1619 | 1198229.9347 | 2617413.3312 | 1198228.4929
28 | 2617455.0077 | 1198288.6464 | 2617466.8723 | 1198292.7106
29 | 2617455.0077 | 1198288.6464 | 2617458.4625 | 1198278.2517
30 | 2617389.4941 | 1198234.5826 | 2617392.6558 | 1198228.8109 | 2617396.1854 | 1198224.8301 | 2617398.4655 | 1198223.725 | 2617400.6899 | 1198223.4313 | 2617403.3384 | 1198223.9281 | 2617409.865 | 1198226.3484 | 2617413.3312 | 1198228.4929
31 | 2617413.3312 | 1198228.4929 | 2617418.826 | 1198221.7052 | 2617422.8212 | 1198217.3923 | 2617428.4553 | 1198212.4838 | 2617435.6135 | 1198207.1906 | 2617443.335 | 1198201.9769 | 2617452.1751 | 1198197.0222 | 2617459.0251 | 1198193.0067
32 | 2617469.3014 | 1198293.5427 | 2617466.8723 | 1198292.7106
33 | 2617458.4625 | 1198278.2517 | 2617464.2879 | 1198260.7243
34 | 2617459.0251 | 1198193.0067 | 2617468.8728 | 1198187.2433 | 2617498.3582 | 1198171.4986 | 2617501.185 | 1198170.1565
35 | 2617400.6349 | 1198056.1078 | 2617405.0183 | 1198057.11 | 2617407.6499 | 1198058.2293 | 2617409.5802 | 1198059.5801 | 2617411.6301 | 1198061.6872 | 2617413.321 | 1198064.2045 | 2617416.8261 | 1198071.3519 | 2617435.9876 | 1198117.8326 | 2617442.7369 | 1198135.3394 | 2617447.68 | 1198150.7287 | 2617451.9805 | 1198164.4819 | 2617455.9797 | 1198179.7017 | 2617459.0251 | 1198193.0067
36 | 2617238.4937 | 1198230.7558 | 2617229.5346 | 1198226.828 | 2617223.1676 | 1198224.5307
37 | 2617229.7557 | 1198210.8533 | 2617223.316 | 1198215.2706 | 2617220.9339 | 1198217.1308
38 | 2617191.342 | 1198254.0474 | 2617191.5157 | 1198260.5259 | 2617190.9733 | 1198264.4481
39 | 2617276.758 | 1198251.582 | 2617267.4705 | 1198245.9362 | 2617262.9916 | 1198243.3448
40 | 2617230.4681 | 1198349.8301 | 2617222.055 | 1198349.4057 | 2617218.712 | 1198349.4184 | 2617215.5965 | 1198349.8208 | 2617208.5227 | 1198352.3463 | 2617200.9587 | 1198355.8709 | 2617195.805 | 1198358.0351 | 2617193.4199 | 1198358.6063 | 2617191.1434 | 1198358.4886 | 2617186.8989 | 1198357.5987
41 | 2617181.8971 | 1198356.55 | 2617186.8989 | 1198357.5987
42 | 2617230.4681 | 1198349.8301 | 2617231.3429 | 1198344.5175
43 | 2617230.4681 | 1198349.8301 | 2617227.129 | 1198369.6979
44 | 2617231.3429 | 1198344.5175 | 2617235.8931 | 1198316.8836 | 2617235.9513 | 1198316.324
45 | 2617227.129 | 1198369.6979 | 2617226.2526 | 1198375.2317
46 | 2617227.129 | 1198369.6979 | 2617231.8523 | 1198368.9555 | 2617235.7311 | 1198367.9439 | 2617240.2331 | 1198367.3454 | 2617245.1294 | 1198367.3595
47 | 2617238.0367 | 1198294.3554 | 2617237.4516 | 1198301.8911 | 2617235.9513 | 1198316.324
48 | 2617226.2526 | 1198375.2317 | 2617230.7401 | 1198416.8114 | 2617231.3221 | 1198428.9085 | 2617230.6272 | 1198442.8362 | 2617228.4466 | 1198459.7168 | 2617225.9078 | 1198479.3312
49 | 2617226.2526 | 1198375.2317 | 2617218.7623 | 1198374.3319 | 2617211.2888 | 1198372.5332
50 | 2617262.7158 | 1198360.6954 | 2617258.6249 | 1198363.9409 | 2617253.099 | 1198365.7593 | 2617245.1294 | 1198367.3595
51 | 2617680.3534 | 1198322.3468 | 2617676.1684 | 1198321.2783 | 2617670.9929 | 1198320.3959 | 2617670.3438 | 1198320.3777
52 | 2617680.3534 | 1198322.3468 | 2617699.5291 | 1198319.2128 | 2617712.1005 | 1198316.8486 | 2617716.6933 | 1198315.4258
53 | 2617680.3534 | 1198322.3468 | 2617685.8401 | 1198326.1317 | 2617707.4792 | 1198347.4959 | 2617774.13 | 1198406.9806 | 2617781.494 | 1198414.4842 | 2617789.7349 | 1198424.1472 | 2617792.4095 | 1198428.6687 | 2617795.0805 | 1198434.3686 | 2617796.9951 | 1198440.9556 | 2617798.4224 | 1198447.53 | 2617799.145 | 1198455.4809 | 2617799.2742 | 1198463.241 | 2617798.2568 | 1198482.7707 | 2617795.2832 | 1198502.0278 | 2617790.8895 | 1198522.6148 | 2617790.3517 | 1198529.339 | 2617790.6194 | 1198534.0868 | 2617792.0403 | 1198540.2054 | 2617792.5502 | 1198541.5143
54 | 2617736.6612 | 1198300.4234 | 2617734.8137 | 1198304.598 | 2617731.6825 | 1198307.6793 | 2617728.248 | 1198310.3039 | 2617720.6674 | 1198314.1947 | 2617716.6933 | 1198315.4258
55 | 2617792.5502 | 1198541.5143 | 2617793.922 | 1198545.0359 | 2617798.6916 | 1198551.7647 | 2617801.7883 | 1198555.1424 | 2617805.9603 | 1198557.9563 | 2617810.9335 | 1198560.1945 | 2617820.5132 | 1198563.4641
56 | 2617216.1734 | 1198281.1217 | 2617217.4113 | 1198272.9043
57 | 2617215.1343 | 1198288.0195 | 2617216.1734 | 1198281.1217
58 | 2617215.1343 | 1198288.0195 | 2617216.2058 | 1198288.7674 | 2617217.2983 | 1198290.1602 | 2617217.9406 | 1198291.9186 | 2617218.3769 | 1198293.7764
59 | 2617215.1343 | 1198288.0195 | 2617209.0414 | 1198285.723 | 2617206.9254 | 1198285.3834 | 2617204.0926 | 1198285.4309 | 2617202.3446 | 1198285.8567
60 | 2617238.0367 | 1198294.3554 | 2617218.3769 | 1198293.7764
61 | 2617202.3446 | 1198285.8567 | 2617200.7549 | 1198286.244 | 2617199.3366 | 1198286.9403 | 2617198.3282 | 1198288.0491 | 2617197.8599 | 1198289.3929 | 2617197.8092 | 1198291.1271
62 | 2617238.4937 | 1198230.7558 | 2617236.621 | 1198243.813 | 2617235.5798 | 1198256.3279 | 2617235.6295 | 1198260.2412 | 2617236.1097 | 1198265.4009 | 2617238.6394 | 1198278.0706
63 | 2617238.4937 | 1198230.7558 | 2617245.9572 | 1198234.4128
64 | 2617238.6394 | 1198278.0706 | 2617238.8003 | 1198280.3834 | 2617238.7922 | 1198283.2182 | 2617238.0367 | 1198294.3554
65 | 2617172.4748 | 1198277.7806 | 2617176.5563 | 1198277.7923 | 2617181.8744 | 1198276.7848 | 2617185.9612 | 1198274.9622 | 2617188.6281 | 1198271.7125 | 2617190.4737 | 1198268.0603 | 2617190.9733 | 1198264.4481
66 | 2617237.08 | 1198195.4428 | 2617236.1973 | 1198197.3001
67 | 2617256.0429 | 1198163.0921 | 2617252.9603 | 1198167.8636 | 2617243.8464 | 1198183.3123 | 2617239.723 | 1198189.8818 | 2617237.08 | 1198195.4428
68 | 2617229.7557 | 1198210.8533 | 2617236.1973 | 1198197.3001
69 | 2617200.825 | 1197956.5781 | 2617218.4246 | 1197988.1455 | 2617240.9758 | 1198029.6326 | 2617267.1687 | 1198059.8797 | 2617275.5825 | 1198068.1195 | 2617300.1039 | 1198086.3444 | 2617304.0673 | 1198090.3802 | 2617306.5476 | 1198093.8115 | 2617309.0963 | 1198099.8887 | 2617303.9643 | 1198110.2351 | 2617299.9191 | 1198116.071 | 2617292.8352 | 1198124.644 | 2617280.4076 | 1198137.8042 | 2617262.085 | 1198156.6282 | 2617256.0429 | 1198163.0921
70 | 2617033.1894 | 1197629.7687 | 2617038.4563 | 1197681.8005 | 2617041.7568 | 1197742.3979 | 2617045.4627 | 1197762.1524 | 2617052.3702 | 1197775.4681 | 2617060.4144 | 1197788.0644 | 2617076.4854 | 1197805.9642 | 2617102.6878 | 1197828.1507 | 2617121.9888 | 1197842.9248 | 2617139.9754 | 1197861.9308 | 2617176.5587 | 1197920.756 | 2617191.0197 | 1197942.1978 | 2617200.825 | 1197956.5781
71 | 2617200.825 | 1197956.5781 | 2617204.7048 | 1197936.7341 | 2617211.3027 | 1197922.4009 | 2617228.2653 | 1197897.4028 | 2617247.1161 | 1197883.1826 | 2617300.0679 | 1197866.5595 | 2617357.4374 | 1197841.9231 | 2617375.8393 | 1197829.2586
72 | 2617400.6349 | 1198056.1078 | 2617414.0956 | 1198046.5973 | 2617421.2975 | 1198040.8266
73 | 2617421.2975 | 1198040.8266 | 2617423.3162 | 1198039.209 | 2617429.6643 | 1198033.5225
74 | 2617033.1894 | 1197629.7687 | 2617031.9758 | 1197614.646
75 | 2617033.1894 | 1197629.7687 | 2617034.919 | 1197624.0928 | 2617037.2289 | 1197620.5863 | 2617040.5779 | 1197618.5948 | 2617045.1965 | 1197617.3739 | 2617050.459 | 1197617.3333 | 2617056.3283 | 1197618.1949 | 2617062.222 | 1197621.1688 | 2617067.7089 | 1197625.2533 | 2617072.0747 | 1197629.8904 | 2617088.6828 | 1197651.8606 | 2617137.8696 | 1197724.7734 | 2617144.3953 | 1197733.0631 | 2617150.5955 | 1197737.9724 | 2617156.9151 | 1197741.0921 | 2617163.2188 | 1197741.7772 | 2617169.5359 | 1197740.4279 | 2617177.0838 | 1197737.4701 | 2617237.4465 | 1197701.5253
76 | 2617392.8741 | 1197817.5349 | 2617375.8393 | 1197829.2586
77 | 2617262.9916 | 1198243.3448 | 2617256.3864 | 1198239.5231 | 2617245.9572 | 1198234.4128
78 | 2617171.2306 | 1198362.6745 | 2617175.7079 | 1198363.9696 | 2617211.2888 | 1198372.5332
79 | 2617225.9078 | 1198479.3312 | 2617231.6501 | 1198481.6711 | 2617238.2593 | 1198484.4138 | 2617262.7683 | 1198495.8678
80 | 2617284.364 | 1198503.479 | 2617277.8279 | 1198501.8259 | 2617270.6919 | 1198499.5708 | 2617262.7683 | 1198495.8678
81 | 2616926.124 | 1197227.1918 | 2616924.9542 | 1197227.4834
82 | 2616938.6366 | 1197224.0723 | 2616926.124 | 1197227.1918
83 | 2616924.9542 | 1197227.4834 | 2616920.7793 | 1197228.5243 | 2616898.525 | 1197234.812
84 | 2616938.6366 | 1197224.0723 | 2616955.0016 | 1197230.244 | 2616959.8677 | 1197233.1816 | 2616962.6139 | 1197237.0358 | 2616964.0787 | 1197241.5202 | 2616964.0809 | 1197248.813 | 2616961.6426 | 1197262.6913 | 2616958.5694 | 1197274.8224 | 2616954.3626 | 1197289.2405 | 2616948.2143 | 1197303.4863 | 2616934.8261 | 1197324.7377 | 2616919.5232 | 1197344.394 | 2616882.2571 | 1197387.9901 | 2616872.3757 | 1197395.7304
85 | 2616868.9436 | 1197398.4188 | 2616872.3757 | 1197395.7304
86 | 2616830.9733 | 1197574.4016 | 2616828.6623 | 1197572.8943 | 2616820.1097 | 1197562.0757 | 2616809.5263 | 1197547.5938 | 2616801.585 | 1197536.032 | 2616796.7179 | 1197525.3571 | 2616794.34 | 1197515.1116 | 2616793.6085 | 1197501.6468 | 2616793.2185 | 1197488.6387 | 2616794.2508 | 1197476.2683 | 2616798.758 | 1197465.8976 | 2616808.4045 | 1197453.3178 | 2616818.0754 | 1197442.9171 | 2616828.5805 | 1197433.7861 | 2616841.9019 | 1197422.5397 | 2616853.6162 | 1197411.3444 | 2616864.8772 | 1197401.6041 | 2616868.9436 | 1197398.4188
87 | 2617249.2443 | 1197661.8612 | 2617247.4963 | 1197655.6949 | 2617245.2156 | 1197651.0738
88 | 2617254.6896 | 1197678.0609 | 2617251.3789 | 1197669.3912 | 2617249.2443 | 1197661.8612
89 | 2617254.6896 | 1197678.0609 | 2617256.049 | 1197684.6795 | 2617253.909 | 1197689.9984 | 2617249.0979 | 1197694.587 | 2617237.4465 | 1197701.5253
90 | 2617254.6896 | 1197678.0609 | 2617262.671 | 1197675.338 | 2617304.326 | 1197670.9334 | 2617346.4437 | 1197669.7989 | 2617360.725 | 1197666.4828 | 2617371.9839 | 1197665.6803
91 | 2617371.9839 | 1197665.6803 | 2617373.3465 | 1197665.5832
92 | 2617390.2493 | 1197664.3783 | 2617373.3465 | 1197665.5832
93 | 2617031.9758 | 1197614.646 | 2617033.3596 | 1197575.1954 | 2617038.6226 | 1197534.8109 | 2617047.3177 | 1197487.3435 | 2617051.3894 | 1197474.9595 | 2617059.4013 | 1197458.8959 | 2617066.1688 | 1197446.5641 | 2617070.3712 | 1197441.6026
94 | 2617031.9758 | 1197614.646 | 2617021.5891 | 1197608.869 | 2617008.3381 | 1197600.6826 | 2616991.4003 | 1197590.1178 | 2616976.9344 | 1197580.6384 | 2616964.0727 | 1197574.7767 | 2616951.2274 | 1197571.2051 | 2616937.7557 | 1197568.31 | 2616930.4059 | 1197565.8435 | 2616928.8097 | 1197565.4863
95 | 2617101.2467 | 1197396.2036 | 2617101.4285 | 1197401.8739 | 2617096.5167 | 1197409.7307 | 2617089.1281 | 1197418.1253 | 2617080.3138 | 1197427.0605 | 2617070.4711 | 1197441.4847 | 2617070.3712 | 1197441.6026
96 | 2616830.9733 | 1197574.4016 | 2616842.3666 | 1197566.207 | 2616854.8528 | 1197556.6814 | 2616862.6207 | 1197554.0462 | 2616877.3272 | 1197553.8875 | 2616893.2587 | 1197554.1325 | 2616901.4258 | 1197555.7897 | 2616908.5605 | 1197558.9337 | 2616919.3852 | 1197563.3777 | 2616928.8097 | 1197565.4863
97 | 2617413.7362 | 1197666.9034 | 2617390.2493 | 1197664.3783
98 | 2617063.2549 | 1198558.7201 | 2617071.3792 | 1198561.5114 | 2617084.6233 | 1198571.3211 | 2617095.4185 | 1198582.7469 | 2617107.0168 | 1198598.2549 | 2617117.9953 | 1198614.784 | 2617130.0967 | 1198632.7394 | 2617142.0995 | 1198650.4943 | 2617151.1456 | 1198663.7384 | 2617162.156 | 1198671.7075 | 2617176.8551 | 1198673.1726 | 2617194.6297 | 1198669.5661 | 2617205.8818 | 1198664.918 | 2617210.4247 | 1198660.6176 | 2617215.5413 | 1198681.9438 | 2617221.3136 | 1198716.1788 | 2617226.0408 | 1198732.5012 | 2617231.1455 | 1198744.6557 | 2617238.385 | 1198758.4951 | 2617249.0937 | 1198773.2783 | 2617270.7532 | 1198798.1095
99 | 2617063.2549 | 1198558.7201 | 2617057.8417 | 1198561.1394 | 2617054.6055 | 1198563.8205 | 2617052.4235 | 1198568.0165 | 2617051.1783 | 1198572.1041 | 2617050.7601 | 1198577.2501 | 2617049.5201 | 1198587.5633 | 2617048.0602 | 1198590.4364
100 | 2617270.7532 | 1198798.1095 | 2617307.3024 | 1198832.0332 | 2617331.5464 | 1198855.3273
101 | 2617270.7532 | 1198798.1095 | 2617276.1967 | 1198790.4211 | 2617277.7923 | 1198786.3012 | 2617284.2081 | 1198729.2223 | 2617289.194 | 1198698.0421 | 2617292.2039 | 1198689.3683 | 2617297.2457 | 1198681.0451 | 2617302.5164 | 1198675.2238 | 2617309.2135 | 1198671.1965 | 2617321.173 | 1198666.8287 | 2617337.7776 | 1198662.352 | 2617364.4201 | 1198659.8055 | 2617370.3904 | 1198659.5893 | 2617376.7137 | 1198661.0418 | 2617387.9701 | 1198665.4879 | 2617393.063 | 1198665.8473 | 2617396.8598 | 1198664.8227
102 | 2617336.6685 | 1198860.2487 | 2617331.5464 | 1198855.3273
103 | 2617396.8598 | 1198664.8227 | 2617398.3211 | 1198664.4284 | 2617405.8536 | 1198661.1263 | 2617416.6865 | 1198651.4636 | 2617425.2552 | 1198638.1767
104 | 2617425.6352 | 1198637.5874 | 2617425.2552 | 1198638.1767
105 | 2617553.7942 | 1198939.0183 | 2617551.7638 | 1198938.1341 | 2617543.8983 | 1198938.2111 | 2617537.3906 | 1198940.0486 | 2617517.1671 | 1198948.105 | 2617509.0307 | 1198949.6932 | 2617502.6566 | 1198950.0859 | 2617495.8826 | 1198949.2546 | 2617486.5433 | 1198945.5809 | 2617463.9797 | 1198931.0407 | 2617445.1555 | 1198918.7571 | 2617416.9111 | 1198904.3894 | 2617377.5923 | 1198893.803 | 2617366.7835 | 1198887.435 | 2617352.8302 | 1198875.7772 | 2617336.6685 | 1198860.2487
106 | 2617464.9407 | 1198776.2823 | 2617476.0258 | 1198821.1054 | 2617482.7637 | 1198834.3655 | 2617491.5454 | 1198846.5199 | 2617529.0305 | 1198887.9517 | 2617551.0074 | 1198926.0253 | 2617553.7942 | 1198939.0183
107 | 2617464.9407 | 1198776.2823 | 2617462.3413 | 1198769.4599 | 2617463.17 | 1198764.6598 | 2617468.6591 | 1198751.8466 | 2617479.9482 | 1198739.773 | 2617491.1152 | 1198727.788 | 2617533.1929 | 1198690.9577 | 2617544.7508 | 1198683.3541 | 2617559.6852 | 1198674.6486 | 2617572.2646 | 1198669.2937 | 2617586.4687 | 1198665.5667 | 2617601.4822 | 1198663.6763 | 2617618.3267 | 1198663.1366 | 2617641.1037 | 1198664.9156 | 2617663.1472 | 1198667.5153 | 2617685.5347 | 1198677.431 | 2617695.208 | 1198684.1298 | 2617704.4693 | 1198693.18
108 | 2617704.4693 | 1198693.18 | 2617708.7756 | 1198697.3881 | 2617717.4839 | 1198713.7004 | 2617722.2441 | 1198727.9842
109 | 2617903.5397 | 1198603.9938 | 2617906.4311 | 1198607.2487 | 2617911.3984 | 1198614.0005 | 2617914.8685 | 1198619.7806 | 2617917.6756 | 1198625.7478 | 2617919.9852 | 1198632.5695 | 2617921.3816 | 1198639.2439 | 2617921.4525 | 1198643.5131 | 2617921.0595 | 1198647.6363 | 2617919.0679 | 1198654.1339 | 2617916.3919 | 1198657.8168 | 2617912.0726 | 1198661.0056 | 2617907.1253 | 1198662.8696 | 2617899.3621 | 1198664.2916 | 2617889.907 | 1198666.1867 | 2617886.8995 | 1198667.5164
110 | 2617902.4072 | 1198740.9643 | 2617895.7118 | 1198731.5948 | 2617889.5226 | 1198720.9706 | 2617885.9932 | 1198712.122 | 2617883.0995 | 1198702.0079 | 2617880.1381 | 1198691.5934 | 2617878.5996 | 1198684.0515 | 2617878.6362 | 1198679.4713 | 2617879.6787 | 1198674.5718 | 2617881.8132 | 1198671.1763 | 2617885.0121 | 1198668.351 | 2617886.8995 | 1198667.5164
111 | 2617903.5397 | 1198603.9938 | 2617899.1409 | 1198600.6678 | 2617874.2382 | 1198583.929 | 2617865.5119 | 1198578.8558
112 | 2617902.4072 | 1198740.9643 | 2617884.3312 | 1198753.6394 | 2617878.1788 | 1198758.7682 | 2617874.13 | 1198763.2252 | 2617870.6924 | 1198769.5295 | 2617867.01 | 1198778.7568 | 2617863.8829 | 1198788.1971 | 2617861.7674 | 1198798.0183 | 2617859.973 | 1198815.0443 | 2617859.49 | 1198826.3823
113 | 2617910.9012 | 1198561.215 | 2617901.6918 | 1198567.4909 | 2617894.8654 | 1198571.3059 | 2617888.4382 | 1198574.0549 | 2617881.609 | 1198576.2913 | 2617874.4915 | 1198578.1488 | 2617865.5119 | 1198578.8558
114 | 2617865.5119 | 1198578.8558 | 2617837.4507 | 1198569.2449 | 2617820.5132 | 1198563.4641
115 | 2617859.49 | 1198826.3823 | 2617853.7077 | 1198827.4323 | 2617847.6847 | 1198827.4811 | 2617842.7238 | 1198826.3213 | 2617838.2983 | 1198824.2959 | 2617831.854 | 1198820.1189 | 2617819.0314 | 1198809.9865 | 2617811.5095 | 1198804.5501 | 2617798.4965 | 1198796.9518 | 2617782.7341 | 1198786.5806
116 | 2617910.9012 | 1198561.215 | 2617912.8687 | 1198562.7995 | 2617915.5396 | 1198563.3967 | 2617918.7002 | 1198563.206 | 2617922.9519 | 1198562.2404 | 2617928.6842 | 1198560.1898 | 2617932.3239 | 1198558.2553
117 | 2617749.7888 | 1198764.7082 | 2617756.5403 | 1198769.3459 | 2617782.7341 | 1198786.5806
118 | 2617736.6612 | 1198300.4234 | 2617735.3784 | 1198291.3259 | 2617732.0293 | 1198285.6796 | 2617727.2032 | 1198282.5081 | 2617723.1555 | 1198278.783 | 2617719.457 | 1198275.4369 | 2617715.9966 | 1198271.369 | 2617713.2016 | 1198266.3358 | 2617712.7693 | 1198265.4178
119 | 2617736.6612 | 1198300.4234 | 2617749.8696 | 1198296.7144
120 | 2617722.2441 | 1198727.9842 | 2617727.3633 | 1198743.3456 | 2617731.1195 | 1198750.2826 | 2617736.206 | 1198755.3782 | 2617749.7888 | 1198764.7082
121 | 2617712.7693 | 1198265.4178 | 2617712.4933 | 1198264.832
122 | 2617962.2323 | 1198273.5136 | 2617872.6304 | 1198272.7455 | 2617806.0799 | 1198274.1372 | 2617789.0558 | 1198275.7987 | 2617768.7153 | 1198283.8983 | 2617758.13 | 1198294.3948 | 2617749.8696 | 1198296.7144
123 | 2617673.0496 | 1198178.1143 | 2617679.5154 | 1198193.3638 | 2617688.4026 | 1198213.8343 | 2617704.3402 | 1198247.5217 | 2617712.4933 | 1198264.832
124 | 2617903.8967 | 1198186.17 | 2617917.2551 | 1198198.3497 | 2617928.4982 | 1198212.4798 | 2617942.5113 | 1198232.2991 | 2617951.5523 | 1198249.402 | 2617962.2323 | 1198273.5136
125 | 2617962.2323 | 1198273.5136 | 2617966.8551 | 1198283.4773 | 2617971.4626 | 1198290.9173 | 2617977.5377 | 1198299.051 | 2617999.5857 | 1198320.8511 | 2618019.08 | 1198338.4635 | 2618038.5779 | 1198354.8198 | 2618054.6236 | 1198367.0191 | 2618072.4676 | 1198378.7459 | 2618090.3155 | 1198389.2053
126 | 2617577.7486 | 1198164.9272 | 2617613.7457 | 1198172.3701 | 2617638.6428 | 1198176.3009 | 2617655.6499 | 1198177.9074 | 2617673.0496 | 1198178.1143
127 | 2617577.7486 | 1198164.9272 | 2617586.9938 | 1198153.684
128 | 2617577.7486 | 1198164.9272 | 2617556.9969 | 1198162.792
129 | 2617903.8967 | 1198186.17 | 2617925.0376 | 1198179.7975
130 | 2617987.4683 | 1198433.2641 | 2618005.8615 | 1198442.1352 | 2618014.7675 | 1198445.7083 | 2618020.2382 | 1198447.1144 | 2618024.1127 | 1198447.5819 | 2618027.7397 | 1198446.7701 | 2618035.4838 | 1198444.2365 | 2618043.9962 | 1198439.4261 | 2618060.2528 | 1198432.0822 | 2618066.3661 | 1198429.9773 | 2618074.9331 | 1198427.2905 | 2618079.7294 | 1198425.0705 | 2618082.6378 | 1198422.7002 | 2618085.0359 | 1198420.3284 | 2618088.0055 | 1198415.3235 | 2618090.2228 | 1198409.805 | 2618090.831 | 1198405.0821 | 2618091.0244 | 1198396.5114 | 2618090.3155 | 1198389.2053
131 | 2618071.0725 | 1198101.4257 | 2618067.2008 | 1198105.0493 | 2618056.059 | 1198118.0005 | 2618036.3149 | 1198137.6517 | 2618020.5057 | 1198147.9208 | 2618004.3226 | 1198155.8987 | 2617925.0376 | 1198179.7975
132 | 2618135.1646 | 1198083.0385 | 2618151.1939 | 1198078.4121
133 | 2618125.5448 | 1198085.815 | 2618135.1646 | 1198083.0385
134 | 2618125.5448 | 1198085.815 | 2618111.251 | 1198089.6714
135 | 2618111.251 | 1198089.6714 | 2618093.826 | 1198094.3726
136 | 2618071.0725 | 1198101.4257 | 2618073.5849 | 1198083.9572 | 2618077.3072 | 1198069.305 | 2618083.6851 | 1198052.8265 | 2618086.2385 | 1198049.5213
137 | 2618086.2385 | 1198049.5213 | 2618084.9832 | 1198041.352
138 | 2618071.0725 | 1198101.4257 | 2618078.0716 | 1198098.6231 | 2618093.826 | 1198094.3726
139 | 2617464.507 | 1198260.065 | 2617464.2879 | 1198260.7243
140 | 2617556.9969 | 1198162.792 | 2617549.0563 | 1198161.9749 | 2617538.7084 | 1198161.6667 | 2617529.0968 | 1198162.15 | 2617520.412 | 1198163.4253 | 2617514.1638 | 1198164.7744 | 2617507.7834 | 1198167.0237 | 2617501.185 | 1198170.1565
141 | 2617776.7653 | 1197910.4756 | 2617776.1148 | 1197912.2648 | 2617772.4562 | 1197921.0587 | 2617769.8883 | 1197926.7097 | 2617766.6267 | 1197932.5921 | 2617762.7261 | 1197938.2836 | 2617756.6875 | 1197945.8698 | 2617750.727 | 1197952.8336 | 2617742.7441 | 1197961.2479 | 2617731.2678 | 1197971.5862 | 2617708.1779 | 1197989.7833 | 2617697.2087 | 1197998.6335 | 2617685.0966 | 1198010.2707 | 2617675.3786 | 1198020.9478 | 2617666.7032 | 1198031.8836 | 2617661.7389 | 1198039.3619 | 2617648.351 | 1198060.1893 | 2617636.1674 | 1198080.6978 | 2617619.2362 | 1198110.1639 | 2617610.1569 | 1198123.8335 | 2617599.7813 | 1198138.1329 | 2617586.9938 | 1198153.684
142 | 2617787.0172 | 1197881.6758 | 2617782.7332 | 1197894.0635 | 2617776.7653 | 1197910.4756
143 | 2616899.7754 | 1197414.4537 | 2616900.617 | 1197432.021 | 2616899.9172 | 1197442.5136 | 2616898.3408 | 1197453.3038 | 2616898.337 | 1197457.3504 | 2616899.3934 | 1197460.833 | 2616902.035 | 1197463.9088 | 2616906.3573 | 1197465.1661 | 2616910.4936 | 1197464.8776 | 2616923.704 | 1197460.5792 | 2616930.515 | 1197457.0409 | 2616936.361 | 1197452.7218 | 2616942.9917 | 1197445.6034 | 2616961.0126 | 1197428.8786 | 2616982.7268 | 1197406.9505 | 2616996.2538 | 1197393.137 | 2617020.0036 | 1197373.2492 | 2617033.5301 | 1197357.0011 | 2617045.0017 | 1197345.6276 | 2617053.566 | 1197336.2469 | 2617057.3792 | 1197331.7442 | 2617059.4168 | 1197330.2825 | 2617061.8402 | 1197329.7558 | 2617064.3593 | 1197330.3966 | 2617066.023 | 1197331.8911 | 2617067.4479 | 1197334.3297 | 2617070.8381 | 1197341.9657 | 2617079.5475 | 1197364.5582 | 2617086.9934 | 1197378.8204 | 2617094.6758 | 1197392.9387 | 2617096.5278 | 1197395.134 | 2617098.711 | 1197396.0296 | 2617101.2467 | 1197396.2036
144 | 2617804.1143 | 1197869.347 | 2617804.7631 | 1197871.4278 | 2617810.5093 | 1197884.3936
145 | 2617818.0304 | 1197904.296 | 2617816.8265 | 1197899.3787 | 2617815.5427 | 1197895.7507 | 2617810.5093 | 1197884.3936
146 | 2617804.1143 | 1197869.347 | 2617803.9427 | 1197865.5889 | 2617804.0377 | 1197859.2413
147 | 2617804.1143 | 1197869.347 | 2617800.4181 | 1197870.2587 | 2617793.0299 | 1197873.2718 | 2617791.4811 | 1197874.2455 | 2617790.2594 | 1197875.3202 | 2617789.0582 | 1197877.2177 | 2617787.4725 | 1197880.3591 | 2617787.0172 | 1197881.6758

## bus_geodata
| x | y | coords
0 | 2617318.6127 | 1198268.3095
1 | 2617335.2109 | 1198270.5373
2 | 2617295.5269 | 1198262.2188
3 | 2617339.397 | 1198270.9349
4 | 2617292.5295 | 1198260.8295
5 | 2617346.0624 | 1198271.3113
6 | 2617321.9928 | 1198301.3899
7 | 2617287.3225 | 1198258.004
8 | 2617355.7891 | 1198271.8606
9 | 2617309.4373 | 1198293.0269
10 | 2617320.6572 | 1198310.3353
11 | 2617299.2672 | 1198290.3536
12 | 2617138.1727 | 1198228.9133
13 | 2617153.3428 | 1198224.1818
14 | 2617136.6939 | 1198229.3745
15 | 2617179.2761 | 1198218.8795
16 | 2616725.2389 | 1198141.366
17 | 2617215.2551 | 1198222.0733
18 | 2617190.8657 | 1198246.6629
19 | 2616678.5208 | 1198040.0148
20 | 2617323.3606 | 1198334.0114
21 | 2617411.3983 | 1198276.2612
22 | 2617435.7616 | 1198283.1496
23 | 2617377.7026 | 1198267.3438
24 | 2617455.0077 | 1198288.6464
25 | 2617413.3312 | 1198228.4929
26 | 2617466.8723 | 1198292.7106
27 | 2617458.4625 | 1198278.2517
28 | 2617389.4941 | 1198234.5826
29 | 2617459.0251 | 1198193.0067
30 | 2617223.1676 | 1198224.5307
31 | 2617220.9339 | 1198217.1308
32 | 2617191.342 | 1198254.0474
33 | 2617276.758 | 1198251.582
34 | 2617186.8989 | 1198357.5987
35 | 2617230.4681 | 1198349.8301
36 | 2617181.8971 | 1198356.55
37 | 2617231.3429 | 1198344.5175
38 | 2617227.129 | 1198369.6979
39 | 2617235.9513 | 1198316.324
40 | 2617226.2526 | 1198375.2317
41 | 2617245.1294 | 1198367.3595
42 | 2617469.3014 | 1198293.5427
43 | 2617670.3438 | 1198320.3777
44 | 2617680.3534 | 1198322.3468
45 | 2617716.6933 | 1198315.4258
46 | 2617792.5502 | 1198541.5143
47 | 2617216.1734 | 1198281.1217
48 | 2617217.4113 | 1198272.9043
49 | 2617215.1343 | 1198288.0195
50 | 2617218.3769 | 1198293.7764
51 | 2617202.3446 | 1198285.8567
52 | 2617238.4937 | 1198230.7558
53 | 2617238.0367 | 1198294.3554
54 | 2617197.8092 | 1198291.1271
55 | 2617190.9733 | 1198264.4481
56 | 2617172.4748 | 1198277.7806
57 | 2617238.6394 | 1198278.0706
58 | 2617237.08 | 1198195.4428
59 | 2617236.1973 | 1198197.3001
60 | 2617256.0429 | 1198163.0921
61 | 2617229.7557 | 1198210.8533
62 | 2617200.825 | 1197956.5781
63 | 2617400.6349 | 1198056.1078
64 | 2617421.2975 | 1198040.8266
65 | 2617033.1894 | 1197629.7687
66 | 2617375.8393 | 1197829.2586
67 | 2617245.9572 | 1198234.4128
68 | 2617171.2306 | 1198362.6745
69 | 2617211.2888 | 1198372.5332
70 | 2617225.9078 | 1198479.3312
71 | 2617262.9916 | 1198243.3448
72 | 2617262.7683 | 1198495.8678
73 | 2617262.7158 | 1198360.6954
74 | 2616926.124 | 1197227.1918
75 | 2616924.9542 | 1197227.4834
76 | 2616938.6366 | 1197224.0723
77 | 2616898.525 | 1197234.812
78 | 2616872.3757 | 1197395.7304
79 | 2616868.9436 | 1197398.4188
80 | 2617249.2443 | 1197661.8612
81 | 2617245.2156 | 1197651.0738
82 | 2617254.6896 | 1197678.0609
83 | 2617237.4465 | 1197701.5253
84 | 2617371.9839 | 1197665.6803
85 | 2617373.3465 | 1197665.5832
86 | 2617031.9758 | 1197614.646
87 | 2617070.3712 | 1197441.6026
88 | 2616928.8096 | 1197565.4863
89 | 2617390.2493 | 1197664.3783
90 | 2617413.7362 | 1197666.9034
91 | 2617284.364 | 1198503.479
92 | 2617063.2549 | 1198558.7201
93 | 2617270.7532 | 1198798.1095
94 | 2617048.0602 | 1198590.4364
95 | 2617331.5464 | 1198855.3273
96 | 2617396.8598 | 1198664.8227
97 | 2617425.2552 | 1198638.1767
98 | 2617425.6352 | 1198637.5874
99 | 2617336.6685 | 1198860.2487
100 | 2617553.7942 | 1198939.0183
101 | 2617464.9407 | 1198776.2823
102 | 2617704.4693 | 1198693.18
103 | 2617886.8995 | 1198667.5164
104 | 2617903.5397 | 1198603.9938
105 | 2617902.4072 | 1198740.9643
106 | 2617865.5119 | 1198578.8558
107 | 2617859.49 | 1198826.3823
108 | 2617910.9012 | 1198561.215
109 | 2617820.5132 | 1198563.4641
110 | 2617782.7341 | 1198786.5806
111 | 2617736.6612 | 1198300.4234
112 | 2617932.3239 | 1198558.2553
113 | 2617722.2441 | 1198727.9842
114 | 2617749.7888 | 1198764.7082
115 | 2617712.7693 | 1198265.4178
116 | 2617749.8696 | 1198296.7144
117 | 2617712.4933 | 1198264.832
118 | 2617962.2323 | 1198273.5136
119 | 2617673.0496 | 1198178.1143
120 | 2617577.7486 | 1198164.9272
121 | 2617903.8967 | 1198186.17
122 | 2618090.3155 | 1198389.2053
123 | 2617925.0376 | 1198179.7975
124 | 2617987.4683 | 1198433.2641
125 | 2618135.1646 | 1198083.0385
126 | 2618151.1939 | 1198078.4121
127 | 2618125.5448 | 1198085.815
128 | 2618111.251 | 1198089.6714
129 | 2618086.2385 | 1198049.5213
130 | 2618071.0725 | 1198101.4257
131 | 2618084.9832 | 1198041.352
132 | 2618093.826 | 1198094.3726
133 | 2617464.507 | 1198260.065
134 | 2617464.2879 | 1198260.7243
135 | 2616830.9733 | 1197574.4016
136 | 2617429.6643 | 1198033.5225
137 | 2617501.185 | 1198170.1565
138 | 2617586.9938 | 1198153.684
139 | 2617556.9969 | 1198162.792
140 | 2617776.7653 | 1197910.4756
141 | 2617101.2467 | 1197396.2036
142 | 2616899.7754 | 1197414.4537
143 | 2617810.5093 | 1197884.3936
144 | 2617804.1143 | 1197869.347
145 | 2617818.0304 | 1197904.296
146 | 2617804.0377 | 1197859.2413
147 | 2617787.0171 | 1197881.6758
148 | 2617392.8741 | 1197817.5349
149 | 2617389.4941 | 1198234.5826

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1