## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6034-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6034-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6034-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6034-2_0_4_node_52 | 0.4 | n |  | TRUE
4 | bus_LV_6034-2_0_4_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_6034-2_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_6034-2_0_4_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_6034-2_0_4_node_42 | 0.4 | n |  | TRUE
8 | bus_LV_6034-2_0_4_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_6034-2_0_4_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_6034-2_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_6034-2_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_6034-2_0_4_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6034-2_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_6034-2_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_6034-2_0_4_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_6034-2_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6034-2_0_4_node_40 | 0.4 | n |  | TRUE
18 | bus_LV_6034-2_0_4_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_6034-2_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_6034-2_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_6034-2_0_4_node_49 | 0.4 | n |  | TRUE
22 | bus_LV_6034-2_0_4_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_6034-2_0_4_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_6034-2_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_6034-2_0_4_node_51 | 0.4 | n |  | TRUE
26 | bus_LV_6034-2_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6034-2_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_6034-2_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_6034-2_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_6034-2_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_6034-2_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_6034-2_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_6034-2_0_4_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_6034-2_0_4_node_46 | 0.4 | n |  | TRUE
35 | bus_LV_6034-2_0_4_node_17 | 0.4 | n |  | TRUE
36 | bus_LV_6034-2_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_6034-2_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_6034-2_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_6034-2_0_4_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_6034-2_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_6034-2_0_4_node_55 | 0.4 | n |  | TRUE
42 | bus_LV_6034-2_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_6034-2_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_6034-2_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_6034-2_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_6034-2_0_4_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_6034-2_0_4_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_6034-2_0_4_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_6034-2_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_6034-2_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_6034-2_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_6034-2_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_6034-2_0_4_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_6034-2_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_6034-2_0_4_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_6034-2_0_4_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_6034-2_0_4_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_6034-2_0_4_node_57 | 0.4 | n |  | TRUE
59 | bus_MV_196_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6034-2_0_4_load_0 | 0 | 0.0097081 | 0.0024331 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6034-2_0_4_load_15 | 4 | 0.002215 | 0.00055512 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6034-2_0_4_load_13 | 5 | 0.0030922 | 0.00077499 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6034-2_0_4_load_60 | 6 | 0.015439 | 0.0038694 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6034-2_0_4_load_42 | 7 | 0.0077157 | 0.0019337 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6034-2_0_4_load_41 | 8 | 0.0034232 | 0.00085794 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6034-2_0_4_load_3 | 9 | 0.0086012 | 0.0021557 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6034-2_0_4_load_4 | 10 | 0.0032399 | 0.00081199 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6034-2_0_4_load_5 | 11 | 0.0086556 | 0.0021693 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6034-2_0_4_load_6 | 12 | 0.0049159 | 0.001232 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6034-2_0_4_load_22 | 15 | 0.0046889 | 0.0011751 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6034-2_0_4_load_12 | 16 | 0.0042411 | 0.0010629 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6034-2_0_4_load_40 | 17 | 0.0062631 | 0.0015697 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6034-2_0_4_load_37 | 18 | 0.0037815 | 0.00094774 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6034-2_0_4_load_23 | 19 | 0.0025971 | 0.00065088 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6034-2_0_4_load_10 | 20 | 0.0033032 | 0.00082785 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6034-2_0_4_load_38 | 22 | 0.0063333 | 0.0015873 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6034-2_0_4_load_9 | 23 | 0.0046843 | 0.001174 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6034-2_0_4_load_11 | 24 | 0.0026942 | 0.00067524 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6034-2_0_4_load_51 | 25 | 0.0055342 | 0.001387 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6034-2_0_4_load_14 | 26 | 0.0021779 | 0.00054584 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6034-2_0_4_load_25 | 29 | 0.0025337 | 0.00063501 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6034-2_0_4_load_26 | 30 | 0.0045546 | 0.0011415 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6034-2_0_4_load_28 | 31 | 0.0054019 | 0.0013538 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6034-2_0_4_load_47 | 32 | 0.0018528 | 0.00046437 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6034-2_0_4_load_45 | 33 | 0.0024034 | 0.00060234 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6034-2_0_4_load_46 | 34 | 0.0022494 | 0.00056374 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6034-2_0_4_load_17 | 35 | 0.0039878 | 0.00099944 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6034-2_0_4_load_18 | 36 | 0.0035205 | 0.00088232 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6034-2_0_4_load_19 | 37 | 0.0038642 | 0.00096845 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6034-2_0_4_load_32 | 39 | 0.0057084 | 0.0014307 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6034-2_0_4_load_29 | 40 | 0.0047975 | 0.0012024 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6034-2_0_4_load_55 | 41 | 0.0049769 | 0.0012473 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6034-2_0_4_load_30 | 42 | 0.0041494 | 0.0010399 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6034-2_0_4_load_24 | 43 | 0.003745 | 0.00093858 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6034-2_0_4_load_33 | 44 | 0.0043615 | 0.0010931 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6034-2_0_4_load_34 | 45 | 0.0031197 | 0.00078188 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6034-2_0_4_load_31 | 46 | 0.0043813 | 0.0010981 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6034-2_0_4_load_48 | 47 | 0.0056508 | 0.0014162 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6034-2_0_4_load_53 | 48 | 0.0034638 | 0.00086812 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6034-2_0_4_load_35 | 49 | 0.0025077 | 0.00062849 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6034-2_0_4_load_36 | 50 | 0.0037288 | 0.00093452 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6034-2_0_4_load_43 | 51 | 0.011651 | 0.0029199 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6034-2_0_4_load_44 | 52 | 0.0057279 | 0.0014355 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6034-2_0_4_load_39 | 53 | 0.0036686 | 0.00091945 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6034-2_0_4_load_50 | 54 | 0.0038778 | 0.00097186 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6034-2_0_4_load_59 | 55 | 0.0039202 | 0.0009825 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6034-2_0_4_load_54 | 56 | 0.0038338 | 0.00096084 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6034-2_0_4_load_56 | 57 | 0.0093568 | 0.002345 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6034-2_0_4_load_57 | 58 | 0.004911 | 0.0012308 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6034-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6034-2_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.014085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6034-2_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.027641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6034-2_0_4_line_3 | NAYY 4x150 SE | 3 | 6 | 0.0077237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6034-2_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.067618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6034-2_0_4_line_5 | NAYY 4x150 SE | 5 | 26 | 0.013372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6034-2_0_4_line_6 | NAYY 4x150 SE | 6 | 52 | 0.011314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6034-2_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.013873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6034-2_0_4_line_8 | NAYY 4x150 SE | 8 | 53 | 0.013868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6034-2_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.00033028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6034-2_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.011501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6034-2_0_4_line_11 | NAYY 4x150 SE | 10 | 12 | 0.020178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6034-2_0_4_line_12 | NAYY 4x150 SE | 11 | 13 | 0.032812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6034-2_0_4_line_13 | NAYY 4x150 SE | 11 | 14 | 0.02641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_6034-2_0_4_line_14 | NAYY 4x150 SE | 12 | 15 | 0.0034007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6034-2_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.012655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6034-2_0_4_line_16 | NAYY 4x150 SE | 14 | 17 | 0.023614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6034-2_0_4_line_17 | NAYY 4x150 SE | 14 | 18 | 0.029542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_6034-2_0_4_line_18 | NAYY 4x150 SE | 15 | 19 | 0.0037103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6034-2_0_4_line_19 | NAYY 4x150 SE | 16 | 20 | 0.010698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6034-2_0_4_line_20 | NAYY 4x150 SE | 17 | 21 | 0.027234 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6034-2_0_4_line_21 | NAYY 4x150 SE | 18 | 22 | 0.016553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6034-2_0_4_line_22 | NAYY 4x150 SE | 19 | 43 | 0.010053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6034-2_0_4_line_23 | NAYY 4x150 SE | 20 | 23 | 0.0089172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6034-2_0_4_line_24 | NAYY 4x150 SE | 21 | 54 | 0.030077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6034-2_0_4_line_25 | NAYY 4x150 SE | 21 | 47 | 0.031244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6034-2_0_4_line_26 | NAYY 4x150 SE | 22 | 53 | 0.013962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6034-2_0_4_line_27 | NAYY 4x150 SE | 23 | 24 | 0.00030596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6034-2_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.094825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6034-2_0_4_line_29 | NAYY 4x150 SE | 25 | 32 | 0.061962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6034-2_0_4_line_30 | NAYY 4x150 SE | 25 | 31 | 0.075215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6034-2_0_4_line_31 | NAYY 4x150 SE | 26 | 27 | 0.038238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6034-2_0_4_line_32 | NAYY 4x150 SE | 27 | 28 | 0.064498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6034-2_0_4_line_33 | NAYY 4x150 SE | 28 | 29 | 0.052775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6034-2_0_4_line_34 | NAYY 4x150 SE | 29 | 30 | 0.029857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6034-2_0_4_line_35 | NAYY 4x150 SE | 30 | 31 | 0.0093556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6034-2_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.0054164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6034-2_0_4_line_37 | NAYY 4x150 SE | 33 | 34 | 0.032134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6034-2_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.014356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6034-2_0_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.0033456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6034-2_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.0085747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6034-2_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.02276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6034-2_0_4_line_42 | NAYY 4x150 SE | 38 | 40 | 0.012692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6034-2_0_4_line_43 | NAYY 4x150 SE | 39 | 41 | 0.0058892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6034-2_0_4_line_44 | NAYY 4x150 SE | 40 | 42 | 0.013193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_6034-2_0_4_line_45 | NAYY 4x150 SE | 41 | 48 | 0.013503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6034-2_0_4_line_46 | NAYY 4x150 SE | 42 | 46 | 0.0077573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6034-2_0_4_line_47 | NAYY 4x150 SE | 43 | 44 | 0.0021858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_6034-2_0_4_line_48 | NAYY 4x150 SE | 44 | 45 | 0.0075889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_6034-2_0_4_line_49 | NAYY 4x150 SE | 45 | 49 | 0.00058624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_6034-2_0_4_line_50 | NAYY 4x150 SE | 46 | 47 | 0.010316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6034-2_0_4_line_51 | NAYY 4x150 SE | 48 | 56 | 0.018492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6034-2_0_4_line_52 | NAYY 4x150 SE | 49 | 50 | 0.019304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6034-2_0_4_line_53 | NAYY 4x150 SE | 50 | 51 | 0.015206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6034-2_0_4_line_54 | NAYY 4x150 SE | 51 | 52 | 0.011343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6034-2_0_4_line_55 | NAYY 4x150 SE | 54 | 55 | 0.015803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_6034-2_0_4_line_56 | NAYY 4x150 SE | 56 | 57 | 0.0049815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_6034-2_0_4_line_57 | NAYY 4x150 SE | 57 | 58 | 0.027722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6034-2_0_4_trafo_37 | 0.25 MVA 20/0.4 kV | 59 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2573622.8984 | 1086741.4626 | 2573637.1347 | 1086736.5203
1 | 2573628.5935 | 1086754.2445 | 2573627.6376 | 1086750.2688 | 2573622.8984 | 1086741.4626
2 | 2573628.5935 | 1086754.2445 | 2573629.8129 | 1086763.5219 | 2573628.9615 | 1086781.7796
3 | 2573628.9615 | 1086781.7796 | 2573630.0147 | 1086786.7332 | 2573629.8679 | 1086789.3885
4 | 2573442.6431 | 1086778.1772 | 2573438.0367 | 1086784.058 | 2573406.0316 | 1086821.3956 | 2573399.9073 | 1086830.4979
5 | 2573399.9073 | 1086830.4979 | 2573393.6235 | 1086839.8375 | 2573392.1302 | 1086841.3358
6 | 2573629.8679 | 1086789.3885 | 2573629.461 | 1086796.7519 | 2573629.3068 | 1086800.6878
7 | 2573660.4431 | 1086832.5776 | 2573662.0524 | 1086818.7981
8 | 2573660.4431 | 1086832.5776 | 2573658.8345 | 1086846.3517
9 | 2573626.2154 | 1086894.5072 | 2573626.2415 | 1086894.178
10 | 2573625.305 | 1086905.9718 | 2573626.2154 | 1086894.5072
11 | 2573626.2415 | 1086894.178 | 2573627.0112 | 1086884.4864 | 2573627.188 | 1086874.0321
12 | 2573625.305 | 1086905.9718 | 2573623.8753 | 1086933.9593 | 2573623.5703 | 1086938.7298
13 | 2573625.305 | 1086905.9718 | 2573651.7951 | 1086905.9678
14 | 2573627.188 | 1086874.0321 | 2573627.2455 | 1086870.6319
15 | 2573623.5703 | 1086938.7298 | 2573617.3067 | 1086937.8788 | 2573611.078 | 1086936.7313
16 | 2573651.7951 | 1086905.9678 | 2573675.2828 | 1086908.4045
17 | 2573651.7951 | 1086905.9678 | 2573655.3483 | 1086882.8625 | 2573655.8769 | 1086876.7197
18 | 2573627.3082 | 1086866.922 | 2573627.2455 | 1086870.6319
19 | 2573611.078 | 1086936.7313 | 2573600.5569 | 1086934.7931
20 | 2573701.8942 | 1086914.1436 | 2573676.9934 | 1086908.582 | 2573675.2828 | 1086908.4045
21 | 2573655.8769 | 1086876.7197 | 2573657.2963 | 1086860.2275
22 | 2573627.3082 | 1086866.922 | 2573627.4782 | 1086856.8709
23 | 2573600.5569 | 1086934.7931 | 2573591.7872 | 1086933.1774
24 | 2573701.8942 | 1086914.1436 | 2573704.0482 | 1086933.2554 | 2573704.01 | 1086944.0999
25 | 2573701.8942 | 1086914.1436 | 2573732.5301 | 1086920.2784
26 | 2573657.2963 | 1086860.2275 | 2573657.5267 | 1086857.5508 | 2573658.8345 | 1086846.3517
27 | 2573591.4863 | 1086933.122 | 2573591.7872 | 1086933.1774
28 | 2573591.4863 | 1086933.122 | 2573503.3283 | 1086898.193
29 | 2573503.3283 | 1086898.193 | 2573507.3391 | 1086887.0202 | 2573507.6017 | 1086870.7772 | 2573511.2924 | 1086865.0803 | 2573516.2697 | 1086859.1332 | 2573518.4867 | 1086857.0113 | 2573519.5654 | 1086855.328 | 2573521.1294 | 1086851.1189 | 2573522.6357 | 1086841.4912
30 | 2573455.149 | 1086955.9512 | 2573503.3283 | 1086898.193
31 | 2573363.4726 | 1086866.5282 | 2573378.7566 | 1086854.7549 | 2573392.1302 | 1086841.3358
32 | 2573363.4726 | 1086866.5282 | 2573357.7262 | 1086872.1897 | 2573357.3182 | 1086874.6706 | 2573358.5935 | 1086877.1441 | 2573366.3198 | 1086887.8046 | 2573371.3991 | 1086899.822 | 2573373.8216 | 1086907.4154 | 2573373.973 | 1086908.3374 | 2573374.3798 | 1086910.8814 | 2573374.1661 | 1086916.9744 | 2573373.6089 | 1086920.8011 | 2573373.0888 | 1086924.2607
33 | 2573373.0888 | 1086924.2607 | 2573377.3054 | 1086925.2872 | 2573380.1884 | 1086929.9993 | 2573384.6355 | 1086935.8384 | 2573389.5402 | 1086939.9079 | 2573395.1237 | 1086943.0962 | 2573405.6997 | 1086947.3632 | 2573412.2628 | 1086949.3021 | 2573416.67 | 1086950.3099
34 | 2573445.8418 | 1086956.5345 | 2573442.7701 | 1086956.2166 | 2573436.5284 | 1086955.0544 | 2573431.5814 | 1086953.7198 | 2573416.67 | 1086950.3099
35 | 2573455.149 | 1086955.9512 | 2573447.6126 | 1086956.7179 | 2573445.8418 | 1086956.5345
36 | 2573524.0303 | 1086836.2944 | 2573523.084 | 1086838.6261 | 2573522.6357 | 1086841.4912
37 | 2573527.7015 | 1086806.0784 | 2573528.6961 | 1086807.5075 | 2573530.8773 | 1086813.1565 | 2573531.0175 | 1086815.0791 | 2573530.3134 | 1086819.0287 | 2573528.648 | 1086824.9168 | 2573524.0303 | 1086836.2944
38 | 2573801.7686 | 1086931.6368 | 2573787.4899 | 1086930.147
39 | 2573784.1624 | 1086929.7998 | 2573787.4899 | 1086930.147
40 | 2573775.6339 | 1086928.91 | 2573784.1624 | 1086929.7998
41 | 2573775.6339 | 1086928.91 | 2573774.9793 | 1086951.6605
42 | 2573775.6339 | 1086928.91 | 2573763.1885 | 1086926.4178
43 | 2573774.9793 | 1086951.6605 | 2573774.8099 | 1086957.5473
44 | 2573750.2519 | 1086923.8272 | 2573763.1885 | 1086926.4178
45 | 2573774.4216 | 1086971.0444 | 2573774.8099 | 1086957.5473
46 | 2573742.6456 | 1086922.3041 | 2573750.2519 | 1086923.8272
47 | 2573627.4782 | 1086856.8709 | 2573627.5152 | 1086854.6855
48 | 2573627.7248 | 1086847.0996 | 2573627.5418 | 1086853.1121 | 2573627.5152 | 1086854.6855
49 | 2573627.7248 | 1086847.0996 | 2573627.7426 | 1086846.5136
50 | 2573742.6456 | 1086922.3041 | 2573732.5301 | 1086920.2784
51 | 2573774.4216 | 1086971.0444 | 2573773.8897 | 1086989.5292
52 | 2573628.3298 | 1086827.2185 | 2573627.7426 | 1086846.5136
53 | 2573628.3298 | 1086827.2185 | 2573628.5463 | 1086820.1015 | 2573628.8628 | 1086812.022
54 | 2573629.3068 | 1086800.6878 | 2573628.8628 | 1086812.022
55 | 2573703.9543 | 1086959.9031 | 2573704.01 | 1086944.0999
56 | 2573773.8897 | 1086989.5292 | 2573773.7464 | 1086994.5087
57 | 2573772.9491 | 1087022.219 | 2573773.7464 | 1086994.5087

## bus_geodata
| x | y | coords
0 | 2573637.1347 | 1086736.5203
1 | 2573622.8984 | 1086741.4626
2 | 2573628.5935 | 1086754.2445
3 | 2573628.9615 | 1086781.7796
4 | 2573442.6431 | 1086778.1772
5 | 2573399.9073 | 1086830.4979
6 | 2573629.8679 | 1086789.3885
7 | 2573662.0524 | 1086818.7981
8 | 2573660.4431 | 1086832.5776
9 | 2573626.2154 | 1086894.5072
10 | 2573626.2415 | 1086894.178
11 | 2573625.305 | 1086905.9718
12 | 2573627.188 | 1086874.0321
13 | 2573623.5703 | 1086938.7298
14 | 2573651.7951 | 1086905.9678
15 | 2573627.2455 | 1086870.6319
16 | 2573611.078 | 1086936.7313
17 | 2573675.2828 | 1086908.4045
18 | 2573655.8769 | 1086876.7197
19 | 2573627.3082 | 1086866.922
20 | 2573600.5569 | 1086934.7931
21 | 2573701.8942 | 1086914.1436
22 | 2573657.2963 | 1086860.2275
23 | 2573591.7872 | 1086933.1774
24 | 2573591.4863 | 1086933.122
25 | 2573503.3283 | 1086898.193
26 | 2573392.1302 | 1086841.3358
27 | 2573363.4726 | 1086866.5282
28 | 2573373.0888 | 1086924.2607
29 | 2573416.6699 | 1086950.3099
30 | 2573445.8418 | 1086956.5345
31 | 2573455.149 | 1086955.9512
32 | 2573522.6357 | 1086841.4912
33 | 2573527.7015 | 1086806.0784
34 | 2573524.0303 | 1086836.2944
35 | 2573787.4899 | 1086930.147
36 | 2573801.7686 | 1086931.6368
37 | 2573784.1624 | 1086929.7998
38 | 2573775.6339 | 1086928.91
39 | 2573774.9793 | 1086951.6605
40 | 2573763.1885 | 1086926.4178
41 | 2573774.8099 | 1086957.5473
42 | 2573750.2519 | 1086923.8272
43 | 2573627.4782 | 1086856.8709
44 | 2573627.5152 | 1086854.6855
45 | 2573627.7248 | 1086847.0996
46 | 2573742.6456 | 1086922.3041
47 | 2573732.5301 | 1086920.2784
48 | 2573774.4216 | 1086971.0444
49 | 2573627.7426 | 1086846.5136
50 | 2573628.3298 | 1086827.2185
51 | 2573628.8628 | 1086812.022
52 | 2573629.3068 | 1086800.6878
53 | 2573658.8345 | 1086846.3517
54 | 2573704.01 | 1086944.0999
55 | 2573703.9543 | 1086959.9031
56 | 2573773.8897 | 1086989.5292
57 | 2573773.7464 | 1086994.5087
58 | 2573772.9491 | 1087022.219
59 | 2573651.7951 | 1086905.9678

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1