## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6037-191_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6037-191_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6037-191_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6037-191_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6037-191_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6037-191_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6037-191_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6037-191_0_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_6037-191_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_6037-191_0_3_node_40 | 0.4 | n |  | TRUE
10 | bus_LV_6037-191_0_3_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_6037-191_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_6037-191_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_6037-191_0_3_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_6037-191_0_3_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_6037-191_0_3_node_45 | 0.4 | n |  | TRUE
16 | bus_LV_6037-191_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_6037-191_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_6037-191_0_3_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_6037-191_0_3_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_6037-191_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_6037-191_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_6037-191_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_6037-191_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_6037-191_0_3_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_6037-191_0_3_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_6037-191_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_6037-191_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6037-191_0_3_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_6037-191_0_3_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_6037-191_0_3_node_42 | 0.4 | n |  | TRUE
31 | bus_LV_6037-191_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_6037-191_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_6037-191_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_6037-191_0_3_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_6037-191_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_6037-191_0_3_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_6037-191_0_3_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_6037-191_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_6037-191_0_3_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_6037-191_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_6037-191_0_3_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_6037-191_0_3_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_6037-191_0_3_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_6037-191_0_3_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_6037-191_0_3_node_44 | 0.4 | n |  | TRUE
46 | bus_MV_101_1_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6037-191_0_3_load_0 | 0 | 0.0081337 | 0.0020385 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6037-191_0_3_load_1 | 1 | 0.0037834 | 0.0009482 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6037-191_0_3_load_4 | 4 | 0.016484 | 0.0041312 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6037-191_0_3_load_5 | 5 | 0.012774 | 0.0032015 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6037-191_0_3_load_6 | 6 | 0.0020365 | 0.00051038 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6037-191_0_3_load_39 | 10 | 0.0087334 | 0.0021888 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6037-191_0_3_load_12 | 12 | 0.0035311 | 0.00088498 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6037-191_0_3_load_47 | 13 | 0.0105 | 0.0026315 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6037-191_0_3_load_48 | 14 | 0.011103 | 0.0027826 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6037-191_0_3_load_45 | 15 | 0.0066011 | 0.0016544 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6037-191_0_3_load_23 | 17 | 0.0082501 | 0.0020677 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6037-191_0_3_load_22 | 18 | 0.0034567 | 0.00086634 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6037-191_0_3_load_19 | 19 | 0.0027508 | 0.00068941 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6037-191_0_3_load_16 | 20 | 0.0033325 | 0.0008352 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6037-191_0_3_load_24 | 23 | 0.0032276 | 0.00080892 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6037-191_0_3_load_21 | 24 | 0.0043513 | 0.0010905 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6037-191_0_3_load_35 | 25 | 0.0037846 | 0.00094851 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6037-191_0_3_load_17 | 27 | 0.0049568 | 0.0012423 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6037-191_0_3_load_41 | 28 | 0.013072 | 0.0032761 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6037-191_0_3_load_36 | 29 | 0.0031277 | 0.00078387 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6037-191_0_3_load_42 | 30 | 0.0067169 | 0.0016834 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6037-191_0_3_load_37 | 31 | 0.0079189 | 0.0019847 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6037-191_0_3_load_20 | 33 | 0.0079822 | 0.0020005 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6037-191_0_3_load_30 | 34 | 0.0056384 | 0.0014131 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6037-191_0_3_load_27 | 35 | 0.0049359 | 0.001237 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6037-191_0_3_load_25 | 36 | 0.0067655 | 0.0016956 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6037-191_0_3_load_31 | 40 | 0.0063751 | 0.0015977 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6037-191_0_3_load_51 | 41 | 0.0066462 | 0.0016657 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6037-191_0_3_load_32 | 42 | 0.0076258 | 0.0019112 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6037-191_0_3_load_33 | 43 | 0.010734 | 0.0026901 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6037-191_0_3_load_49 | 44 | 0.0054362 | 0.0013624 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6037-191_0_3_load_44 | 45 | 0.0039561 | 0.00099149 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6037-191_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6037-191_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.025126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6037-191_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.010261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6037-191_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0032887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6037-191_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.015296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6037-191_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6037-191_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0019312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6037-191_0_3_line_7 | NAYY 4x150 SE | 7 | 11 | 0.027765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6037-191_0_3_line_8 | NAYY 4x150 SE | 7 | 12 | 0.014818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_6037-191_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.031561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6037-191_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.0098624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6037-191_0_3_line_11 | NAYY 4x150 SE | 9 | 13 | 0.039763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6037-191_0_3_line_12 | NAYY 4x150 SE | 9 | 14 | 0.018796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6037-191_0_3_line_13 | NAYY 4x150 SE | 9 | 15 | 0.026713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6037-191_0_3_line_14 | NAYY 4x150 SE | 10 | 16 | 0.023785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6037-191_0_3_line_15 | NAYY 4x150 SE | 11 | 19 | 0.011743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6037-191_0_3_line_16 | NAYY 4x150 SE | 11 | 20 | 0.029883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6037-191_0_3_line_17 | NAYY 4x150 SE | 12 | 21 | 0.03804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6037-191_0_3_line_18 | NAYY 4x150 SE | 13 | 44 | 0.0078299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6037-191_0_3_line_19 | NAYY 4x150 SE | 14 | 45 | 0.036661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6037-191_0_3_line_20 | NAYY 4x150 SE | 16 | 28 | 0.016063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6037-191_0_3_line_21 | NAYY 4x150 SE | 16 | 21 | 0.028588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6037-191_0_3_line_22 | NAYY 4x150 SE | 17 | 18 | 0.0017159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6037-191_0_3_line_23 | NAYY 4x150 SE | 18 | 33 | 0.013354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6037-191_0_3_line_24 | NAYY 4x150 SE | 19 | 25 | 0.0036723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6037-191_0_3_line_25 | NAYY 4x150 SE | 21 | 26 | 0.024873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6037-191_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.022261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6037-191_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.015145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6037-191_0_3_line_28 | NAYY 4x150 SE | 23 | 32 | 0.0046375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6037-191_0_3_line_29 | NAYY 4x150 SE | 24 | 33 | 0.013328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6037-191_0_3_line_30 | NAYY 4x150 SE | 25 | 34 | 0.0065114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6037-191_0_3_line_31 | NAYY 4x150 SE | 26 | 27 | 0.028812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6037-191_0_3_line_32 | NAYY 4x150 SE | 27 | 29 | 0.010887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6037-191_0_3_line_33 | NAYY 4x150 SE | 28 | 30 | 0.018949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6037-191_0_3_line_34 | NAYY 4x150 SE | 29 | 31 | 0.015306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6037-191_0_3_line_35 | NAYY 4x150 SE | 32 | 34 | 0.014874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6037-191_0_3_line_36 | NAYY 4x150 SE | 32 | 35 | 0.01701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6037-191_0_3_line_37 | NAYY 4x150 SE | 35 | 37 | 0.024351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6037-191_0_3_line_38 | NAYY 4x150 SE | 36 | 37 | 0.018699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6037-191_0_3_line_39 | NAYY 4x150 SE | 37 | 38 | 0.05753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6037-191_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.048711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6037-191_0_3_line_41 | NAYY 4x150 SE | 38 | 40 | 0.013535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6037-191_0_3_line_42 | NAYY 4x150 SE | 39 | 41 | 0.0455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6037-191_0_3_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0012653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6037-191_0_3_line_44 | NAYY 4x150 SE | 42 | 43 | 0.010742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6037-191_0_3_trafo_12 | 0.25 MVA 20/0.4 kV | 46 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2579271.4302 | 1103989.9685 | 2579264.2446 | 1103992.1017 | 2579261.8008 | 1103993.8365
1 | 2579294.1149 | 1103980.0043 | 2579284.5996 | 1103986.4513 | 2579274.3596 | 1103989.0988 | 2579271.4302 | 1103989.9685
2 | 2579253.434 | 1103999.776 | 2579261.8008 | 1103993.8365
3 | 2579294.1149 | 1103980.0043 | 2579296.2751 | 1103977.5246
4 | 2579294.1149 | 1103980.0043 | 2579285.0349 | 1103992.3138
5 | 2579253.434 | 1103999.776 | 2579253.8245 | 1104007.6453 | 2579255.4468 | 1104010.082
6 | 2579297.5436 | 1103976.0684 | 2579296.2751 | 1103977.5246
7 | 2579297.5436 | 1103976.0684 | 2579318.3601 | 1103994.5064
8 | 2579297.5436 | 1103976.0684 | 2579301.712 | 1103971.3073 | 2579307.1998 | 1103964.8287
9 | 2579264.4833 | 1103926.4233 | 2579265.9544 | 1103933.5997 | 2579267.4877 | 1103945.3559 | 2579272.7165 | 1103956.5769
10 | 2579272.7165 | 1103956.5769 | 2579282.1646 | 1103953.7488
11 | 2579264.4833 | 1103926.4233 | 2579248.7598 | 1103902.2873 | 2579241.9831 | 1103893.6769
12 | 2579264.4833 | 1103926.4233 | 2579279.9785 | 1103915.7837
13 | 2579264.4833 | 1103926.4233 | 2579243.1993 | 1103938.6469 | 2579241.278 | 1103939.6524
14 | 2579304.8139 | 1103946.4952 | 2579291.2001 | 1103951.0442 | 2579282.1646 | 1103953.7488
15 | 2579318.3601 | 1103994.5064 | 2579326.5335 | 1104002.9387
16 | 2579318.3601 | 1103994.5064 | 2579321.8994 | 1103986.7126 | 2579329.8164 | 1103969.7881 | 2579331.1252 | 1103967.4966
17 | 2579331.2069 | 1103935.3327 | 2579319.6318 | 1103950.2131 | 2579311.2034 | 1103960.1025 | 2579307.1998 | 1103964.8287
18 | 2579241.9831 | 1103893.6769 | 2579237.1406 | 1103887.524
19 | 2579279.9785 | 1103915.7837 | 2579306.1864 | 1103897.7882 | 2579310.1845 | 1103895.0081
20 | 2579304.8139 | 1103946.4952 | 2579303.7648 | 1103936.038 | 2579305.4329 | 1103930.7407
21 | 2579331.2069 | 1103935.3327 | 2579324.6576 | 1103938.2788 | 2579304.8139 | 1103946.4952
22 | 2579286.2051 | 1104053.3015 | 2579285.0652 | 1104054.5841
23 | 2579286.2051 | 1104053.3015 | 2579291.8536 | 1104046.9458 | 2579294.7238 | 1104043.0352
24 | 2579326.5335 | 1104002.9387 | 2579329.0894 | 1104005.5756
25 | 2579331.2069 | 1103935.3327 | 2579343.6029 | 1103929.7653 | 2579353.8588 | 1103924.9167
26 | 2579310.5797 | 1104019.6791 | 2579326.6151 | 1104017.5676 | 2579330.9409 | 1104021.8496
27 | 2579310.5797 | 1104019.6791 | 2579308.3963 | 1104023.5774 | 2579306.6489 | 1104028.3191 | 2579303.7217 | 1104031.8754 | 2579303.0592 | 1104032.6474
28 | 2579334.2368 | 1104025.112 | 2579330.9409 | 1104021.8496
29 | 2579294.7238 | 1104043.0352 | 2579298.1438 | 1104038.3755 | 2579303.0592 | 1104032.6474
30 | 2579329.0894 | 1104005.5756 | 2579333.6213 | 1104010.2511
31 | 2579353.8588 | 1103924.9167 | 2579379.9027 | 1103912.5952
32 | 2579379.9027 | 1103912.5952 | 2579389.7435 | 1103907.9394
33 | 2579318.4898 | 1103917.0239 | 2579309.185 | 1103926.359 | 2579305.4329 | 1103930.7407
34 | 2579403.7432 | 1103901.7559 | 2579393.3607 | 1103906.2281 | 2579389.7435 | 1103907.9394
35 | 2579334.2368 | 1104025.112 | 2579333.6213 | 1104010.2511
36 | 2579334.2368 | 1104025.112 | 2579343.8345 | 1104039.1559
37 | 2579357.5742 | 1104059.2606 | 2579343.8345 | 1104039.1559
38 | 2579357.5742 | 1104059.2606 | 2579341.9671 | 1104069.5589
39 | 2579357.5742 | 1104059.2606 | 2579394.1322 | 1104037.1915 | 2579406.7059 | 1104029.3335
40 | 2579448.0786 | 1104003.6243 | 2579441.0386 | 1104007.8614 | 2579412.0626 | 1104025.9803 | 2579406.7059 | 1104029.3335
41 | 2579406.7059 | 1104029.3335 | 2579398.7529 | 1104018.381
42 | 2579417.7135 | 1103984.0955 | 2579425.1585 | 1103978.3784 | 2579428.3742 | 1103977.756 | 2579430.7679 | 1103978.7817 | 2579441.6012 | 1103993.6301 | 2579448.0786 | 1104003.6243
43 | 2579398.7529 | 1104018.381 | 2579398.0095 | 1104017.3571 | 2579398.0095 | 1104017.3571
44 | 2579406.6707 | 1104011.0022 | 2579398.0095 | 1104017.3571

## bus_geodata
| x | y | coords
0 | 2579271.4302 | 1103989.9685
1 | 2579261.8008 | 1103993.8365
2 | 2579294.1149 | 1103980.0043
3 | 2579253.434 | 1103999.776
4 | 2579296.2751 | 1103977.5246
5 | 2579285.0349 | 1103992.3138
6 | 2579255.4468 | 1104010.082
7 | 2579297.5436 | 1103976.0684
8 | 2579272.7165 | 1103956.577
9 | 2579264.4833 | 1103926.4233
10 | 2579282.1646 | 1103953.7488
11 | 2579318.3601 | 1103994.5064
12 | 2579307.1998 | 1103964.8287
13 | 2579241.9831 | 1103893.6769
14 | 2579279.9785 | 1103915.7837
15 | 2579241.278 | 1103939.6524
16 | 2579304.8139 | 1103946.4952
17 | 2579285.0652 | 1104054.5841
18 | 2579286.2051 | 1104053.3015
19 | 2579326.5335 | 1104002.9387
20 | 2579331.1252 | 1103967.4966
21 | 2579331.2069 | 1103935.3327
22 | 2579310.5797 | 1104019.6791
23 | 2579330.9409 | 1104021.8496
24 | 2579303.0592 | 1104032.6474
25 | 2579329.0894 | 1104005.5756
26 | 2579353.8588 | 1103924.9167
27 | 2579379.9027 | 1103912.5952
28 | 2579305.4329 | 1103930.7407
29 | 2579389.7435 | 1103907.9394
30 | 2579318.4898 | 1103917.0239
31 | 2579403.7432 | 1103901.7559
32 | 2579334.2368 | 1104025.112
33 | 2579294.7238 | 1104043.0352
34 | 2579333.6213 | 1104010.2511
35 | 2579343.8345 | 1104039.1559
36 | 2579341.9671 | 1104069.5589
37 | 2579357.5742 | 1104059.2606
38 | 2579406.7059 | 1104029.3335
39 | 2579448.0786 | 1104003.6243
40 | 2579398.7529 | 1104018.381
41 | 2579417.7135 | 1103984.0955
42 | 2579398.0095 | 1104017.3571
43 | 2579406.6707 | 1104011.0022
44 | 2579237.1406 | 1103887.524
45 | 2579310.1845 | 1103895.0081
46 | 2579297.5436 | 1103976.0684

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1