## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6037-239_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6037-239_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6037-239_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6037-239_0_4_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_6037-239_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6037-239_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_6037-239_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_6037-239_0_4_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_6037-239_0_4_node_44 | 0.4 | n |  | TRUE
9 | bus_LV_6037-239_0_4_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_6037-239_0_4_node_31 | 0.4 | n |  | TRUE
11 | bus_LV_6037-239_0_4_node_45 | 0.4 | n |  | TRUE
12 | bus_LV_6037-239_0_4_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_6037-239_0_4_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_6037-239_0_4_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_6037-239_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_6037-239_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_6037-239_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_6037-239_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_6037-239_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_6037-239_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_6037-239_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_6037-239_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_6037-239_0_4_node_37 | 0.4 | n |  | TRUE
24 | bus_LV_6037-239_0_4_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_6037-239_0_4_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_6037-239_0_4_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_6037-239_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_6037-239_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_6037-239_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_6037-239_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_6037-239_0_4_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_6037-239_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_6037-239_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_6037-239_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_6037-239_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_6037-239_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_6037-239_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6037-239_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_6037-239_0_4_node_40 | 0.4 | n |  | TRUE
40 | bus_LV_6037-239_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_6037-239_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_6037-239_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_MV_197_0_node_287 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6037-239_0_4_load_0 | 0 | 0.00043865 | 0.00010994 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6037-239_0_4_load_1 | 1 | 0.00059063 | 0.00014803 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6037-239_0_4_load_8 | 3 | 0.00049282 | 0.00012351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6037-239_0_4_load_3 | 4 | 0.00053343 | 0.00013369 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6037-239_0_4_load_7 | 6 | 0.00071568 | 0.00017937 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6037-239_0_4_load_44 | 8 | 0.0082341 | 0.0020637 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6037-239_0_4_load_48 | 9 | 0.00057437 | 0.00014395 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6037-239_0_4_load_31 | 10 | 0.0053617 | 0.0013438 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6037-239_0_4_load_45 | 11 | 0.0010469 | 0.00026237 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6037-239_0_4_load_47 | 13 | 0.0005574 | 0.0001397 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6037-239_0_4_load_30 | 14 | 0.00037085 | 9.2944e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6037-239_0_4_load_9 | 15 | 0.0017748 | 0.0004448 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6037-239_0_4_load_10 | 16 | 0.010723 | 0.0026875 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6037-239_0_4_load_13 | 18 | 0.0052556 | 0.0013172 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6037-239_0_4_load_37 | 23 | 0.0075897 | 0.0019022 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6037-239_0_4_load_36 | 24 | 0.009891 | 0.0024789 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6037-239_0_4_load_39 | 26 | 0.010795 | 0.0027056 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6037-239_0_4_load_20 | 28 | 0.0024727 | 0.00061972 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6037-239_0_4_load_38 | 29 | 0.013335 | 0.0033421 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6037-239_0_4_load_26 | 30 | 0.012342 | 0.0030933 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6037-239_0_4_load_19 | 32 | 0.0026115 | 0.00065451 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6037-239_0_4_load_21 | 33 | 0.0032569 | 0.00081626 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6037-239_0_4_load_22 | 34 | 0.00273 | 0.00068421 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6037-239_0_4_load_23 | 35 | 0.0065185 | 0.0016337 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6037-239_0_4_load_24 | 36 | 0.0081454 | 0.0020414 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6037-239_0_4_load_27 | 37 | 0.0059557 | 0.0014926 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6037-239_0_4_load_29 | 38 | 0.0069589 | 0.0017441 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6037-239_0_4_load_40 | 39 | 0.010876 | 0.0027257 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6037-239_0_4_load_41 | 40 | 0.0058589 | 0.0014684 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6037-239_0_4_load_32 | 41 | 0.007458 | 0.0018692 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6037-239_0_4_load_34 | 42 | 0.003725 | 0.00093358 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6037-239_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.014982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6037-239_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.083442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6037-239_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.093753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6037-239_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.024768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6037-239_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.11943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6037-239_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.050963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6037-239_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.055461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6037-239_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.074179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6037-239_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.013174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6037-239_0_4_line_9 | NAYY 4x150 SE | 7 | 10 | 0.011426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6037-239_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.024962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6037-239_0_4_line_11 | NAYY 4x150 SE | 9 | 13 | 0.038313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6037-239_0_4_line_12 | NAYY 4x150 SE | 10 | 41 | 0.0054624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6037-239_0_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.068593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6037-239_0_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.17849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6037-239_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.0066763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6037-239_0_4_line_16 | NAYY 4x150 SE | 15 | 17 | 0.015135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6037-239_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.0095569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6037-239_0_4_line_18 | NAYY 4x150 SE | 18 | 19 | 0.039893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6037-239_0_4_line_19 | NAYY 4x150 SE | 19 | 20 | 0.026854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6037-239_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.02599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6037-239_0_4_line_21 | NAYY 4x150 SE | 20 | 22 | 0.05467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_6037-239_0_4_line_22 | NAYY 4x150 SE | 20 | 23 | 0.060994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6037-239_0_4_line_23 | NAYY 4x150 SE | 21 | 26 | 0.070462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6037-239_0_4_line_24 | NAYY 4x150 SE | 21 | 27 | 0.077323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6037-239_0_4_line_25 | NAYY 4x150 SE | 22 | 29 | 0.018539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6037-239_0_4_line_26 | NAYY 4x150 SE | 22 | 30 | 0.015829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6037-239_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.055467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6037-239_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.028758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6037-239_0_4_line_29 | NAYY 4x150 SE | 25 | 42 | 0.020517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6037-239_0_4_line_30 | NAYY 4x150 SE | 26 | 31 | 0.014227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6037-239_0_4_line_31 | NAYY 4x150 SE | 27 | 28 | 0.016971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6037-239_0_4_line_32 | NAYY 4x150 SE | 28 | 32 | 0.0043164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6037-239_0_4_line_33 | NAYY 4x150 SE | 30 | 36 | 0.0063766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6037-239_0_4_line_34 | NAYY 4x150 SE | 31 | 40 | 0.031312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6037-239_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.013092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6037-239_0_4_line_36 | NAYY 4x150 SE | 33 | 34 | 0.013141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6037-239_0_4_line_37 | NAYY 4x150 SE | 35 | 36 | 0.070379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6037-239_0_4_line_38 | NAYY 4x150 SE | 37 | 38 | 0.031023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6037-239_0_4_line_39 | NAYY 4x150 SE | 38 | 39 | 0.0011664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6037-239_0_4_line_40 | NAYY 4x150 SE | 39 | 40 | 0.0070307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6037-239_0_4_line_41 | NAYY 4x150 SE | 41 | 42 | 0.023533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6037-239_0_4_trafo_28 | 0.25 MVA 20/0.4 kV | 43 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2585308.8647 | 1101531.3689 | 2585297.0832 | 1101540.6245
1 | 2585374.0177 | 1101479.4505 | 2585366.9784 | 1101486.9269 | 2585348.7093 | 1101500.0666 | 2585308.8647 | 1101531.3689
2 | 2585297.0832 | 1101540.6245 | 2585325.9718 | 1101629.8162
3 | 2585374.0177 | 1101479.4505 | 2585350.385 | 1101486.862
4 | 2585344.727 | 1101424.7829 | 2585349.1792 | 1101429.0631 | 2585387.1041 | 1101438.2759 | 2585386.342 | 1101446.3262 | 2585383.6633 | 1101455.4261 | 2585387.152 | 1101454.8952 | 2585391.4159 | 1101454.9071 | 2585395.686 | 1101454.2965 | 2585400.3538 | 1101454.9522 | 2585399.2959 | 1101462.3029 | 2585397.5917 | 1101467.9432 | 2585394.5733 | 1101470.9854 | 2585374.0177 | 1101479.4505
5 | 2585302.3165 | 1101503.7807 | 2585314.1799 | 1101499.6169 | 2585344.9747 | 1101488.5588 | 2585350.385 | 1101486.862
6 | 2585344.727 | 1101424.7829 | 2585347.0824 | 1101422.7984 | 2585352.0727 | 1101419.24 | 2585357.1478 | 1101412.3131 | 2585361.0783 | 1101405.678 | 2585361.1855 | 1101392.4266 | 2585359.6129 | 1101375.7999
7 | 2585344.727 | 1101424.7829 | 2585332.4011 | 1101428.5146 | 2585292.497 | 1101435.9821 | 2585275.5636 | 1101441.5706 | 2585273.0993 | 1101443.0456
8 | 2585302.3165 | 1101503.7807 | 2585289.8858 | 1101508.1435
9 | 2585359.6129 | 1101375.7999 | 2585356.954 | 1101373.872 | 2585355.0359 | 1101371.1419 | 2585354.6606 | 1101366.3516
10 | 2585273.0993 | 1101443.0456 | 2585262.2113 | 1101449.5628 | 2585255.7728 | 1101460.0103
11 | 2585256.4228 | 1101525.7646 | 2585262.5924 | 1101520.0862 | 2585268.6651 | 1101516.1694 | 2585275.2356 | 1101513.2853 | 2585289.8858 | 1101508.1435
12 | 2585354.6606 | 1101366.3516 | 2585357.2103 | 1101361.5207
13 | 2585208.2081 | 1101573.8462 | 2585216.7208 | 1101567.8224 | 2585221.2146 | 1101563.8093 | 2585227.0568 | 1101554.2791 | 2585230.1438 | 1101550.8699 | 2585234.3961 | 1101546.2016 | 2585247.7451 | 1101533.7516 | 2585256.4228 | 1101525.7646
14 | 2585208.2081 | 1101573.8462 | 2585039.762 | 1101514.8143
15 | 2585464.6361 | 1101202.9014 | 2585471.1609 | 1101201.4872
16 | 2585449.8443 | 1101206.1075 | 2585464.6361 | 1101202.9014
17 | 2585449.8443 | 1101206.1075 | 2585448.8305 | 1101202.875 | 2585444.6021 | 1101198.3829
18 | 2585405.2028 | 1101204.0586 | 2585413.1842 | 1101202.0383 | 2585424.6423 | 1101200.8767 | 2585439.7735 | 1101198.5279 | 2585444.6021 | 1101198.3829
19 | 2585384.4822 | 1101218.3381 | 2585389.2894 | 1101218.9268 | 2585394.8273 | 1101214.5334 | 2585399.9106 | 1101207.6954 | 2585405.2028 | 1101204.0586
20 | 2585384.4822 | 1101218.3381 | 2585386.4979 | 1101207.0387 | 2585387.0122 | 1101192.5412
21 | 2585384.4822 | 1101218.3381 | 2585377.7619 | 1101223.3903 | 2585373.5295 | 1101236.4626 | 2585366.9499 | 1101248.4735 | 2585359.8599 | 1101257.4619 | 2585353.4149 | 1101261.1572
22 | 2585384.4822 | 1101218.3381 | 2585383.8331 | 1101221.8859 | 2585374.8329 | 1101256.9698 | 2585368.0656 | 1101277.0265
23 | 2585387.0122 | 1101192.5412 | 2585369.0927 | 1101197.0424 | 2585317.6978 | 1101204.8567
24 | 2585387.0122 | 1101192.5412 | 2585386.0516 | 1101185.6957 | 2585385.3973 | 1101180.7614 | 2585384.1359 | 1101171.193 | 2585384.0043 | 1101161.5774 | 2585386.9256 | 1101153.5663 | 2585392.1438 | 1101148.0953 | 2585401.4546 | 1101138.9682 | 2585414.398 | 1101127.8869
25 | 2585360.3611 | 1101243.965 | 2585353.4149 | 1101261.1572
26 | 2585353.4149 | 1101261.1572 | 2585339.6842 | 1101269.0321
27 | 2585376.2095 | 1101326.8906 | 2585372.2815 | 1101321.8309 | 2585368.0889 | 1101316.1048 | 2585363.6288 | 1101308.6119 | 2585361.0552 | 1101303.6156 | 2585362.1784 | 1101294.4749 | 2585368.0656 | 1101277.0265
28 | 2585376.2095 | 1101326.8906 | 2585376.5518 | 1101321.2758 | 2585374.956 | 1101314.1983 | 2585373.6208 | 1101309.2769 | 2585381.2866 | 1101301.7007
29 | 2585376.2095 | 1101326.8906 | 2585378.3196 | 1101332.2437 | 2585378.541 | 1101337.4013 | 2585376.983 | 1101342.73 | 2585374.6686 | 1101346.052
30 | 2585303.6323 | 1101206.9952 | 2585317.6978 | 1101204.8567
31 | 2585414.398 | 1101127.8869 | 2585422.1526 | 1101131.2365 | 2585425.2635 | 1101131.229 | 2585429.5133 | 1101128.5285 | 2585429.8294 | 1101128.3222
32 | 2585429.8294 | 1101128.3222 | 2585433.4438 | 1101125.9626
33 | 2585334.1528 | 1101272.2045 | 2585339.6842 | 1101269.0321
34 | 2585303.6323 | 1101206.9952 | 2585298.3388 | 1101237.8568
35 | 2585445.8032 | 1101122.2895 | 2585441.8503 | 1101122.707 | 2585436.0423 | 1101124.2662 | 2585433.4438 | 1101125.9626
36 | 2585458.8713 | 1101120.9095 | 2585445.8032 | 1101122.2895
37 | 2585334.1528 | 1101272.2045 | 2585327.6426 | 1101275.9383 | 2585322.3526 | 1101289.9582 | 2585321.6255 | 1101306.0125 | 2585315.9432 | 1101317.8211 | 2585305.1261 | 1101333.0916
38 | 2585296.953 | 1101245.936 | 2585296.6047 | 1101247.9663 | 2585292.838 | 1101276.683
39 | 2585297.1502 | 1101244.7863 | 2585296.953 | 1101245.936
40 | 2585297.1502 | 1101244.7863 | 2585298.3388 | 1101237.8568
41 | 2585357.2103 | 1101361.5207 | 2585365.1676 | 1101356.0209 | 2585371.847 | 1101350.1017 | 2585374.6686 | 1101346.052

## bus_geodata
| x | y | coords
0 | 2585308.8647 | 1101531.3689
1 | 2585297.0832 | 1101540.6245
2 | 2585374.0177 | 1101479.4505
3 | 2585325.9718 | 1101629.8162
4 | 2585350.385 | 1101486.862
5 | 2585344.727 | 1101424.7828
6 | 2585302.3165 | 1101503.7807
7 | 2585359.6129 | 1101375.7999
8 | 2585273.0993 | 1101443.0456
9 | 2585289.8858 | 1101508.1435
10 | 2585354.6606 | 1101366.3516
11 | 2585255.7728 | 1101460.0103
12 | 2585208.2081 | 1101573.8462
13 | 2585256.4228 | 1101525.7646
14 | 2585039.762 | 1101514.8143
15 | 2585464.6361 | 1101202.9014
16 | 2585471.1609 | 1101201.4872
17 | 2585449.8443 | 1101206.1075
18 | 2585444.6021 | 1101198.3829
19 | 2585405.2028 | 1101204.0586
20 | 2585384.4822 | 1101218.3381
21 | 2585387.0122 | 1101192.5412
22 | 2585353.4149 | 1101261.1572
23 | 2585368.0656 | 1101277.0265
24 | 2585381.2866 | 1101301.7007
25 | 2585376.2095 | 1101326.8906
26 | 2585317.6978 | 1101204.8567
27 | 2585414.398 | 1101127.8869
28 | 2585429.8294 | 1101128.3222
29 | 2585360.3611 | 1101243.965
30 | 2585339.6842 | 1101269.0321
31 | 2585303.6323 | 1101206.9952
32 | 2585433.4438 | 1101125.9626
33 | 2585445.8032 | 1101122.2895
34 | 2585458.8713 | 1101120.9095
35 | 2585305.1261 | 1101333.0916
36 | 2585334.1528 | 1101272.2045
37 | 2585292.838 | 1101276.683
38 | 2585296.953 | 1101245.936
39 | 2585297.1502 | 1101244.7863
40 | 2585298.3388 | 1101237.8568
41 | 2585357.2103 | 1101361.5207
42 | 2585374.6686 | 1101346.052
43 | 2585360.3611 | 1101243.965

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1