## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6037-269_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6037-269_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6037-269_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6037-269_0_3_node_48 | 0.4 | n |  | TRUE
4 | bus_LV_6037-269_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_6037-269_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_6037-269_0_3_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_6037-269_0_3_node_60 | 0.4 | n |  | TRUE
8 | bus_LV_6037-269_0_3_node_43 | 0.4 | n |  | TRUE
9 | bus_LV_6037-269_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_6037-269_0_3_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_6037-269_0_3_node_44 | 0.4 | n |  | TRUE
12 | bus_LV_6037-269_0_3_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_6037-269_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_6037-269_0_3_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_6037-269_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_6037-269_0_3_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_6037-269_0_3_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_6037-269_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6037-269_0_3_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_6037-269_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_6037-269_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_6037-269_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_6037-269_0_3_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_6037-269_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_6037-269_0_3_node_51 | 0.4 | n |  | TRUE
26 | bus_LV_6037-269_0_3_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_6037-269_0_3_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_6037-269_0_3_node_38 | 0.4 | n |  | TRUE
29 | bus_LV_6037-269_0_3_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_6037-269_0_3_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_6037-269_0_3_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_6037-269_0_3_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_6037-269_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_6037-269_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_6037-269_0_3_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_6037-269_0_3_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_6037-269_0_3_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_6037-269_0_3_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_6037-269_0_3_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_6037-269_0_3_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_6037-269_0_3_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_6037-269_0_3_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_6037-269_0_3_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_6037-269_0_3_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_6037-269_0_3_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_6037-269_0_3_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_6037-269_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_6037-269_0_3_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_6037-269_0_3_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_6037-269_0_3_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_6037-269_0_3_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_6037-269_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_6037-269_0_3_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_6037-269_0_3_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_6037-269_0_3_node_55 | 0.4 | n |  | TRUE
56 | bus_LV_6037-269_0_3_node_54 | 0.4 | n |  | TRUE
57 | bus_LV_6037-269_0_3_node_56 | 0.4 | n |  | TRUE
58 | bus_MV_198_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6037-269_0_3_load_0 | 0 | 0.0052873 | 0.0013251 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6037-269_0_3_load_1 | 1 | 0.0049459 | 0.0012396 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6037-269_0_3_load_48 | 3 | 0.0045065 | 0.0011294 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6037-269_0_3_load_3 | 4 | 0.0042202 | 0.0010577 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6037-269_0_3_load_4 | 5 | 0.0049733 | 0.0012464 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6037-269_0_3_load_60 | 7 | 0.0069962 | 0.0017534 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6037-269_0_3_load_42 | 10 | 0.0023851 | 0.00059777 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6037-269_0_3_load_44 | 11 | 0.004232 | 0.0010607 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6037-269_0_3_load_41 | 12 | 0.0066983 | 0.0016787 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6037-269_0_3_load_8 | 13 | 0.002647 | 0.00066339 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6037-269_0_3_load_5 | 14 | 0.0077214 | 0.0019352 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6037-269_0_3_load_6 | 16 | 0.0062193 | 0.0015587 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6037-269_0_3_load_7 | 17 | 0.0041355 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6037-269_0_3_load_14 | 18 | 0.0051476 | 0.0012901 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6037-269_0_3_load_10 | 19 | 0.001483 | 0.00037167 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6037-269_0_3_load_13 | 20 | 0.0056004 | 0.0014036 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6037-269_0_3_load_18 | 21 | 0.003038 | 0.0007614 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6037-269_0_3_load_62 | 23 | 0.0024078 | 0.00060346 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6037-269_0_3_load_11 | 24 | 0.0026933 | 0.00067501 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6037-269_0_3_load_51 | 25 | 0.0023761 | 0.00059551 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6037-269_0_3_load_52 | 27 | 0.0030925 | 0.00077507 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6037-269_0_3_load_38 | 28 | 0.0049484 | 0.0012402 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6037-269_0_3_load_35 | 29 | 0.0026404 | 0.00066176 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6037-269_0_3_load_63 | 30 | 0.010691 | 0.0026795 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6037-269_0_3_load_28 | 31 | 0.0094643 | 0.002372 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6037-269_0_3_load_29 | 32 | 0.0067707 | 0.0016969 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6037-269_0_3_load_27 | 33 | 0.0051102 | 0.0012807 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6037-269_0_3_load_19 | 34 | 0.0038489 | 0.00096463 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6037-269_0_3_load_20 | 35 | 0.0028244 | 0.00070785 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6037-269_0_3_load_22 | 37 | 0.0039397 | 0.00098739 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6037-269_0_3_load_59 | 38 | 0.003535 | 0.00088595 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6037-269_0_3_load_23 | 39 | 0.0037209 | 0.00093254 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6037-269_0_3_load_24 | 40 | 0.0079262 | 0.0019865 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6037-269_0_3_load_49 | 41 | 0.00605 | 0.0015163 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6037-269_0_3_load_25 | 42 | 0.0040636 | 0.0010184 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6037-269_0_3_load_50 | 43 | 0.0034015 | 0.0008525 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6037-269_0_3_load_33 | 44 | 0.0045727 | 0.001146 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6037-269_0_3_load_31 | 45 | 0.0037425 | 0.00093796 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6037-269_0_3_load_30 | 46 | 0.0024894 | 0.0006239 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6037-269_0_3_load_32 | 47 | 0.0040386 | 0.0010122 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6037-269_0_3_load_34 | 48 | 0.0043586 | 0.0010924 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6037-269_0_3_load_39 | 50 | 0.0045928 | 0.0011511 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6037-269_0_3_load_40 | 51 | 0.0048914 | 0.0012259 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6037-269_0_3_load_46 | 52 | 0.0021723 | 0.00054444 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6037-269_0_3_load_47 | 53 | 0.0020045 | 0.00050237 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6037-269_0_3_load_53 | 54 | 0.0075191 | 0.0018845 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6037-269_0_3_load_55 | 55 | 0.0022073 | 0.0005532 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6037-269_0_3_load_54 | 56 | 0.0018003 | 0.0004512 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6037-269_0_3_load_56 | 57 | 0.0024253 | 0.00060784 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6037-269_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6037-269_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6037-269_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.065822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6037-269_0_3_line_3 | NAYY 4x150 SE | 1 | 4 | 0.0095854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6037-269_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.010627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6037-269_0_3_line_5 | NAYY 4x150 SE | 3 | 11 | 0.0018952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6037-269_0_3_line_6 | NAYY 4x150 SE | 4 | 13 | 0.036705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6037-269_0_3_line_7 | NAYY 4x150 SE | 5 | 14 | 0.024074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6037-269_0_3_line_8 | NAYY 4x150 SE | 6 | 7 | 0.025207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6037-269_0_3_line_9 | NAYY 4x150 SE | 6 | 8 | 0.028338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6037-269_0_3_line_10 | NAYY 4x150 SE | 6 | 9 | 0.029879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6037-269_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.010331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6037-269_0_3_line_12 | NAYY 4x150 SE | 9 | 18 | 0.018893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6037-269_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.0010094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6037-269_0_3_line_14 | NAYY 4x150 SE | 10 | 12 | 0.034322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6037-269_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.0037787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6037-269_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.043882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6037-269_0_3_line_17 | NAYY 4x150 SE | 15 | 25 | 0.011011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_6037-269_0_3_line_18 | NAYY 4x150 SE | 15 | 26 | 0.026071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6037-269_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.044556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6037-269_0_3_line_20 | NAYY 4x150 SE | 17 | 19 | 0.008438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6037-269_0_3_line_21 | NAYY 4x150 SE | 19 | 24 | 0.062994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6037-269_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.011329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6037-269_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.035236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6037-269_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.068725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6037-269_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.056257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6037-269_0_3_line_26 | NAYY 4x150 SE | 24 | 30 | 0.08936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6037-269_0_3_line_27 | NAYY 4x150 SE | 25 | 27 | 0.006753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_6037-269_0_3_line_28 | NAYY 4x150 SE | 26 | 28 | 0.018549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6037-269_0_3_line_29 | NAYY 4x150 SE | 26 | 29 | 0.0074334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6037-269_0_3_line_30 | NAYY 4x150 SE | 27 | 48 | 0.0072038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_6037-269_0_3_line_31 | NAYY 4x150 SE | 29 | 49 | 0.0092242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6037-269_0_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.022606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6037-269_0_3_line_33 | NAYY 4x150 SE | 31 | 33 | 0.02919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6037-269_0_3_line_34 | NAYY 4x150 SE | 32 | 44 | 0.017282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6037-269_0_3_line_35 | NAYY 4x150 SE | 33 | 40 | 0.018027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6037-269_0_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.038032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6037-269_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.033093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6037-269_0_3_line_38 | NAYY 4x150 SE | 35 | 37 | 0.017272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6037-269_0_3_line_39 | NAYY 4x150 SE | 35 | 38 | 0.06958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6037-269_0_3_line_40 | NAYY 4x150 SE | 36 | 39 | 0.011344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6037-269_0_3_line_41 | NAYY 4x150 SE | 36 | 40 | 0.044207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6037-269_0_3_line_42 | NAYY 4x150 SE | 37 | 41 | 0.024679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6037-269_0_3_line_43 | NAYY 4x150 SE | 39 | 42 | 0.049428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6037-269_0_3_line_44 | NAYY 4x150 SE | 41 | 43 | 0.03502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_6037-269_0_3_line_45 | NAYY 4x150 SE | 43 | 55 | 0.0023883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6037-269_0_3_line_46 | NAYY 4x150 SE | 44 | 45 | 0.0097699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6037-269_0_3_line_47 | NAYY 4x150 SE | 45 | 46 | 0.018864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_6037-269_0_3_line_48 | NAYY 4x150 SE | 46 | 47 | 0.03087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_6037-269_0_3_line_49 | NAYY 4x150 SE | 47 | 48 | 0.0052105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_6037-269_0_3_line_50 | NAYY 4x150 SE | 49 | 50 | 0.011551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6037-269_0_3_line_51 | NAYY 4x150 SE | 49 | 51 | 0.0065378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6037-269_0_3_line_52 | NAYY 4x150 SE | 51 | 52 | 0.010549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6037-269_0_3_line_53 | NAYY 4x150 SE | 52 | 53 | 0.0068316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6037-269_0_3_line_54 | NAYY 4x150 SE | 53 | 54 | 0.00023005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6037-269_0_3_line_55 | NAYY 4x150 SE | 55 | 56 | 0.026916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_6037-269_0_3_line_56 | NAYY 4x150 SE | 56 | 57 | 0.0089604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6037-269_0_3_trafo_31 | 0.25 MVA 20/0.4 kV | 58 | 45 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2573652.3249 | 1104358.1072 | 2573652.1058 | 1104350.9382 | 2573643.7974 | 1104332.3368
1 | 2573651.2586 | 1104369.5291 | 2573652.5839 | 1104366.5774 | 2573652.3249 | 1104358.1072
2 | 2573652.3249 | 1104358.1072 | 2573714.1487 | 1104335.5161
3 | 2573643.7974 | 1104332.3368 | 2573639.8883 | 1104323.5848
4 | 2573651.2586 | 1104369.5291 | 2573657.6199 | 1104378.0415
5 | 2573714.1487 | 1104335.5161 | 2573715.9249 | 1104334.8547
6 | 2573622.0386 | 1104291.9648 | 2573629.2898 | 1104299.8562 | 2573639.8883 | 1104323.5848
7 | 2573657.6199 | 1104378.0415 | 2573659.4977 | 1104380.5544 | 2573669.8066 | 1104398.7771
8 | 2573738.243 | 1104337.4124 | 2573736.4169 | 1104337.2536 | 2573734.3929 | 1104337.8182 | 2573732.558 | 1104339.1936 | 2573730.2742 | 1104342.2828 | 2573726.7588 | 1104348.5235 | 2573724.7102 | 1104352.3454 | 2573722.5108 | 1104355.2787
9 | 2573749.9351 | 1104311.7931 | 2573746.4161 | 1104317.2111 | 2573742.4643 | 1104324.5098 | 2573739.1557 | 1104333.8511 | 2573738.243 | 1104337.4124
10 | 2573733.9235 | 1104366.8683 | 2573734.1046 | 1104358.7079 | 2573735.616 | 1104348.7296 | 2573737.338 | 1104340.9626 | 2573738.243 | 1104337.4124
11 | 2573749.9351 | 1104311.7931 | 2573746.6405 | 1104310.1177 | 2573745.308 | 1104309.6232 | 2573743.0483 | 1104309.3551 | 2573740.3929 | 1104310.6117
12 | 2573733.9235 | 1104366.8683 | 2573738.2458 | 1104366.5383 | 2573749.7689 | 1104366.1659 | 2573752.7228 | 1104365.4944
13 | 2573715.9249 | 1104334.8547 | 2573716.8708 | 1104334.5025
14 | 2573740.3929 | 1104310.6117 | 2573740.3929 | 1104310.6117 | 2573737.877 | 1104313.6909 | 2573735.8665 | 1104317.3681 | 2573734.085 | 1104320.3551 | 2573731.2088 | 1104324.1696 | 2573727.635 | 1104327.6646 | 2573725.3016 | 1104330.0204 | 2573719.6161 | 1104333.4802 | 2573716.8708 | 1104334.5025
15 | 2573619.4819 | 1104289.1824 | 2573622.0386 | 1104291.9648
16 | 2573669.8066 | 1104398.7771 | 2573677.1137 | 1104411.6935 | 2573686.074 | 1104424.9502 | 2573691.9846 | 1104432.3727 | 2573694.6206 | 1104434.7546
17 | 2573619.4819 | 1104289.1824 | 2573620.7239 | 1104278.2412
18 | 2573595.0458 | 1104279.9065 | 2573619.4819 | 1104289.1824
19 | 2573694.6206 | 1104434.7546 | 2573703.1509 | 1104442.4626 | 2573712.7227 | 1104450.5029 | 2573724.7389 | 1104467.1836
20 | 2573729.6709 | 1104474.0301 | 2573724.7389 | 1104467.1836
21 | 2573729.6709 | 1104474.0301 | 2573786.8104 | 1104447.5099
22 | 2573799.7035 | 1104349.919 | 2573798.3775 | 1104358.0622 | 2573797.2125 | 1104360.9119
23 | 2573789.2667 | 1104392.1412 | 2573787.406 | 1104391.1265 | 2573786.0271 | 1104387.0637 | 2573786.4008 | 1104382.2819 | 2573787.9062 | 1104378.051 | 2573791.3204 | 1104371.6552 | 2573793.2237 | 1104368.2119 | 2573795.9283 | 1104364.0536 | 2573797.2125 | 1104360.9119
24 | 2573799.7035 | 1104349.919 | 2573867.9884 | 1104357.6831
25 | 2573789.2667 | 1104392.1412 | 2573787.5786 | 1104395.2723 | 2573786.0025 | 1104401.0265 | 2573784.7543 | 1104407.4907 | 2573784.5339 | 1104411.9606 | 2573784.87 | 1104416.3391 | 2573785.7732 | 1104421.2822 | 2573786.1083 | 1104425.4273 | 2573786.4261 | 1104429.1611 | 2573786.8104 | 1104447.5099
26 | 2573786.8104 | 1104447.5099 | 2573875.7095 | 1104456.5777
27 | 2573620.7239 | 1104278.2412 | 2573621.4856 | 1104271.5313 | 2573621.4856 | 1104271.5313
28 | 2573595.0458 | 1104279.9065 | 2573594.7955 | 1104281.0526 | 2573594.6157 | 1104282.3763 | 2573594.1644 | 1104283.5455 | 2573593.7294 | 1104284.8814 | 2573593.5988 | 1104285.0821 | 2573592.8246 | 1104286.6974 | 2573591.8409 | 1104288.1469 | 2573590.5114 | 1104290.1204 | 2573589.9436 | 1104291.1789 | 2573589.715 | 1104291.9581 | 2573589.6506 | 1104293.1479 | 2573589.5875 | 1104294.6378 | 2573589.2994 | 1104295.9731 | 2573588.9329 | 1104297.0752
29 | 2573595.0458 | 1104279.9065 | 2573588.0965 | 1104277.2679
30 | 2573621.4856 | 1104271.5313 | 2573628.5745 | 1104270.2496
31 | 2573579.4729 | 1104273.9937 | 2573588.0965 | 1104277.2679
32 | 2573722.2869 | 1104231.8509 | 2573708.8797 | 1104242.614 | 2573704.612 | 1104245.9445
33 | 2573743.7667 | 1104212.1385 | 2573730.516 | 1104225.2446 | 2573722.2869 | 1104231.8509
34 | 2573690.9878 | 1104256.5767 | 2573704.612 | 1104245.9445
35 | 2573756.3693 | 1104199.2525 | 2573756.3693 | 1104199.2525 | 2573750.949 | 1104205.0345 | 2573743.7667 | 1104212.1385
36 | 2573733.8855 | 1104164.1955 | 2573721.3603 | 1104163.4863 | 2573695.8742 | 1104163.6527 | 2573695.8742 | 1104163.6527
37 | 2573765.559 | 1104156.6021 | 2573757.2005 | 1104160.8628 | 2573744.6526 | 1104164.0299 | 2573734.4897 | 1104164.2297 | 2573733.8855 | 1104164.1955
38 | 2573679.4451 | 1104168.9824 | 2573695.8742 | 1104163.6527
39 | 2573695.8742 | 1104163.6527 | 2573671.2334 | 1104098.5824
40 | 2573765.559 | 1104156.6021 | 2573766.5537 | 1104152.3067 | 2573768.8092 | 1104145.7486
41 | 2573765.559 | 1104156.6021 | 2573764.3401 | 1104162.6883 | 2573763.2219 | 1104179.5128 | 2573760.2931 | 1104192.6321 | 2573756.3693 | 1104199.2525
42 | 2573679.4451 | 1104168.9824 | 2573679.4451 | 1104168.9824 | 2573666.7206 | 1104177.7534 | 2573660.1958 | 1104184.2736
43 | 2573768.8092 | 1104145.7486 | 2573777.1562 | 1104121.4785 | 2573778.3747 | 1104113.5025 | 2573778.5612 | 1104106.5759 | 2573777.8496 | 1104099.4532 | 2573777.6424 | 1104097.8597
44 | 2573660.1958 | 1104184.2736 | 2573654.0055 | 1104190.4596 | 2573636.9405 | 1104206.0307 | 2573634.09 | 1104207.4116
45 | 2573631.9407 | 1104208.4529 | 2573634.09 | 1104207.4116
46 | 2573681.924 | 1104260.2235 | 2573690.9878 | 1104256.5767 | 2573690.9878 | 1104256.5767
47 | 2573663.4418 | 1104263.0293 | 2573663.9361 | 1104263.0421 | 2573677.5526 | 1104261.9823 | 2573681.924 | 1104260.2235
48 | 2573663.4418 | 1104263.0293 | 2573653.315 | 1104262.766 | 2573647.8067 | 1104264.3019 | 2573643.1835 | 1104266.5898 | 2573633.6809 | 1104269.231
49 | 2573633.6809 | 1104269.231 | 2573632.7 | 1104269.5037 | 2573628.5745 | 1104270.2496
50 | 2573579.4729 | 1104273.9937 | 2573576.9549 | 1104273.0375 | 2573574.1599 | 1104272.405 | 2573571.3526 | 1104272.5062 | 2573568.3372 | 1104273.5255
51 | 2573579.4729 | 1104273.9937 | 2573582.7879 | 1104268.3586
52 | 2573582.7879 | 1104268.3586 | 2573586.2064 | 1104262.5474 | 2573586.3334 | 1104258.7424
53 | 2573586.5612 | 1104251.9146 | 2573586.3334 | 1104258.7424
54 | 2573586.5689 | 1104251.6847 | 2573586.5612 | 1104251.9146
55 | 2573606.5375 | 1104216.6991 | 2573617.0001 | 1104214.9666 | 2573624.7373 | 1104211.9425 | 2573631.9407 | 1104208.4529
56 | 2573606.5375 | 1104216.6991 | 2573604.7955 | 1104216.9876 | 2573597.601 | 1104216.9456

## bus_geodata
| x | y | coords
0 | 2573652.3249 | 1104358.1072
1 | 2573643.7974 | 1104332.3368
2 | 2573651.2586 | 1104369.5291
3 | 2573714.1487 | 1104335.5161
4 | 2573639.8883 | 1104323.5848
5 | 2573657.6199 | 1104378.0415
6 | 2573738.243 | 1104337.4124
7 | 2573722.5108 | 1104355.2787
8 | 2573749.9351 | 1104311.7931
9 | 2573733.9235 | 1104366.8683
10 | 2573716.8708 | 1104334.5025
11 | 2573715.9249 | 1104334.8547
12 | 2573740.3929 | 1104310.6117
13 | 2573622.0386 | 1104291.9648
14 | 2573669.8066 | 1104398.7771
15 | 2573619.4819 | 1104289.1824
16 | 2573694.6206 | 1104434.7546
17 | 2573724.7389 | 1104467.1836
18 | 2573752.7228 | 1104365.4944
19 | 2573729.6709 | 1104474.0301
20 | 2573797.2125 | 1104360.9119
21 | 2573799.7035 | 1104349.919
22 | 2573789.2667 | 1104392.1412
23 | 2573867.9884 | 1104357.6831
24 | 2573786.8104 | 1104447.5099
25 | 2573620.7239 | 1104278.2412
26 | 2573595.0458 | 1104279.9065
27 | 2573621.4856 | 1104271.5313
28 | 2573588.9329 | 1104297.0752
29 | 2573588.0965 | 1104277.2679
30 | 2573875.7095 | 1104456.5777
31 | 2573722.2869 | 1104231.8509
32 | 2573704.612 | 1104245.9445
33 | 2573743.7667 | 1104212.1385
34 | 2573733.8855 | 1104164.1955
35 | 2573695.8742 | 1104163.6527
36 | 2573765.559 | 1104156.6021
37 | 2573679.4451 | 1104168.9824
38 | 2573671.2334 | 1104098.5824
39 | 2573768.8092 | 1104145.7486
40 | 2573756.3693 | 1104199.2525
41 | 2573660.1958 | 1104184.2736
42 | 2573777.6424 | 1104097.8597
43 | 2573634.09 | 1104207.4116
44 | 2573690.9878 | 1104256.5767
45 | 2573681.924 | 1104260.2235
46 | 2573663.4418 | 1104263.0293
47 | 2573633.6809 | 1104269.231
48 | 2573628.5745 | 1104270.2496
49 | 2573579.4729 | 1104273.9937
50 | 2573568.3372 | 1104273.5255
51 | 2573582.7879 | 1104268.3586
52 | 2573586.3334 | 1104258.7424
53 | 2573586.5612 | 1104251.9146
54 | 2573586.5689 | 1104251.6847
55 | 2573631.9407 | 1104208.4529
56 | 2573606.5375 | 1104216.6991
57 | 2573597.601 | 1104216.9456
58 | 2573619.4819 | 1104289.1824

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1