## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6083-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6083-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6083-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6083-15_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6083-15_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6083-15_0_4_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_6083-15_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_6083-15_0_4_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_6083-15_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_6083-15_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_6083-15_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_6083-15_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_6083-15_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_6083-15_0_4_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_6083-15_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_6083-15_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_6083-15_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_6083-15_0_4_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_6083-15_0_4_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_6083-15_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_6083-15_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_6083-15_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_6083-15_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_6083-15_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_6083-15_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_6083-15_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_6083-15_0_4_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_6083-15_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_6083-15_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_6083-15_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_6083-15_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_6083-15_0_4_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_6083-15_0_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_6083-15_0_4_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_6083-15_0_4_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_6083-15_0_4_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_6083-15_0_4_node_68 | 0.4 | n |  | TRUE
37 | bus_LV_6083-15_0_4_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_6083-15_0_4_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_6083-15_0_4_node_75 | 0.4 | n |  | TRUE
40 | bus_LV_6083-15_0_4_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_6083-15_0_4_node_73 | 0.4 | n |  | TRUE
42 | bus_LV_6083-15_0_4_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_6083-15_0_4_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_6083-15_0_4_node_55 | 0.4 | n |  | TRUE
45 | bus_LV_6083-15_0_4_node_57 | 0.4 | n |  | TRUE
46 | bus_LV_6083-15_0_4_node_71 | 0.4 | n |  | TRUE
47 | bus_LV_6083-15_0_4_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_6083-15_0_4_node_63 | 0.4 | n |  | TRUE
49 | bus_LV_6083-15_0_4_node_64 | 0.4 | n |  | TRUE
50 | bus_LV_6083-15_0_4_node_65 | 0.4 | n |  | TRUE
51 | bus_LV_6083-15_0_4_node_66 | 0.4 | n |  | TRUE
52 | bus_LV_6083-15_0_4_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_6083-15_0_4_node_70 | 0.4 | n |  | TRUE
54 | bus_MV_202_0_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6083-15_0_4_load_0 | 0 | 0.001611 | 0.00040375 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6083-15_0_4_load_1 | 1 | 0.00077011 | 0.00019301 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6083-15_0_4_load_2 | 2 | 0.0016436 | 0.00041193 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6083-15_0_4_load_3 | 3 | 0.0010122 | 0.00025369 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6083-15_0_4_load_4 | 4 | 0.0014085 | 0.00035301 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6083-15_0_4_load_27 | 5 | 0.0010394 | 0.00026051 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6083-15_0_4_load_15 | 6 | 0.0011402 | 0.00028576 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6083-15_0_4_load_5 | 9 | 0.00089173 | 0.00022349 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6083-15_0_4_load_6 | 10 | 0.00079339 | 0.00019884 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6083-15_0_4_load_7 | 11 | 0.0010361 | 0.00025967 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6083-15_0_4_load_8 | 12 | 0.00069506 | 0.0001742 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6083-15_0_4_load_26 | 13 | 0.0018042 | 0.00045218 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6083-15_0_4_load_24 | 15 | 0.00076182 | 0.00019093 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6083-15_0_4_load_28 | 17 | 0.00088974 | 0.00022299 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6083-15_0_4_load_29 | 18 | 0.0024426 | 0.00061217 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6083-15_0_4_load_10 | 19 | 0.003032 | 0.00075989 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6083-15_0_4_load_11 | 20 | 0.0030251 | 0.00075817 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6083-15_0_4_load_12 | 21 | 0.0025515 | 0.00063947 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6083-15_0_4_load_13 | 22 | 0.0022661 | 0.00056793 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6083-15_0_4_load_14 | 23 | 0.0040399 | 0.0010125 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6083-15_0_4_load_21 | 24 | 0.0035129 | 0.00088041 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6083-15_0_4_load_22 | 25 | 0.00097409 | 0.00024413 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6083-15_0_4_load_30 | 26 | 0.0010535 | 0.00026404 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6083-15_0_4_load_23 | 27 | 0.00076402 | 0.00019148 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6083-15_0_4_load_25 | 28 | 0.0014681 | 0.00036793 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6083-15_0_4_load_38 | 29 | 0.0028305 | 0.00070939 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6083-15_0_4_load_39 | 30 | 0.0023676 | 0.00059337 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6083-15_0_4_load_41 | 31 | 0.0025534 | 0.00063994 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6083-15_0_4_load_58 | 34 | 0.0047546 | 0.0011916 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6083-15_0_4_load_68 | 36 | 0.0051996 | 0.0013031 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6083-15_0_4_load_59 | 38 | 0.0042697 | 0.0010701 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6083-15_0_4_load_75 | 39 | 0.005002 | 0.0012536 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6083-15_0_4_load_56 | 40 | 0.0034352 | 0.00086093 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6083-15_0_4_load_73 | 41 | 0.0038629 | 0.00096814 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6083-15_0_4_load_54 | 43 | 0.0025317 | 0.0006345 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6083-15_0_4_load_55 | 44 | 0.0023812 | 0.00059678 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6083-15_0_4_load_57 | 45 | 0.0045741 | 0.0011464 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6083-15_0_4_load_71 | 46 | 0.0034976 | 0.00087658 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6083-15_0_4_load_69 | 47 | 0.0035563 | 0.00089128 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6083-15_0_4_load_63 | 48 | 0.0037396 | 0.00093722 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6083-15_0_4_load_64 | 49 | 0.0036268 | 0.00090896 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6083-15_0_4_load_65 | 50 | 0.0057679 | 0.0014456 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6083-15_0_4_load_66 | 51 | 0.0052422 | 0.0013138 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6083-15_0_4_load_70 | 53 | 0.0038481 | 0.00096441 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6083-15_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6083-15_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.010509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6083-15_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6083-15_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.047879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6083-15_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.046912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6083-15_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.011294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6083-15_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.66097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_6083-15_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.025303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6083-15_0_4_line_8 | NAYY 4x150 SE | 7 | 39 | 0.13409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6083-15_0_4_line_9 | NAYY 4x150 SE | 7 | 37 | 0.15827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6083-15_0_4_line_10 | NAYY 4x150 SE | 8 | 14 | 0.067918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6083-15_0_4_line_11 | NAYY 4x150 SE | 8 | 11 | 0.099448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6083-15_0_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.00028723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6083-15_0_4_line_13 | NAYY 4x150 SE | 9 | 11 | 0.0086827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6083-15_0_4_line_14 | NAYY 4x150 SE | 10 | 12 | 0.026876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6083-15_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.01251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6083-15_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0010782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6083-15_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.38406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6083-15_0_4_line_18 | NAYY 4x150 SE | 14 | 17 | 0.18017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6083-15_0_4_line_19 | NAYY 4x150 SE | 15 | 28 | 0.01122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6083-15_0_4_line_20 | NAYY 4x150 SE | 16 | 18 | 0.43237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6083-15_0_4_line_21 | NAYY 4x150 SE | 18 | 26 | 0.030965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6083-15_0_4_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0057982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6083-15_0_4_line_23 | NAYY 4x150 SE | 19 | 21 | 0.0046971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6083-15_0_4_line_24 | NAYY 4x150 SE | 20 | 22 | 0.0024464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6083-15_0_4_line_25 | NAYY 4x150 SE | 21 | 23 | 0.0082569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6083-15_0_4_line_26 | NAYY 4x150 SE | 22 | 24 | 0.010709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6083-15_0_4_line_27 | NAYY 4x150 SE | 24 | 25 | 0.01592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6083-15_0_4_line_28 | NAYY 4x150 SE | 25 | 27 | 0.023869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6083-15_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.010117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6083-15_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.22817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6083-15_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.015251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6083-15_0_4_line_32 | NAYY 4x150 SE | 31 | 32 | 0.28225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6083-15_0_4_line_33 | NAYY 4x150 SE | 32 | 33 | 0.22799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6083-15_0_4_line_34 | NAYY 4x150 SE | 33 | 34 | 0.021369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6083-15_0_4_line_35 | NAYY 4x150 SE | 34 | 40 | 0.0090692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6083-15_0_4_line_36 | NAYY 4x150 SE | 35 | 36 | 0.010513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6083-15_0_4_line_37 | NAYY 4x150 SE | 35 | 37 | 0.064189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6083-15_0_4_line_38 | NAYY 4x150 SE | 36 | 47 | 0.00905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6083-15_0_4_line_39 | NAYY 4x150 SE | 37 | 38 | 0.0090361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6083-15_0_4_line_40 | NAYY 4x150 SE | 38 | 45 | 0.064466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6083-15_0_4_line_41 | NAYY 4x150 SE | 40 | 43 | 0.010061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6083-15_0_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.009641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6083-15_0_4_line_43 | NAYY 4x150 SE | 42 | 46 | 0.008387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6083-15_0_4_line_44 | NAYY 4x150 SE | 42 | 52 | 0.018843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_6083-15_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.008279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6083-15_0_4_line_46 | NAYY 4x150 SE | 44 | 45 | 0.0067995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6083-15_0_4_line_47 | NAYY 4x150 SE | 47 | 53 | 0.0080174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_6083-15_0_4_line_48 | NAYY 4x150 SE | 48 | 49 | 0.019434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_6083-15_0_4_line_49 | NAYY 4x150 SE | 48 | 50 | 0.028898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_6083-15_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.054068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6083-15_0_4_line_51 | NAYY 4x150 SE | 51 | 52 | 0.064148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6083-15_0_4_line_52 | NAYY 4x150 SE | 52 | 53 | 0.0062965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6083-15_0_4_trafo_62 | 0.25 MVA 20/0.4 kV | 54 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28
0 | 2603006.3262 | 1106930.5595 | 2603009.7214 | 1106928.3601 | 2603015.0262 | 1106926.0282 | 2603018.2501 | 1106926.0631 | 2603021.171 | 1106929.2216 | 2603024.8972 | 1106929.7459 | 2603027.4948 | 1106930.0918 | 2603027.4948 | 1106930.0918
1 | 2603006.3262 | 1106930.5595 | 2603006.3262 | 1106930.5595 | 2602999.8632 | 1106929.8894 | 2602996.0659 | 1106931.1826
2 | 2603027.4948 | 1106930.0918 | 2603028.7323 | 1106929.192 | 2603031.1455 | 1106926.9142 | 2603039.5893 | 1106924.5728 | 2603041.7643 | 1106922.3886
3 | 2602996.0659 | 1106931.1826 | 2602987.6071 | 1106934.0634 | 2602966.9787 | 1106936.6881 | 2602955.0111 | 1106935.7153 | 2602949.3867 | 1106933.2494
4 | 2603041.7643 | 1106922.3886 | 2603046.1951 | 1106917.9394 | 2603050.3509 | 1106909.6039 | 2603053.2375 | 1106903.9025 | 2603053.8876 | 1106902.5577 | 2603055.3873 | 1106902.803 | 2603056.9558 | 1106904.9049 | 2603058.9026 | 1106907.8851 | 2603069.8557 | 1106912.4261 | 2603073.3394 | 1106914.1242
5 | 2602949.3867 | 1106933.2494 | 2602946.9645 | 1106932.1875 | 2602942.621 | 1106929.0616 | 2602940.7243 | 1106926.3638
6 | 2602949.3867 | 1106933.2494 | 2602976.7685 | 1107593.6521
7 | 2602926.172 | 1106905.6645 | 2602940.7243 | 1106926.3638
8 | 2602976.7685 | 1107593.6521 | 2602976.2975 | 1107624.8895 | 2602977.2994 | 1107631.1931 | 2602982.2738 | 1107639.4663 | 2602985.3776 | 1107647.5273 | 2602987.8618 | 1107657.8559 | 2602989.9267 | 1107671.9083 | 2602989.9221 | 1107681.6242 | 2602989.0895 | 1107692.7849 | 2602985.3451 | 1107715.1053 | 2602982.233 | 1107724.3973
9 | 2602976.7685 | 1107593.6521 | 2602995.3114 | 1107598.8636 | 2603003.3036 | 1107601.113 | 2603015.9257 | 1107604.6875 | 2603034.7467 | 1107610.0327 | 2603037.0887 | 1107610.6897 | 2603057.88 | 1107618.1036 | 2603062.4556 | 1107619.6177 | 2603087.5522 | 1107628.0677 | 2603089.9435 | 1107638.2406 | 2603096.7799 | 1107648.3712 | 2603100.5093 | 1107657.044 | 2603108.1436 | 1107663.6623
10 | 2602909.0043 | 1106848.4836 | 2602914.4592 | 1106855.8342 | 2602929.0521 | 1106864.3675 | 2602930.8656 | 1106871.3941 | 2602930.3429 | 1106881.51 | 2602926.172 | 1106905.6645
11 | 2602926.172 | 1106905.6645 | 2602941.4949 | 1106890.7421 | 2602959.1996 | 1106874.6647 | 2602987.4351 | 1106857.692 | 2603006.3918 | 1106848.2002
12 | 2603014.4759 | 1106844.3141 | 2603014.2165 | 1106844.4374
13 | 2603014.2165 | 1106844.4374 | 2603008.1293 | 1106847.3302 | 2603006.3918 | 1106848.2002
14 | 2603014.4759 | 1106844.3141 | 2603025.3048 | 1106839.1678 | 2603035.8452 | 1106834.1149 | 2603038.0219 | 1106831.7732
15 | 2603038.0219 | 1106831.7732 | 2603046.539 | 1106822.6106
16 | 2603046.539 | 1106822.6106 | 2603047.273 | 1106821.8209
17 | 2602550.0763 | 1106954.7345 | 2602553.0996 | 1106953.7797 | 2602572.7271 | 1106940.3923 | 2602595.9706 | 1106932.7314 | 2602630.2705 | 1106923.608 | 2602668.7271 | 1106903.2698 | 2602706.6445 | 1106896.694 | 2602738.5799 | 1106903.0889 | 2602763.5047 | 1106905.301 | 2602776.1462 | 1106903.628 | 2602789.1783 | 1106892.9285 | 2602848.7958 | 1106873.8794 | 2602878.4907 | 1106860.1641 | 2602909.0043 | 1106848.4836
18 | 2602909.0043 | 1106848.4836 | 2602953.2452 | 1106828.4167 | 2602991.4658 | 1106803.9339 | 2603007.5303 | 1106791.0353 | 2603029.5691 | 1106782.8086 | 2603051.9734 | 1106770.2689 | 2603068.3341 | 1106769.1433
19 | 2603054.7639 | 1106813.4723 | 2603052.113 | 1106816.6142 | 2603047.273 | 1106821.8209
20 | 2602550.0763 | 1106954.7345 | 2602548.5003 | 1106951.7435 | 2602548.6873 | 1106948.353 | 2602556.4136 | 1106941.6529 | 2602564.8819 | 1106935.52 | 2602574.7275 | 1106926.4417 | 2602584.301 | 1106921.3098 | 2602618.6206 | 1106902.3481 | 2602633.8946 | 1106891.6269 | 2602644.2908 | 1106879.2474 | 2602650.2776 | 1106872.7467 | 2602666.7406 | 1106865.9615 | 2602677.7843 | 1106858.3625 | 2602686.8973 | 1106845.8046 | 2602700.2367 | 1106839.7518 | 2602714.4104 | 1106835.089 | 2602719.7461 | 1106832.7902 | 2602744.4865 | 1106833.1679 | 2602754.0598 | 1106829.2368 | 2602763.4427 | 1106818.6913 | 2602775.6906 | 1106798.4312 | 2602781.5803 | 1106784.9604 | 2602789.2233 | 1106775.3368 | 2602802.3781 | 1106767.6389 | 2602813.1496 | 1106764.3422 | 2602841.6718 | 1106746.0127 | 2602863.577 | 1106725.5793 | 2602876.736 | 1106709.1661 | 2602879.207 | 1106705.5325
21 | 2602896.6198 | 1106679.9275 | 2602879.207 | 1106705.5325
22 | 2603109.1214 | 1106772.2002 | 2603104.1418 | 1106775.1706
23 | 2603109.1214 | 1106772.2002 | 2603113.1553 | 1106769.7939
24 | 2603104.1418 | 1106775.1706 | 2603102.0408 | 1106776.4239
25 | 2603113.1553 | 1106769.7939 | 2603120.2464 | 1106765.564
26 | 2603092.8439 | 1106781.91 | 2603102.0408 | 1106776.4239
27 | 2603079.4148 | 1106790.4587 | 2603091.8078 | 1106782.528 | 2603092.8439 | 1106781.91
28 | 2603061.2881 | 1106805.7397 | 2603065.7825 | 1106800.4129 | 2603073.981 | 1106793.9359 | 2603079.4148 | 1106790.4587
29 | 2603054.7639 | 1106813.4723 | 2603061.2881 | 1106805.7397
30 | 2602714.9517 | 1107819.586 | 2602732.1096 | 1107816.7281 | 2602751.7076 | 1107812.1901 | 2602774.5143 | 1107806.2083 | 2602776.387 | 1107801.7625 | 2602776.4897 | 1107796.9046 | 2602776.3899 | 1107795.2482 | 2602779.1883 | 1107795.2494 | 2602781.0502 | 1107797.5292 | 2602780.9473 | 1107803.1097 | 2602789.0307 | 1107808.2825 | 2602792.4574 | 1107803.3261 | 2602794.5356 | 1107788.8531 | 2602795.9897 | 1107786.9973 | 2602798.9885 | 1107788.2326 | 2602802.5099 | 1107796.0937 | 2602802.5071 | 1107802.2967 | 2602806.343 | 1107815.7273 | 2602814.3196 | 1107817.6986 | 2602810.4704 | 1107850.9689 | 2602813.377 | 1107850.9702 | 2602844.5836 | 1107834.7559
31 | 2602844.5836 | 1107834.7559 | 2602851.5343 | 1107831.1444 | 2602858.2466 | 1107827.9873
32 | 2602882.2534 | 1107765.5928 | 2602893.2282 | 1107786.8862 | 2602929.9028 | 1107847.2444 | 2602935.6977 | 1107869.3692 | 2602943.5701 | 1107879.0778 | 2602959.319 | 1107889.6349 | 2602958.0735 | 1107891.4908 | 2602954.5482 | 1107892.3117 | 2602931.7484 | 1107884.0413 | 2602920.7593 | 1107877.4217 | 2602906.6802 | 1107849.9237 | 2602877.2478 | 1107824.6975 | 2602870.199 | 1107822.2153 | 2602862.9387 | 1107825.7803 | 2602858.2466 | 1107827.9873
33 | 2602882.2534 | 1107765.5928 | 2602878.934 | 1107755.6752 | 2602880.3891 | 1107751.7406 | 2602885.163 | 1107742.4493 | 2602890.5541 | 1107735.8374 | 2602900.0945 | 1107733.1516 | 2602917.0981 | 1107739.5628 | 2602940.1055 | 1107751.5685 | 2602974.9562 | 1107778.1315 | 2602983.5266 | 1107783.216 | 2603000.1141 | 1107786.5367 | 2603018.3586 | 1107784.0665 | 2603036.6133 | 1107776.6384 | 2603054.0319 | 1107771.6778 | 2603066.4723 | 1107766.726
34 | 2603066.4723 | 1107766.726 | 2603079.7047 | 1107770.3899 | 2603087.1421 | 1107768.6483 | 2603087.1421 | 1107768.6483
35 | 2603088.7795 | 1107759.7281 | 2603087.1421 | 1107768.6483
36 | 2603148.6997 | 1107628.1762 | 2603156.3766 | 1107635.3587
37 | 2603108.1436 | 1107663.6623 | 2603115.5237 | 1107653.0274 | 2603117.2581 | 1107647.6033 | 2603117.9223 | 1107633.3299 | 2603123.9989 | 1107632.4992 | 2603141.0772 | 1107628.7615 | 2603148.6997 | 1107628.1762
38 | 2603156.3766 | 1107635.3587 | 2603161.4797 | 1107640.1331 | 2603163.3549 | 1107640.9898
39 | 2603108.1436 | 1107663.6623 | 2603105.5519 | 1107672.3187
40 | 2603096.1439 | 1107735.7757 | 2603097.4114 | 1107730.5234 | 2603100.0772 | 1107717.2515 | 2603100.7447 | 1107711.8714 | 2603101.1489 | 1107692.084 | 2603101.6848 | 1107686.9372 | 2603102.5762 | 1107682.2576 | 2603105.5519 | 1107672.3187
41 | 2603091.4481 | 1107750.0607 | 2603089.607 | 1107755.2206 | 2603088.7795 | 1107759.7281
42 | 2603190.7352 | 1107633.2447 | 2603198.4196 | 1107627.4225
43 | 2603190.7352 | 1107633.2447 | 2603182.4085 | 1107632.2407
44 | 2603190.7352 | 1107633.2447 | 2603189.0554 | 1107637.6682 | 2603180.758 | 1107642.8332 | 2603177.023 | 1107645.0991
45 | 2603091.4481 | 1107750.0607 | 2603092.1847 | 1107747.9961 | 2603094.5313 | 1107742.3797
46 | 2603096.1439 | 1107735.7757 | 2603094.5762 | 1107742.2722 | 2603094.5313 | 1107742.3797
47 | 2603163.3549 | 1107640.9898 | 2603166.4492 | 1107642.4034 | 2603170.9217 | 1107643.5436
48 | 2603141.7177 | 1107768.4645 | 2603143.9971 | 1107770.3332 | 2603146.8956 | 1107771.1573 | 2603150.6303 | 1107769.0915 | 2603152.2933 | 1107767.2359 | 2603154.2109 | 1107760.8019
49 | 2603142.9767 | 1107739.951 | 2603140.6766 | 1107763.5059 | 2603140.675 | 1107766.6075 | 2603141.7177 | 1107768.4645
50 | 2603154.2109 | 1107760.8019 | 2603161.841 | 1107735.2026 | 2603162.2613 | 1107729.6223 | 2603163.5115 | 1107718.4619 | 2603165.768 | 1107708.1768
51 | 2603177.023 | 1107645.0991 | 2603175.1539 | 1107657.0818 | 2603174.7328 | 1107664.1184 | 2603172.0347 | 1107679.6136 | 2603165.768 | 1107708.1768
52 | 2603177.023 | 1107645.0991 | 2603170.9217 | 1107643.5436

## bus_geodata
| x | y | coords
0 | 2603006.3262 | 1106930.5595
1 | 2603027.4948 | 1106930.0918
2 | 2602996.0659 | 1106931.1826
3 | 2603041.7643 | 1106922.3886
4 | 2602949.3867 | 1106933.2494
5 | 2603073.3394 | 1106914.1242
6 | 2602940.7243 | 1106926.3638
7 | 2602976.7685 | 1107593.6521
8 | 2602926.172 | 1106905.6645
9 | 2603014.2165 | 1106844.4374
10 | 2603014.4759 | 1106844.3141
11 | 2603006.3918 | 1106848.2002
12 | 2603038.0219 | 1106831.7732
13 | 2603046.539 | 1106822.6106
14 | 2602909.0043 | 1106848.4836
15 | 2603047.273 | 1106821.8209
16 | 2602550.0763 | 1106954.7345
17 | 2603068.3341 | 1106769.1433
18 | 2602879.207 | 1106705.5325
19 | 2603109.1214 | 1106772.2002
20 | 2603104.1418 | 1106775.1706
21 | 2603113.1553 | 1106769.7939
22 | 2603102.0408 | 1106776.4239
23 | 2603120.2464 | 1106765.564
24 | 2603092.8439 | 1106781.91
25 | 2603079.4148 | 1106790.4587
26 | 2602896.6198 | 1106679.9274
27 | 2603061.2881 | 1106805.7397
28 | 2603054.7639 | 1106813.4723
29 | 2602714.9517 | 1107819.586
30 | 2602844.5836 | 1107834.7559
31 | 2602858.2466 | 1107827.9873
32 | 2602882.2534 | 1107765.5928
33 | 2603066.4723 | 1107766.726
34 | 2603087.1421 | 1107768.6483
35 | 2603148.6997 | 1107628.1762
36 | 2603156.3766 | 1107635.3587
37 | 2603108.1436 | 1107663.6623
38 | 2603105.5519 | 1107672.3187
39 | 2602982.233 | 1107724.3973
40 | 2603088.7795 | 1107759.7281
41 | 2603198.4196 | 1107627.4225
42 | 2603190.7351 | 1107633.2447
43 | 2603091.4481 | 1107750.0607
44 | 2603094.5313 | 1107742.3797
45 | 2603096.1439 | 1107735.7757
46 | 2603182.4085 | 1107632.2407
47 | 2603163.3549 | 1107640.9898
48 | 2603141.7177 | 1107768.4645
49 | 2603154.2109 | 1107760.8019
50 | 2603142.9767 | 1107739.951
51 | 2603165.768 | 1107708.1768
52 | 2603177.0231 | 1107645.0991
53 | 2603170.9217 | 1107643.5436
54 | 2602995.3114 | 1107598.8636

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1