## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6109-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6109-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6109-3_0_5_node_30 | 0.4 | n |  | TRUE
3 | bus_LV_6109-3_0_5_node_39 | 0.4 | n |  | TRUE
4 | bus_LV_6109-3_0_5_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_6109-3_0_5_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_6109-3_0_5_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_6109-3_0_5_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_6109-3_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_6109-3_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6109-3_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_6109-3_0_5_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_6109-3_0_5_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6109-3_0_5_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_6109-3_0_5_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_6109-3_0_5_node_43 | 0.4 | n |  | TRUE
16 | bus_LV_6109-3_0_5_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_6109-3_0_5_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_6109-3_0_5_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_6109-3_0_5_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_6109-3_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_6109-3_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_6109-3_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_6109-3_0_5_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_6109-3_0_5_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_6109-3_0_5_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_6109-3_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_6109-3_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_6109-3_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6109-3_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_6109-3_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_6109-3_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_6109-3_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_6109-3_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_6109-3_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_6109-3_0_5_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_6109-3_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_6109-3_0_5_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6109-3_0_5_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_6109-3_0_5_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_6109-3_0_5_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_6109-3_0_5_node_42 | 0.4 | n |  | TRUE
42 | bus_MV_99_0_node_51 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6109-3_0_5_load_0 | 0 | 0.0038656 | 0.0009688 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6109-3_0_5_load_30 | 2 | 0.001982 | 0.00049674 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6109-3_0_5_load_39 | 3 | 0.0069506 | 0.001742 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6109-3_0_5_load_29 | 4 | 0.0032773 | 0.00082136 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6109-3_0_5_load_40 | 5 | 0.0040377 | 0.0010119 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6109-3_0_5_load_2 | 6 | 0.0070276 | 0.0017613 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6109-3_0_5_load_3 | 7 | 0.0032098 | 0.00080446 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6109-3_0_5_load_43 | 15 | 0.0045453 | 0.0011392 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6109-3_0_5_load_37 | 16 | 0.0050779 | 0.0012726 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6109-3_0_5_load_33 | 18 | 0.0043025 | 0.0010783 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6109-3_0_5_load_13 | 19 | 0.0037334 | 0.00093568 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6109-3_0_5_load_10 | 20 | 0.0039553 | 0.0009913 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6109-3_0_5_load_14 | 21 | 0.0021589 | 0.00054107 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6109-3_0_5_load_11 | 22 | 0.0016827 | 0.00042172 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6109-3_0_5_load_26 | 23 | 0.0061416 | 0.0015392 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6109-3_0_5_load_31 | 24 | 0.0068843 | 0.0017254 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6109-3_0_5_load_34 | 25 | 0.0047286 | 0.0011851 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6109-3_0_5_load_15 | 26 | 0.0017003 | 0.00042612 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6109-3_0_5_load_22 | 27 | 0.0027813 | 0.00069705 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6109-3_0_5_load_16 | 28 | 0.0023018 | 0.00057688 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6109-3_0_5_load_23 | 29 | 0.0030833 | 0.00077275 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6109-3_0_5_load_17 | 30 | 0.0036982 | 0.00092686 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6109-3_0_5_load_18 | 31 | 0.0017047 | 0.00042724 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6109-3_0_5_load_19 | 32 | 0.003862 | 0.0009679 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6109-3_0_5_load_20 | 33 | 0.0018457 | 0.00046256 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6109-3_0_5_load_21 | 34 | 0.0051929 | 0.0013015 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6109-3_0_5_load_24 | 35 | 0.004253 | 0.0010659 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6109-3_0_5_load_25 | 36 | 0.0098887 | 0.0024783 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6109-3_0_5_load_27 | 37 | 0.0054176 | 0.0013578 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6109-3_0_5_load_35 | 38 | 0.0045632 | 0.0011436 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6109-3_0_5_load_36 | 39 | 0.014716 | 0.0036881 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6109-3_0_5_load_42 | 41 | 0.010421 | 0.0026117 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6109-3_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.13541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6109-3_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.26861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6109-3_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.23818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6109-3_0_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.15178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_6109-3_0_5_line_4 | NAYY 4x150 SE | 3 | 5 | 0.081407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6109-3_0_5_line_5 | NAYY 4x150 SE | 4 | 14 | 0.053919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_6109-3_0_5_line_6 | NAYY 4x150 SE | 5 | 40 | 0.016853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6109-3_0_5_line_7 | NAYY 4x150 SE | 6 | 7 | 0.024305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6109-3_0_5_line_8 | NAYY 4x150 SE | 7 | 8 | 0.078191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6109-3_0_5_line_9 | NAYY 4x150 SE | 8 | 9 | 0.15928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6109-3_0_5_line_10 | NAYY 4x150 SE | 8 | 10 | 0.23603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_6109-3_0_5_line_11 | NAYY 4x150 SE | 8 | 11 | 0.13714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_6109-3_0_5_line_12 | NAYY 4x150 SE | 9 | 16 | 0.1111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6109-3_0_5_line_13 | NAYY 4x150 SE | 10 | 17 | 0.052068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6109-3_0_5_line_14 | NAYY 4x150 SE | 10 | 18 | 0.058567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6109-3_0_5_line_15 | NAYY 4x150 SE | 11 | 19 | 0.036187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6109-3_0_5_line_16 | NAYY 4x150 SE | 11 | 20 | 0.058992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_6109-3_0_5_line_17 | NAYY 4x150 SE | 12 | 13 | 0.090254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_6109-3_0_5_line_18 | NAYY 4x150 SE | 12 | 14 | 0.038466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_6109-3_0_5_line_19 | NAYY 4x150 SE | 12 | 15 | 0.014865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6109-3_0_5_line_20 | NAYY 4x150 SE | 13 | 21 | 0.010376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6109-3_0_5_line_21 | NAYY 4x150 SE | 13 | 22 | 0.031479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_6109-3_0_5_line_22 | NAYY 4x150 SE | 14 | 23 | 0.037703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6109-3_0_5_line_23 | NAYY 4x150 SE | 17 | 24 | 0.066609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6109-3_0_5_line_24 | NAYY 4x150 SE | 18 | 25 | 0.012352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6109-3_0_5_line_25 | NAYY 4x150 SE | 19 | 26 | 0.0011086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6109-3_0_5_line_26 | NAYY 4x150 SE | 20 | 22 | 0.0063986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_6109-3_0_5_line_27 | NAYY 4x150 SE | 21 | 27 | 0.009605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6109-3_0_5_line_28 | NAYY 4x150 SE | 23 | 37 | 0.045692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6109-3_0_5_line_29 | NAYY 4x150 SE | 25 | 38 | 0.0012116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6109-3_0_5_line_30 | NAYY 4x150 SE | 26 | 28 | 0.011785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6109-3_0_5_line_31 | NAYY 4x150 SE | 27 | 29 | 0.0056693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6109-3_0_5_line_32 | NAYY 4x150 SE | 28 | 30 | 0.0067266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6109-3_0_5_line_33 | NAYY 4x150 SE | 29 | 35 | 0.004224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6109-3_0_5_line_34 | NAYY 4x150 SE | 30 | 31 | 0.007651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6109-3_0_5_line_35 | NAYY 4x150 SE | 31 | 32 | 0.0034848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6109-3_0_5_line_36 | NAYY 4x150 SE | 32 | 33 | 0.012278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6109-3_0_5_line_37 | NAYY 4x150 SE | 33 | 34 | 0.0026733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6109-3_0_5_line_38 | NAYY 4x150 SE | 35 | 36 | 0.0028391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6109-3_0_5_line_39 | NAYY 4x150 SE | 38 | 39 | 0.0051415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6109-3_0_5_line_40 | NAYY 4x150 SE | 40 | 41 | 0.034063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6109-3_0_5_trafo_29 | 0.25 MVA 20/0.4 kV | 42 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2613851.9809 | 1131684.5552 | 2613851.0767 | 1131713.0337 | 2613863.301 | 1131788.4096 | 2613866.5618 | 1131806.9372 | 2613866.1176 | 1131818.6765
1 | 2613877.2374 | 1132087.0535 | 2613866.1176 | 1131818.6765
2 | 2614074.8679 | 1131600.5875 | 2613851.9809 | 1131684.5552
3 | 2613928.3009 | 1132229.4416 | 2613922.2468 | 1132198.9118 | 2613901.3147 | 1132141.0133 | 2613877.2374 | 1132087.0535
4 | 2614074.8679 | 1131600.5875 | 2614074.3905 | 1131587.5861 | 2614077.3335 | 1131567.005 | 2614093.9061 | 1131542.7539 | 2614100.8518 | 1131525.8956
5 | 2613918.8313 | 1132281.5666 | 2613930.4134 | 1132240.0951 | 2613928.3009 | 1132229.4416
6 | 2614107.2717 | 1131510.3135 | 2614100.8518 | 1131525.8956
7 | 2613797.1103 | 1132385.1919 | 2613796.5425 | 1132392.286 | 2613794.5139 | 1132404.1205 | 2613793.1228 | 1132409.1115
8 | 2613758.4524 | 1132478.8196 | 2613762.9898 | 1132470.7926 | 2613780.1843 | 1132442.2732 | 2613785.2043 | 1132431.9796 | 2613789.2002 | 1132421.6948 | 2613792.2318 | 1132412.3082 | 2613793.1228 | 1132409.1115
9 | 2613705.4664 | 1132371.1693 | 2613705.5565 | 1132375.5939 | 2613699.9518 | 1132389.1657 | 2613687.5159 | 1132410.6481 | 2613683.8738 | 1132421.1339 | 2613685.5954 | 1132436.0562 | 2613688.2614 | 1132445.3334 | 2613692.8889 | 1132451.9249 | 2613700.0068 | 1132456.8878 | 2613710.8777 | 1132460.1917 | 2613742.2902 | 1132469.7341 | 2613753.7031 | 1132475.0737 | 2613758.4524 | 1132478.8196
10 | 2613805.4844 | 1132262.1538 | 2613798.2188 | 1132288.2612 | 2613789.8799 | 1132315.7112 | 2613776.0297 | 1132356.3107 | 2613764.0942 | 1132391.2007 | 2613758.7005 | 1132423.7488 | 2613742.91 | 1132468.0013 | 2613742.2902 | 1132469.7341 | 2613753.7031 | 1132475.0737 | 2613758.4524 | 1132478.8196
11 | 2613758.4524 | 1132478.8196 | 2613756.9174 | 1132483.5295 | 2613755.744 | 1132488.3181 | 2613755.3967 | 1132492.0969 | 2613755.8961 | 1132495.9444 | 2613757.3723 | 1132500.2165 | 2613759.4566 | 1132504.49 | 2613764.7361 | 1132512.1056 | 2613768.8297 | 1132516.4282 | 2613773.8399 | 1132520.5526 | 2613784.8571 | 1132527.192 | 2613787.6856 | 1132529.2216 | 2613790.4515 | 1132531.6736 | 2613820.4167 | 1132513.9442 | 2613831.3877 | 1132503.6753 | 2613843.3864 | 1132491.7635 | 2613844.16 | 1132490.1311
12 | 2613705.4664 | 1132371.1693 | 2613707.9966 | 1132348.5307 | 2613704.713 | 1132336.5841 | 2613705.1548 | 1132325.0572 | 2613707.2339 | 1132318.0585 | 2613722.5563 | 1132300.3956 | 2613726.7149 | 1132289.6998 | 2613727.5685 | 1132276.5286 | 2613727.2896 | 1132270.4694 | 2613727.1723 | 1132267.879 | 2613727.125 | 1132267.5065
13 | 2613805.4844 | 1132262.1538 | 2613808.5296 | 1132250.1993 | 2613808.3569 | 1132234.7581 | 2613805.334 | 1132223.3901 | 2613802.7826 | 1132211.1338
14 | 2613805.4844 | 1132262.1538 | 2613802.7178 | 1132239.6476 | 2613799.8522 | 1132226.7793 | 2613796.6606 | 1132221.8252 | 2613794.3927 | 1132220.3748 | 2613792.1215 | 1132220.3697 | 2613789.1235 | 1132221.708 | 2613787.5683 | 1132225.095 | 2613786.0935 | 1132229.7065
15 | 2613844.16 | 1132490.1311 | 2613855.2448 | 1132490.7567 | 2613859.6107 | 1132487.0426 | 2613865.8289 | 1132474.6285 | 2613870.1301 | 1132471.2525
16 | 2613844.16 | 1132490.1311 | 2613854.8052 | 1132467.4999 | 2613866.23 | 1132447.3606 | 2613872.3029 | 1132438.3954
17 | 2613904.7063 | 1132317.3517 | 2613891.1919 | 1132358.8966 | 2613891.5763 | 1132369.1914 | 2613891.1442 | 1132379.6956 | 2613886.2207 | 1132404.9633
18 | 2613904.7063 | 1132317.3517 | 2613918.8313 | 1132281.5666
19 | 2613904.7063 | 1132317.3517 | 2613916.9992 | 1132325.7101
20 | 2613886.2207 | 1132404.9633 | 2613888.5226 | 1132404.9797 | 2613896.4645 | 1132406.4319
21 | 2613886.2207 | 1132404.9633 | 2613885.5897 | 1132408.219 | 2613885.7304 | 1132413.9888 | 2613885.8729 | 1132419.0027 | 2613882.943 | 1132424.2986 | 2613879.4627 | 1132427.8257 | 2613875.8915 | 1132433.0977
22 | 2613918.8313 | 1132281.5666 | 2613932.2558 | 1132279.3296 | 2613953.968 | 1132268.8855 | 2613953.968 | 1132268.8855
23 | 2613802.7826 | 1132211.1338 | 2613802.7188 | 1132191.8354 | 2613801.3125 | 1132177.1139 | 2613796.3709 | 1132169.7991 | 2613776.3596 | 1132157.1121
24 | 2613786.0935 | 1132229.7065 | 2613782.3309 | 1132241.4718
25 | 2613870.1301 | 1132471.2525 | 2613871.0022 | 1132470.568
26 | 2613872.3029 | 1132438.3954 | 2613875.8915 | 1132433.0977
27 | 2613896.4645 | 1132406.4319 | 2613905.0686 | 1132410.7011
28 | 2613953.968 | 1132268.8855 | 2613981.2779 | 1132244.8699 | 2613989.5259 | 1132240.5202
29 | 2613781.9618 | 1132242.6259 | 2613782.3309 | 1132241.4718
30 | 2613871.0022 | 1132470.568 | 2613872.9322 | 1132469.0531 | 2613880.452 | 1132463.5277
31 | 2613910.1471 | 1132413.221 | 2613905.0686 | 1132410.7011
32 | 2613885.8725 | 1132459.5447 | 2613880.452 | 1132463.5277
33 | 2613910.1471 | 1132413.221 | 2613913.9309 | 1132415.0985
34 | 2613885.8725 | 1132459.5447 | 2613885.8725 | 1132459.5447 | 2613889.228 | 1132456.7177 | 2613892.2564 | 1132455.5018 | 2613892.2564 | 1132455.5018
35 | 2613892.2564 | 1132455.5018 | 2613895.3708 | 1132457.0653 | 2613895.3708 | 1132457.0653
36 | 2613904.3418 | 1132465.4479 | 2613895.3708 | 1132457.0653
37 | 2613906.2951 | 1132467.2731 | 2613904.3418 | 1132465.4479
38 | 2613916.4742 | 1132416.3604 | 2613913.9309 | 1132415.0985
39 | 2613780.3957 | 1132247.523 | 2613781.9618 | 1132242.6259
40 | 2614107.2717 | 1131510.3135 | 2614105.7619 | 1131503.9291 | 2614104.3552 | 1131499.6015 | 2614097.4559 | 1131479.7424 | 2614096.7768 | 1131477.9375

## bus_geodata
| x | y | coords
0 | 2613866.1176 | 1131818.6765
1 | 2613851.9809 | 1131684.5552
2 | 2613877.2374 | 1132087.0535
3 | 2614074.8679 | 1131600.5875
4 | 2613928.3009 | 1132229.4416
5 | 2614100.8518 | 1131525.8956
6 | 2613797.1103 | 1132385.1919
7 | 2613793.1228 | 1132409.1115
8 | 2613758.4524 | 1132478.8196
9 | 2613705.4664 | 1132371.1693
10 | 2613805.4844 | 1132262.1538
11 | 2613844.16 | 1132490.1311
12 | 2613904.7063 | 1132317.3517
13 | 2613886.2207 | 1132404.9633
14 | 2613918.8313 | 1132281.5666
15 | 2613916.9992 | 1132325.7101
16 | 2613727.125 | 1132267.5065
17 | 2613802.7826 | 1132211.1338
18 | 2613786.0935 | 1132229.7065
19 | 2613870.1301 | 1132471.2525
20 | 2613872.3029 | 1132438.3954
21 | 2613896.4645 | 1132406.4319
22 | 2613875.8915 | 1132433.0977
23 | 2613953.968 | 1132268.8855
24 | 2613776.3596 | 1132157.1121
25 | 2613782.3309 | 1132241.4718
26 | 2613871.0022 | 1132470.568
27 | 2613905.0686 | 1132410.7011
28 | 2613880.452 | 1132463.5277
29 | 2613910.1471 | 1132413.221
30 | 2613885.8725 | 1132459.5447
31 | 2613892.2564 | 1132455.5018
32 | 2613895.3708 | 1132457.0653
33 | 2613904.3418 | 1132465.4479
34 | 2613906.2951 | 1132467.2731
35 | 2613913.9309 | 1132415.0985
36 | 2613916.4742 | 1132416.3604
37 | 2613989.5259 | 1132240.5202
38 | 2613781.9618 | 1132242.6259
39 | 2613780.3957 | 1132247.523
40 | 2614107.2717 | 1131510.3135
41 | 2614096.7768 | 1131477.9375
42 | 2613918.8313 | 1132281.5666

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1