## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6151-31_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6151-31_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6151-31_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6151-31_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6151-31_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_6151-31_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6151-31_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_6151-31_0_2_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_6151-31_0_2_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_6151-31_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_6151-31_0_2_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_6151-31_0_2_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_6151-31_0_2_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_6151-31_0_2_node_18 | 0.4 | n |  | TRUE
14 | bus_LV_6151-31_0_2_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_6151-31_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_6151-31_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_6151-31_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_6151-31_0_2_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_6151-31_0_2_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_6151-31_0_2_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_6151-31_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_6151-31_0_2_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_6151-31_0_2_node_17 | 0.4 | n |  | TRUE
24 | bus_MV_204_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6151-31_0_2_load_0 | 0 | 0.0051543 | 0.0012918 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6151-31_0_2_load_1 | 1 | 0.0032687 | 0.0008192 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6151-31_0_2_load_3 | 3 | 0.0059289 | 0.0014859 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6151-31_0_2_load_4 | 4 | 0.0038472 | 0.00096419 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6151-31_0_2_load_5 | 5 | 0.0097233 | 0.0024369 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6151-31_0_2_load_8 | 6 | 0.0035452 | 0.00088852 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6151-31_0_2_load_22 | 8 | 0.016484 | 0.0041314 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6151-31_0_2_load_7 | 9 | 0.0026509 | 0.00066438 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6151-31_0_2_load_10 | 10 | 0.014405 | 0.0036103 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6151-31_0_2_load_21 | 11 | 0.01033 | 0.0025889 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6151-31_0_2_load_6 | 12 | 0.0029181 | 0.00073135 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6151-31_0_2_load_18 | 13 | 0.016576 | 0.0041543 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6151-31_0_2_load_19 | 14 | 0.015738 | 0.0039444 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6151-31_0_2_load_15 | 16 | 0.0065783 | 0.0016487 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6151-31_0_2_load_11 | 17 | 0.007591 | 0.0019025 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6151-31_0_2_load_14 | 19 | 0.0094545 | 0.0023695 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6151-31_0_2_load_24 | 20 | 0.017927 | 0.0044929 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6151-31_0_2_load_16 | 21 | 0.0097669 | 0.0024478 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6151-31_0_2_load_23 | 22 | 0.0049635 | 0.001244 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6151-31_0_2_load_17 | 23 | 0.016423 | 0.0041159 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6151-31_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6151-31_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0072823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6151-31_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.034792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6151-31_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.016127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6151-31_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.051179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6151-31_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.01431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6151-31_0_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.040202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6151-31_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.027392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6151-31_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.011956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6151-31_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.05607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6151-31_0_2_line_10 | NAYY 4x150 SE | 8 | 11 | 0.029453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6151-31_0_2_line_11 | NAYY 4x150 SE | 9 | 12 | 0.022996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6151-31_0_2_line_12 | NAYY 4x150 SE | 10 | 13 | 0.0041389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6151-31_0_2_line_13 | NAYY 4x150 SE | 11 | 22 | 0.025792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6151-31_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.022351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6151-31_0_2_line_15 | NAYY 4x150 SE | 14 | 21 | 0.04568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_6151-31_0_2_line_16 | NAYY 4x150 SE | 15 | 16 | 0.049436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6151-31_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.038745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6151-31_0_2_line_18 | NAYY 4x150 SE | 16 | 21 | 0.025849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6151-31_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.023951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6151-31_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.051233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6151-31_0_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.12903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6151-31_0_2_line_22 | NAYY 4x150 SE | 21 | 23 | 0.011615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6151-31_0_2_trafo_17 | 0.25 MVA 20/0.4 kV | 24 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2556301.5331 | 1114666.4127 | 2556309.4394 | 1114672.5911 | 2556318.8666 | 1114678.922
1 | 2556295.7951 | 1114661.9287 | 2556301.5331 | 1114666.4127
2 | 2556318.8666 | 1114678.922 | 2556325.2766 | 1114683.2267 | 2556348.6117 | 1114696.9481
3 | 2556295.7951 | 1114661.9287 | 2556284.4765 | 1114650.4409
4 | 2556295.7951 | 1114661.9287 | 2556302.5695 | 1114662.2577 | 2556332.7265 | 1114673.39 | 2556344.2377 | 1114677.5807
5 | 2556359.5906 | 1114706.065 | 2556350.7509 | 1114698.206 | 2556348.6117 | 1114696.9481
6 | 2556258.6487 | 1114619.731 | 2556264.3226 | 1114628.0276 | 2556280.0038 | 1114645.9012 | 2556284.4765 | 1114650.4409
7 | 2556344.2377 | 1114677.5807 | 2556363.4475 | 1114684.574 | 2556370.1098 | 1114686.5497
8 | 2556359.5906 | 1114706.065 | 2556361.2194 | 1114707.5131 | 2556367.8544 | 1114714.6934
9 | 2556258.6487 | 1114619.731 | 2556268.4406 | 1114624.0735 | 2556286.4679 | 1114630.024 | 2556298.7767 | 1114635.3712 | 2556310.9556 | 1114639.7864
10 | 2556398.796 | 1114690.9021 | 2556394.9506 | 1114689.6605 | 2556382.9173 | 1114690.3476 | 2556370.1098 | 1114686.5497
11 | 2556387.1218 | 1114726.9147 | 2556378.9464 | 1114723.2489 | 2556369.0565 | 1114715.9942 | 2556367.8544 | 1114714.6934
12 | 2556310.9556 | 1114639.7864 | 2556312.4261 | 1114640.3195 | 2556314.589 | 1114641.7163
13 | 2556423.3403 | 1114698.8272 | 2556398.796 | 1114690.9021
14 | 2556333.3652 | 1114653.8419 | 2556314.589 | 1114641.7163
15 | 2556333.3652 | 1114653.8419 | 2556358.0059 | 1114615.3775
16 | 2556328.9233 | 1114553.1441 | 2556326.8972 | 1114559.1397 | 2556326.9514 | 1114567.7104 | 2556327.7551 | 1114578.4879 | 2556328.8061 | 1114587.1515 | 2556332.7219 | 1114592.5927 | 2556338.4336 | 1114598.6129
17 | 2556328.9233 | 1114553.1441 | 2556341.5907 | 1114566.4262 | 2556355.9877 | 1114580.8663
18 | 2556358.0059 | 1114615.3775 | 2556344.8838 | 1114605.4115 | 2556338.4336 | 1114598.6129
19 | 2556372.8983 | 1114597.8276 | 2556355.9877 | 1114580.8663
20 | 2556372.8983 | 1114597.8276 | 2556387.0066 | 1114611.7886 | 2556399.9307 | 1114622.1674 | 2556411.2633 | 1114629.2227 | 2556412.5972 | 1114629.8168
21 | 2556372.8983 | 1114597.8276 | 2556461.2469 | 1114503.7866
22 | 2556368.2918 | 1114620.7727 | 2556358.0059 | 1114615.3775

## bus_geodata
| x | y | coords
0 | 2556301.5331 | 1114666.4127
1 | 2556318.8666 | 1114678.922
2 | 2556295.7951 | 1114661.9287
3 | 2556348.6117 | 1114696.9481
4 | 2556284.4765 | 1114650.4409
5 | 2556344.2377 | 1114677.5807
6 | 2556359.5906 | 1114706.065
7 | 2556258.6487 | 1114619.731
8 | 2556370.1098 | 1114686.5497
9 | 2556367.8544 | 1114714.6934
10 | 2556310.9556 | 1114639.7864
11 | 2556398.796 | 1114690.9021
12 | 2556387.1218 | 1114726.9147
13 | 2556314.589 | 1114641.7163
14 | 2556333.3652 | 1114653.8419
15 | 2556328.9233 | 1114553.1441
16 | 2556338.4336 | 1114598.6129
17 | 2556355.9877 | 1114580.8663
18 | 2556372.8983 | 1114597.8276
19 | 2556412.5972 | 1114629.8168
20 | 2556461.2469 | 1114503.7866
21 | 2556358.0059 | 1114615.3775
22 | 2556423.3403 | 1114698.8272
23 | 2556368.2918 | 1114620.7727
24 | 2556328.9233 | 1114553.1441

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97959 | -0.14296 | 0.0051543 | 0.0012918
1 | 0.97901 | -0.14703 | 0.0032687 | 0.0008192
2 | 0.97983 | -0.14118 | 0 | 0
3 | 0.97825 | -0.15249 | 0.0059289 | 0.0014859
4 | 0.98136 | -0.1303 | 0.0038472 | 0.00096419
5 | 0.97673 | -0.16333 | 0.0097233 | 0.0024369
6 | 0.97806 | -0.15385 | 0.0035452 | 0.00088852
7 | 0.9854 | -0.10174 | 0 | 0
8 | 0.97546 | -0.17245 | 0.016484 | 0.0041314
9 | 0.97796 | -0.15455 | 0.0026509 | 0.00066438
10 | 0.99103 | -0.062287 | 0.014405 | 0.0036103
11 | 0.9748 | -0.17718 | 0.01033 | 0.0025889
12 | 0.97787 | -0.15525 | 0.0029181 | 0.00073135
13 | 0.99153 | -0.058787 | 0.016576 | 0.0041543
14 | 0.99477 | -0.03621 | 0.015738 | 0.0039444
15 | 0.99456 | -0.037876 | 0 | 0
16 | 0.99705 | -0.020463 | 0.0065783 | 0.0016487
17 | 0.99261 | -0.051583 | 0.007591 | 0.0019025
18 | 0.99167 | -0.058237 | 0 | 0
19 | 0.99097 | -0.063157 | 0.0094545 | 0.0023695
20 | 0.98833 | -0.0818 | 0.017927 | 0.0044929
21 | 0.9986 | -0.0096889 | 0.0097669 | 0.0024478
22 | 0.97461 | -0.17853 | 0.0049635 | 0.001244
23 | 1 | 0 | -0.16995 | -0.042691
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.018336 | 0.0045974 | -0.018326 | -0.0045937 | 1.0355e-05 | 3.7136e-06 | 0.027854 | 0.027854 | 0.027854 | 0.97959 | -0.14296 | 0.97901 | -0.14703 | 10.3162
1 | -0.02349 | -0.0058892 | 0.023496 | 0.0058913 | 5.786e-06 | 2.1337e-06 | 0.035683 | 0.035683 | 0.035683 | 0.97959 | -0.14296 | 0.97983 | -0.14118 | 13.216
2 | 0.015057 | 0.0037745 | -0.015046 | -0.0037705 | 1.1371e-05 | 3.9363e-06 | 0.022886 | 0.022886 | 0.022886 | 0.97901 | -0.14703 | 0.97825 | -0.15249 | 8.4763
3 | -0.065176 | -0.01636 | 0.065275 | 0.016397 | 9.8607e-05 | 3.7722e-05 | 0.098989 | 0.098988 | 0.098989 | 0.97983 | -0.14118 | 0.98136 | -0.1303 | 36.6624
4 | 0.04168 | 0.010468 | -0.041552 | -0.01042 | 0.00012798 | 4.8582e-05 | 0.063305 | 0.063306 | 0.063306 | 0.97983 | -0.14118 | 0.97673 | -0.16333 | 23.4465
5 | 0.0091168 | 0.0022846 | -0.0091151 | -0.0022841 | 1.7172e-06 | 4.8083e-07 | 0.013867 | 0.013868 | 0.013868 | 0.97825 | -0.15249 | 0.97806 | -0.15385 | 5.1361
6 | -0.069122 | -0.017362 | 0.069398 | 0.017467 | 0.00027563 | 0.0001055 | 0.10482 | 0.10482 | 0.10482 | 0.98136 | -0.1303 | 0.9854 | -0.10174 | 38.8229
7 | 0.031829 | 0.0079829 | -0.031789 | -0.0079678 | 4.0194e-05 | 1.5117e-05 | 0.048492 | 0.048493 | 0.048493 | 0.97673 | -0.16333 | 0.97546 | -0.17245 | 17.9602
8 | 0.0055699 | 0.0013956 | -0.0055693 | -0.0013956 | 5.3571e-07 | 5.6012e-08 | 0.0084739 | 0.0084739 | 0.0084739 | 0.97806 | -0.15385 | 0.97796 | -0.15455 | 3.1385
9 | -0.069398 | -0.017467 | 0.069782 | 0.017614 | 0.00038443 | 0.00014714 | 0.10482 | 0.10482 | 0.10482 | 0.9854 | -0.10174 | 0.99103 | -0.062287 | 38.8228
10 | 0.015304 | 0.0038364 | -0.015294 | -0.0038329 | 1.0017e-05 | 3.4854e-06 | 0.023346 | 0.023347 | 0.023347 | 0.97546 | -0.17245 | 0.9748 | -0.17718 | 8.6469
11 | 0.0029184 | 0.00073117 | -0.0029181 | -0.00073135 | 2.8294e-07 | -1.7969e-07 | 0.0044404 | 0.0044405 | 0.0044405 | 0.97796 | -0.15455 | 0.97787 | -0.15525 | 1.6446
12 | -0.084188 | -0.021225 | 0.084229 | 0.02124 | 4.1297e-05 | 1.583e-05 | 0.12645 | 0.12645 | 0.12645 | 0.99103 | -0.062287 | 0.99153 | -0.058787 | 46.8336
13 | 0.0049644 | 0.001244 | -0.0049635 | -0.001244 | 9.2424e-07 | 3.4004e-08 | 0.007578 | 0.0075781 | 0.0075781 | 0.9748 | -0.17718 | 0.97461 | -0.17853 | 2.8067
14 | -0.1008 | -0.025395 | 0.10112 | 0.025517 | 0.00031938 | 0.00012255 | 0.15133 | 0.15133 | 0.15133 | 0.99153 | -0.058787 | 0.99477 | -0.03621 | 56.0467
15 | -0.11686 | -0.029462 | 0.1173 | 0.029628 | 0.00043581 | 0.00016643 | 0.17487 | 0.17487 | 0.17487 | 0.99477 | -0.03621 | 0.9986 | -0.0096889 | 32.383
16 | -0.03513 | -0.0088223 | 0.035215 | 0.0088544 | 8.5238e-05 | 3.2141e-05 | 0.052566 | 0.052565 | 0.052566 | 0.99456 | -0.037876 | 0.99705 | -0.020463 | 19.4687
17 | 0.03513 | 0.0088223 | -0.035063 | -0.0087971 | 6.6804e-05 | 2.5192e-05 | 0.052566 | 0.052566 | 0.052566 | 0.99456 | -0.037876 | 0.99261 | -0.051583 | 19.4688
18 | -0.041793 | -0.010503 | 0.041856 | 0.010527 | 6.2771e-05 | 2.3805e-05 | 0.062383 | 0.062383 | 0.062383 | 0.99705 | -0.020463 | 0.9986 | -0.0096889 | 23.1048
19 | 0.027472 | 0.0068946 | -0.027447 | -0.0068852 | 2.5352e-05 | 9.4415e-06 | 0.041186 | 0.041186 | 0.041186 | 0.99261 | -0.051583 | 0.99167 | -0.058237 | 15.2542
20 | 0.009461 | 0.0023713 | -0.0094545 | -0.0023695 | 6.4432e-06 | 1.8176e-06 | 0.014196 | 0.014197 | 0.014197 | 0.99167 | -0.058237 | 0.99097 | -0.063157 | 5.258
21 | 0.017986 | 0.0045138 | -0.017927 | -0.0044929 | 5.8653e-05 | 2.09e-05 | 0.02699 | 0.02699 | 0.02699 | 0.99167 | -0.058237 | 0.98833 | -0.0818 | 9.9965
22 | -0.16892 | -0.042603 | 0.16915 | 0.042691 | 0.00022977 | 8.807e-05 | 0.2518 | 0.2518 | 0.2518 | 0.9986 | -0.0096889 | 1 | 0 | 46.6304

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18637 | 0.046807

## res_load
| p_mw | q_mvar
0 | 0.0051543 | 0.0012918
1 | 0.0032687 | 0.0008192
2 | 0.0059289 | 0.0014859
3 | 0.0038472 | 0.00096419
4 | 0.0097233 | 0.0024369
5 | 0.0035452 | 0.00088852
6 | 0.016484 | 0.0041314
7 | 0.0026509 | 0.00066438
8 | 0.014405 | 0.0036103
9 | 0.01033 | 0.0025889
10 | 0.0029181 | 0.00073135
11 | 0.016576 | 0.0041543
12 | 0.015738 | 0.0039444
13 | 0.0065783 | 0.0016487
14 | 0.007591 | 0.0019025
15 | 0.0094545 | 0.0023695
16 | 0.017927 | 0.0044929
17 | 0.0097669 | 0.0024478
18 | 0.0049635 | 0.001244
19 | 0.016423 | 0.0041159

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1