## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6181-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6181-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6181-15_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_6181-15_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_6181-15_0_4_node_73 | 0.4 | n |  | TRUE
5 | bus_LV_6181-15_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_6181-15_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_6181-15_0_4_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_6181-15_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_6181-15_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_6181-15_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_6181-15_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_6181-15_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_6181-15_0_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_6181-15_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_6181-15_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_6181-15_0_4_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_6181-15_0_4_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_6181-15_0_4_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_6181-15_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_6181-15_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_6181-15_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_6181-15_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_6181-15_0_4_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_6181-15_0_4_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_6181-15_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_6181-15_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_6181-15_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_6181-15_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_6181-15_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_6181-15_0_4_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_6181-15_0_4_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_6181-15_0_4_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_6181-15_0_4_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_6181-15_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_6181-15_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_6181-15_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_6181-15_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_6181-15_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6181-15_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_6181-15_0_4_node_72 | 0.4 | n |  | TRUE
41 | bus_LV_6181-15_0_4_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_6181-15_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_6181-15_0_4_node_49 | 0.4 | n |  | TRUE
44 | bus_LV_6181-15_0_4_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_6181-15_0_4_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_6181-15_0_4_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_6181-15_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_6181-15_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_6181-15_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_6181-15_0_4_node_69 | 0.4 | n |  | TRUE
51 | bus_LV_6181-15_0_4_node_70 | 0.4 | n |  | TRUE
52 | bus_LV_6181-15_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_6181-15_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_6181-15_0_4_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_6181-15_0_4_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_6181-15_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_6181-15_0_4_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_6181-15_0_4_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_6181-15_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_6181-15_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_6181-15_0_4_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_6181-15_0_4_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_6181-15_0_4_node_71 | 0.4 | n |  | TRUE
64 | bus_LV_6181-15_0_4_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_6181-15_0_4_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_6181-15_0_4_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_6181-15_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_6181-15_0_4_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_6181-15_0_4_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_6181-15_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_MV_87_1_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6181-15_0_4_load_0 | 0 | 0.006564 | 0.0016451 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6181-15_0_4_load_4 | 3 | 0.012418 | 0.0031121 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6181-15_0_4_load_73 | 4 | 0.0049335 | 0.0012364 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6181-15_0_4_load_74 | 7 | 0.0059413 | 0.001489 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6181-15_0_4_load_7 | 8 | 0.0052945 | 0.0013269 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6181-15_0_4_load_8 | 9 | 0.015606 | 0.0039113 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6181-15_0_4_load_9 | 10 | 0.00665 | 0.0016666 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6181-15_0_4_load_10 | 11 | 0.0052223 | 0.0013088 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6181-15_0_4_load_11 | 12 | 0.0056299 | 0.001411 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6181-15_0_4_load_12 | 13 | 0.005533 | 0.0013867 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6181-15_0_4_load_13 | 14 | 0.0042371 | 0.0010619 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6181-15_0_4_load_15 | 16 | 0.042961 | 0.010767 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6181-15_0_4_load_16 | 19 | 0.0062828 | 0.0015746 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6181-15_0_4_load_18 | 20 | 0.0054507 | 0.0013661 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6181-15_0_4_load_20 | 21 | 0.0017701 | 0.00044364 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6181-15_0_4_load_21 | 22 | 0.0016021 | 0.00040153 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6181-15_0_4_load_22 | 23 | 0.0023417 | 0.0005869 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6181-15_0_4_load_28 | 24 | 0.0025607 | 0.00064178 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6181-15_0_4_load_23 | 26 | 0.0022668 | 0.00056812 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6181-15_0_4_load_38 | 29 | 0.0056384 | 0.0014131 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6181-15_0_4_load_36 | 30 | 0.0055652 | 0.0013948 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6181-15_0_4_load_37 | 31 | 0.0021308 | 0.00053402 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6181-15_0_4_load_35 | 32 | 0.0052436 | 0.0013142 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6181-15_0_4_load_29 | 35 | 0.0017267 | 0.00043276 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6181-15_0_4_load_30 | 36 | 0.0059152 | 0.0014825 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6181-15_0_4_load_31 | 37 | 0.0054687 | 0.0013706 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6181-15_0_4_load_32 | 38 | 0.001643 | 0.00041178 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6181-15_0_4_load_34 | 39 | 0.0016476 | 0.00041292 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6181-15_0_4_load_72 | 40 | 0.0060598 | 0.0015187 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6181-15_0_4_load_39 | 41 | 0.0016549 | 0.00041475 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6181-15_0_4_load_40 | 42 | 0.0028273 | 0.00070858 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6181-15_0_4_load_49 | 43 | 0.0018494 | 0.00046352 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6181-15_0_4_load_50 | 44 | 0.0025758 | 0.00064555 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6181-15_0_4_load_44 | 45 | 0.0016851 | 0.00042234 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6181-15_0_4_load_41 | 47 | 0.0026569 | 0.00066589 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6181-15_0_4_load_43 | 49 | 0.0034264 | 0.00085874 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6181-15_0_4_load_69 | 50 | 0.0035503 | 0.0008898 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6181-15_0_4_load_70 | 51 | 0.0040572 | 0.0010168 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6181-15_0_4_load_47 | 53 | 0.0016667 | 0.00041771 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6181-15_0_4_load_68 | 54 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6181-15_0_4_load_65 | 55 | 0.0026097 | 0.00065406 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6181-15_0_4_load_56 | 56 | 0.0015634 | 0.00039181 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6181-15_0_4_load_64 | 57 | 0.0023972 | 0.0006008 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6181-15_0_4_load_51 | 59 | 0.0019478 | 0.00048816 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6181-15_0_4_load_55 | 61 | 0.0024842 | 0.00062261 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6181-15_0_4_load_71 | 63 | 0.0027051 | 0.00067796 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6181-15_0_4_load_57 | 64 | 0.0023305 | 0.00058408 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6181-15_0_4_load_60 | 66 | 0.0025631 | 0.00064237 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6181-15_0_4_load_62 | 68 | 0.0022825 | 0.00057206 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6181-15_0_4_load_67 | 69 | 0.0019777 | 0.00049566 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6181-15_0_4_load_63 | 70 | 0.0021328 | 0.00053452 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6181-15_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.011783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6181-15_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.013284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6181-15_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.021615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6181-15_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.030752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6181-15_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.028914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6181-15_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.032129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6181-15_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.041183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6181-15_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.017743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6181-15_0_4_line_8 | NAYY 4x150 SE | 8 | 9 | 0.0081837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6181-15_0_4_line_9 | NAYY 4x150 SE | 9 | 10 | 0.019931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6181-15_0_4_line_10 | NAYY 4x150 SE | 10 | 11 | 0.018133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6181-15_0_4_line_11 | NAYY 4x150 SE | 11 | 12 | 0.020727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6181-15_0_4_line_12 | NAYY 4x150 SE | 12 | 13 | 0.017452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6181-15_0_4_line_13 | NAYY 4x150 SE | 13 | 14 | 0.027035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6181-15_0_4_line_14 | NAYY 4x150 SE | 14 | 15 | 0.027443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6181-15_0_4_line_15 | NAYY 4x150 SE | 15 | 16 | 0.020901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6181-15_0_4_line_16 | NAYY 4x150 SE | 16 | 17 | 0.015358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_6181-15_0_4_line_17 | NAYY 4x150 SE | 17 | 18 | 0.029181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_6181-15_0_4_line_18 | NAYY 4x150 SE | 18 | 20 | 0.030459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_6181-15_0_4_line_19 | NAYY 4x150 SE | 18 | 19 | 0.01642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6181-15_0_4_line_20 | NAYY 4x150 SE | 20 | 21 | 0.018464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_6181-15_0_4_line_21 | NAYY 4x150 SE | 21 | 22 | 0.029217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_6181-15_0_4_line_22 | NAYY 4x150 SE | 22 | 23 | 0.021974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_6181-15_0_4_line_23 | NAYY 4x150 SE | 23 | 24 | 0.028332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_6181-15_0_4_line_24 | NAYY 4x150 SE | 24 | 25 | 0.006324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_6181-15_0_4_line_25 | NAYY 4x150 SE | 25 | 27 | 0.059873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_6181-15_0_4_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0067908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6181-15_0_4_line_27 | NAYY 4x150 SE | 27 | 31 | 0.034985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_6181-15_0_4_line_28 | NAYY 4x150 SE | 27 | 32 | 0.013792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6181-15_0_4_line_29 | NAYY 4x150 SE | 28 | 29 | 0.010959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6181-15_0_4_line_30 | NAYY 4x150 SE | 28 | 30 | 0.023946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6181-15_0_4_line_31 | NAYY 4x150 SE | 29 | 33 | 0.018197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6181-15_0_4_line_32 | NAYY 4x150 SE | 30 | 32 | 0.018105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6181-15_0_4_line_33 | NAYY 4x150 SE | 31 | 34 | 0.0043293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_6181-15_0_4_line_34 | NAYY 4x150 SE | 33 | 43 | 0.027182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6181-15_0_4_line_35 | NAYY 4x150 SE | 33 | 44 | 0.057553 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6181-15_0_4_line_36 | NAYY 4x150 SE | 34 | 40 | 0.013891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6181-15_0_4_line_37 | NAYY 4x150 SE | 34 | 37 | 0.028896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_6181-15_0_4_line_38 | NAYY 4x150 SE | 35 | 36 | 0.0032162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
39 | LV_6181-15_0_4_line_39 | NAYY 4x150 SE | 35 | 37 | 0.016018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_6181-15_0_4_line_40 | NAYY 4x150 SE | 36 | 38 | 0.01383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_6181-15_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.0066694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_6181-15_0_4_line_42 | NAYY 4x150 SE | 39 | 41 | 0.013623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_6181-15_0_4_line_43 | NAYY 4x150 SE | 41 | 42 | 0.011144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_6181-15_0_4_line_44 | NAYY 4x150 SE | 42 | 45 | 0.015289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_6181-15_0_4_line_45 | NAYY 4x150 SE | 45 | 46 | 0.070062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_6181-15_0_4_line_46 | NAYY 4x150 SE | 46 | 52 | 0.020842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6181-15_0_4_line_47 | NAYY 4x150 SE | 46 | 53 | 0.075691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_6181-15_0_4_line_48 | NAYY 4x150 SE | 47 | 48 | 0.0065348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_6181-15_0_4_line_49 | NAYY 4x150 SE | 48 | 49 | 0.0020085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_6181-15_0_4_line_50 | NAYY 4x150 SE | 49 | 50 | 0.034043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6181-15_0_4_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0074055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6181-15_0_4_line_52 | NAYY 4x150 SE | 51 | 60 | 0.08744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6181-15_0_4_line_53 | NAYY 4x150 SE | 52 | 54 | 0.019573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6181-15_0_4_line_54 | NAYY 4x150 SE | 52 | 55 | 0.0035736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6181-15_0_4_line_55 | NAYY 4x150 SE | 53 | 56 | 0.015087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_6181-15_0_4_line_56 | NAYY 4x150 SE | 55 | 57 | 0.018194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_6181-15_0_4_line_57 | NAYY 4x150 SE | 56 | 58 | 0.0177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_6181-15_0_4_line_58 | NAYY 4x150 SE | 57 | 70 | 0.020151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_6181-15_0_4_line_59 | NAYY 4x150 SE | 58 | 62 | 0.037879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_6181-15_0_4_line_60 | NAYY 4x150 SE | 58 | 59 | 0.083277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_6181-15_0_4_line_61 | NAYY 4x150 SE | 59 | 60 | 0.004373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_6181-15_0_4_line_62 | NAYY 4x150 SE | 60 | 61 | 0.023524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_6181-15_0_4_line_63 | NAYY 4x150 SE | 62 | 63 | 0.10078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_6181-15_0_4_line_64 | NAYY 4x150 SE | 64 | 65 | 0.0032702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_6181-15_0_4_line_65 | NAYY 4x150 SE | 65 | 66 | 0.017559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_6181-15_0_4_line_66 | NAYY 4x150 SE | 65 | 67 | 0.029634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_6181-15_0_4_line_67 | NAYY 4x150 SE | 66 | 68 | 0.018411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_6181-15_0_4_line_68 | NAYY 4x150 SE | 67 | 69 | 0.010644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_6181-15_0_4_line_69 | NAYY 4x150 SE | 67 | 70 | 0.0022637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6181-15_0_4_trafo_18 | 0.25 MVA 20/0.4 kV | 71 | 20 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2647283.0384 | 1137134.0193 | 2647293.9603 | 1137138.4402
1 | 2647283.0384 | 1137134.0193 | 2647284.934 | 1137138.5364 | 2647291.2841 | 1137144.0334
2 | 2647283.0384 | 1137134.0193 | 2647270.5634 | 1137129.6417 | 2647262.4716 | 1137127.4096
3 | 2647291.2841 | 1137144.0334 | 2647280.1273 | 1137146.2028 | 2647274.4243 | 1137149.4487 | 2647272.7152 | 1137157.4617 | 2647272.3818 | 1137160.7497 | 2647273.7179 | 1137161.0714
4 | 2647291.2841 | 1137144.0334 | 2647292.4868 | 1137145.6659 | 2647291.1979 | 1137155.0384 | 2647289.535 | 1137169.9331 | 2647290.6566 | 1137172.0985
5 | 2647230.5961 | 1137126.8055 | 2647241.3603 | 1137125.6446 | 2647257.4977 | 1137126.0376 | 2647262.4716 | 1137127.4096
6 | 2647290.6566 | 1137172.0985 | 2647271.6428 | 1137175.5516 | 2647269.5666 | 1137177.3918 | 2647269.7606 | 1137179.1387 | 2647271.5081 | 1137179.975 | 2647272.9471 | 1137180.909 | 2647272.2015 | 1137183.7824 | 2647270.239 | 1137183.8782 | 2647269.4086 | 1137184.7944 | 2647268.4609 | 1137186.9437 | 2647269.7923 | 1137187.8768 | 2647271.6297 | 1137190.9817
7 | 2647230.5961 | 1137126.8055 | 2647220.8866 | 1137127.8635 | 2647217.5018 | 1137127.837 | 2647212.971 | 1137127.0953
8 | 2647204.973 | 1137125.4403 | 2647207.375 | 1137126.1793 | 2647212.971 | 1137127.0953
9 | 2647204.973 | 1137125.4403 | 2647199.0325 | 1137123.6128 | 2647195.138 | 1137121.8592 | 2647186.5246 | 1137117.9845
10 | 2647186.5246 | 1137117.9845 | 2647179.445 | 1137114.7997 | 2647170.4359 | 1137109.6632
11 | 2647170.4359 | 1137109.6632 | 2647164.2033 | 1137106.1096 | 2647153.4798 | 1137097.8228
12 | 2647153.4798 | 1137097.8228 | 2647149.1766 | 1137094.4975 | 2647139.8677 | 1137086.9024
13 | 2647118.9483 | 1137069.7768 | 2647125.0196 | 1137074.7878 | 2647139.8677 | 1137086.9024
14 | 2647097.7835 | 1137052.3083 | 2647118.9483 | 1137069.7768
15 | 2647097.7835 | 1137052.3083 | 2647088.1213 | 1137044.3289 | 2647080.6088 | 1137040.638
16 | 2647066.2101 | 1137035.5092 | 2647074.7859 | 1137037.7772 | 2647080.6088 | 1137040.638
17 | 2647066.2101 | 1137035.5092 | 2647052.1711 | 1137034.3438 | 2647043.1158 | 1137033.3839 | 2647037.3031 | 1137031.949
18 | 2647037.3031 | 1137031.949 | 2647028.2346 | 1137029.7106 | 2647016.3816 | 1137025.4384 | 2647008.262 | 1137022.8609
19 | 2647037.3031 | 1137031.949 | 2647031.6824 | 1137047.3775
20 | 2646990.6636 | 1137017.2745 | 2647008.262 | 1137022.8609
21 | 2646990.6636 | 1137017.2745 | 2646978.0401 | 1137013.2673 | 2646966.4475 | 1137008.1523 | 2646963.9382 | 1137006.0066
22 | 2646963.9382 | 1137006.0066 | 2646955.8472 | 1136999.0875 | 2646948.267 | 1136990.6701
23 | 2646927.372 | 1136971.7165 | 2646927.4781 | 1136971.7975 | 2646939.6157 | 1136981.0632 | 2646948.267 | 1136990.6701
24 | 2646922.3463 | 1136967.8779 | 2646927.372 | 1136971.7165
25 | 2646875.6531 | 1136933.3867 | 2646887.0739 | 1136940.8458 | 2646892.805 | 1136946.86 | 2646899.5859 | 1136951.4372 | 2646909.2599 | 1136953.9802 | 2646917.8901 | 1136959.1833 | 2646922.3463 | 1136967.8779
26 | 2646922.3463 | 1136967.8779 | 2646916.5364 | 1136964.3622
27 | 2646875.6531 | 1136933.3867 | 2646884.3486 | 1136933.154 | 2646897.9978 | 1136935.9947 | 2646904.4717 | 1136935.5225 | 2646909.8898 | 1136933.3078
28 | 2646875.6531 | 1136933.3867 | 2646861.9157 | 1136932.1644
29 | 2646821.5406 | 1136921.0164 | 2646812.5911 | 1136914.6907
30 | 2646821.5406 | 1136921.0164 | 2646830.3061 | 1136922.6629 | 2646844.5259 | 1136927.5232
31 | 2646796.9572 | 1136905.4624 | 2646806.5128 | 1136910.3945 | 2646812.5911 | 1136914.6907
32 | 2646861.9157 | 1136932.1644 | 2646856.7632 | 1136931.706 | 2646844.5259 | 1136927.5232
33 | 2646912.05 | 1136929.556 | 2646909.8898 | 1136933.3078
34 | 2646796.9572 | 1136905.4624 | 2646796.7846 | 1136896.9567 | 2646786.0416 | 1136886.3903 | 2646785.1379 | 1136882.8815
35 | 2646796.9572 | 1136905.4624 | 2646777.4977 | 1136900.8316 | 2646751.6846 | 1136897.0188 | 2646740.7281 | 1136893.6686
36 | 2646912.05 | 1136929.556 | 2646925.126 | 1136924.8692
37 | 2646912.05 | 1136929.556 | 2646909.2618 | 1136926.9886 | 2646896.7925 | 1136921.7891 | 2646887.9889 | 1136914.2419
38 | 2646875.8277 | 1136903.8163 | 2646873.3859 | 1136901.723
39 | 2646875.8277 | 1136903.8163 | 2646887.9889 | 1136914.2419
40 | 2646873.3859 | 1136901.723 | 2646862.8859 | 1136892.7215
41 | 2646857.8225 | 1136888.3807 | 2646857.8225 | 1136888.3807 | 2646862.8859 | 1136892.7215
42 | 2646857.8225 | 1136888.3807 | 2646850.3563 | 1136876.9853
43 | 2646850.3563 | 1136876.9853 | 2646847.7782 | 1136873.0505 | 2646845.2659 | 1136867.1206
44 | 2646846.1328 | 1136854.7444 | 2646846.1337 | 1136854.9395 | 2646847.902 | 1136860.067 | 2646844.4002 | 1136861.2071 | 2646845.1414 | 1136866.8269 | 2646845.2659 | 1136867.1206
45 | 2646832.1898 | 1136786.8741 | 2646836.1334 | 1136806.148 | 2646838.9837 | 1136837.4195 | 2646846.1189 | 1136851.8934 | 2646846.1328 | 1136854.7444
46 | 2646832.1898 | 1136786.8741 | 2646827.0731 | 1136785.934 | 2646818.2289 | 1136781.4965 | 2646813.0481 | 1136778.8995
47 | 2646832.1898 | 1136786.8741 | 2646835.8314 | 1136784.5678 | 2646844.5035 | 1136773.4849 | 2646852.3033 | 1136766.7419 | 2646865.2196 | 1136758.9936 | 2646871.1627 | 1136752.5919 | 2646882.1843 | 1136732.2225 | 2646882.2166 | 1136732.1981
48 | 2646968.0487 | 1136851.6841 | 2646973.3535 | 1136855.5003
49 | 2646968.0487 | 1136851.6841 | 2646966.7091 | 1136850.1875
50 | 2646949.5236 | 1136822.9233 | 2646948.5012 | 1136825.6966 | 2646949.8803 | 1136831.388 | 2646966.7091 | 1136850.1875
51 | 2646952.0851 | 1136815.9749 | 2646949.5236 | 1136822.9233
52 | 2646952.0851 | 1136815.9749 | 2646988.8547 | 1136736.642
53 | 2646813.0481 | 1136778.8995 | 2646815.5523 | 1136784.3773 | 2646815.4391 | 1136785.0879 | 2646813.4399 | 1136783.9385 | 2646811.5148 | 1136792.1056 | 2646809.4019 | 1136791.7334
54 | 2646813.0481 | 1136778.8995 | 2646809.8241 | 1136777.3579
55 | 2646882.2166 | 1136732.1981 | 2646889.0876 | 1136727.0066 | 2646894.6689 | 1136723.7239
56 | 2646793.4096 | 1136769.5093 | 2646809.8241 | 1136777.3579
57 | 2646905.3656 | 1136710.4244 | 2646903.2351 | 1136716.2776 | 2646898.4707 | 1136721.4877 | 2646894.6689 | 1136723.7239
58 | 2646793.4096 | 1136769.5093 | 2646785.0662 | 1136768.9555 | 2646781.1504 | 1136768.9252 | 2646777.5282 | 1136769.7198 | 2646774.8262 | 1136772.8894
59 | 2646910.212 | 1136672.8649 | 2646905.3656 | 1136710.4244
60 | 2646905.3656 | 1136710.4244 | 2646985.1334 | 1136734.3452
61 | 2646988.8547 | 1136736.642 | 2646985.1334 | 1136734.3452
62 | 2646988.8547 | 1136736.642 | 2647002.6027 | 1136739.6949 | 2647011.9036 | 1136741.3176
63 | 2646910.212 | 1136672.8649 | 2646962.9319 | 1136586.9685
64 | 2646754.1186 | 1136793.273 | 2646751.7974 | 1136791.9877 | 2646751.2928 | 1136791.6327
65 | 2646754.1186 | 1136793.273 | 2646769.3935 | 1136801.9329
66 | 2646773.6725 | 1136774.837 | 2646764.3729 | 1136789.4726 | 2646760.7476 | 1136793.6467 | 2646757.1045 | 1136794.1743 | 2646754.1186 | 1136793.273
67 | 2646785.4099 | 1136811.0132 | 2646769.3935 | 1136801.9329
68 | 2646773.6725 | 1136774.837 | 2646776.5453 | 1136777.4272 | 2646781.6655 | 1136781.8914
69 | 2646773.6725 | 1136774.837 | 2646774.8262 | 1136772.8894

## bus_geodata
| x | y | coords
0 | 2647293.9603 | 1137138.4402
1 | 2647283.0384 | 1137134.0193
2 | 2647291.2841 | 1137144.0334
3 | 2647262.4716 | 1137127.4096
4 | 2647273.7179 | 1137161.0714
5 | 2647290.6566 | 1137172.0985
6 | 2647230.5961 | 1137126.8055
7 | 2647271.6297 | 1137190.9817
8 | 2647212.971 | 1137127.0953
9 | 2647204.973 | 1137125.4403
10 | 2647186.5246 | 1137117.9845
11 | 2647170.4359 | 1137109.6632
12 | 2647153.4798 | 1137097.8228
13 | 2647139.8677 | 1137086.9024
14 | 2647118.9483 | 1137069.7768
15 | 2647097.7835 | 1137052.3083
16 | 2647080.6088 | 1137040.638
17 | 2647066.2101 | 1137035.5092
18 | 2647037.3031 | 1137031.949
19 | 2647031.6824 | 1137047.3775
20 | 2647008.262 | 1137022.8609
21 | 2646990.6636 | 1137017.2745
22 | 2646963.9382 | 1137006.0066
23 | 2646948.267 | 1136990.6701
24 | 2646927.372 | 1136971.7165
25 | 2646922.3463 | 1136967.8779
26 | 2646916.5364 | 1136964.3622
27 | 2646875.6531 | 1136933.3867
28 | 2646821.5406 | 1136921.0164
29 | 2646812.5911 | 1136914.6907
30 | 2646844.5259 | 1136927.5232
31 | 2646909.8898 | 1136933.3078
32 | 2646861.9157 | 1136932.1644
33 | 2646796.9572 | 1136905.4624
34 | 2646912.05 | 1136929.556
35 | 2646875.8277 | 1136903.8163
36 | 2646873.3859 | 1136901.723
37 | 2646887.9889 | 1136914.2419
38 | 2646862.8859 | 1136892.7215
39 | 2646857.8225 | 1136888.3807
40 | 2646925.126 | 1136924.8692
41 | 2646850.3563 | 1136876.9853
42 | 2646845.2659 | 1136867.1206
43 | 2646785.1379 | 1136882.8815
44 | 2646740.7281 | 1136893.6686
45 | 2646846.1328 | 1136854.7444
46 | 2646832.1898 | 1136786.8741
47 | 2646973.3535 | 1136855.5003
48 | 2646968.0487 | 1136851.6841
49 | 2646966.7091 | 1136850.1875
50 | 2646949.5236 | 1136822.9233
51 | 2646952.0851 | 1136815.9749
52 | 2646813.0481 | 1136778.8995
53 | 2646882.2166 | 1136732.1981
54 | 2646809.4019 | 1136791.7335
55 | 2646809.8241 | 1136777.3579
56 | 2646894.6689 | 1136723.7239
57 | 2646793.4096 | 1136769.5093
58 | 2646905.3656 | 1136710.4244
59 | 2646985.1334 | 1136734.3452
60 | 2646988.8547 | 1136736.642
61 | 2647011.9036 | 1136741.3176
62 | 2646910.212 | 1136672.8649
63 | 2646962.9319 | 1136586.9685
64 | 2646751.2928 | 1136791.6327
65 | 2646754.1186 | 1136793.273
66 | 2646769.3935 | 1136801.9329
67 | 2646773.6725 | 1136774.837
68 | 2646785.4099 | 1136811.0132
69 | 2646781.6655 | 1136781.8914
70 | 2646774.8262 | 1136772.8894
71 | 2647037.3031 | 1137031.949

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1