## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6252-38_1_5_node_16 | 0.4 | n |  | TRUE
1 | bus_LV_6252-38_1_5_node_17 | 0.4 | n |  | TRUE
2 | bus_LV_6252-38_1_5_node_18 | 0.4 | n |  | TRUE
3 | bus_LV_6252-38_1_5_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_6252-38_1_5_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_6252-38_1_5_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_6252-38_1_5_node_78 | 0.4 | n |  | TRUE
7 | bus_LV_6252-38_1_5_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_6252-38_1_5_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_6252-38_1_5_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_6252-38_1_5_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_6252-38_1_5_node_26 | 0.4 | n |  | TRUE
12 | bus_LV_6252-38_1_5_node_72 | 0.4 | n |  | TRUE
13 | bus_LV_6252-38_1_5_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_6252-38_1_5_node_61 | 0.4 | n |  | TRUE
15 | bus_LV_6252-38_1_5_node_62 | 0.4 | n |  | TRUE
16 | bus_LV_6252-38_1_5_node_63 | 0.4 | n |  | TRUE
17 | bus_LV_6252-38_1_5_node_65 | 0.4 | n |  | TRUE
18 | bus_LV_6252-38_1_5_node_64 | 0.4 | n |  | TRUE
19 | bus_LV_6252-38_1_5_node_66 | 0.4 | n |  | TRUE
20 | bus_LV_6252-38_1_5_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_6252-38_1_5_node_67 | 0.4 | n |  | TRUE
22 | bus_LV_6252-38_1_5_node_68 | 0.4 | n |  | TRUE
23 | bus_LV_6252-38_1_5_node_69 | 0.4 | n |  | TRUE
24 | bus_LV_6252-38_1_5_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_6252-38_1_5_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_6252-38_1_5_node_73 | 0.4 | n |  | TRUE
27 | bus_LV_6252-38_1_5_node_86 | 0.4 | n |  | TRUE
28 | bus_LV_6252-38_1_5_node_75 | 0.4 | n |  | TRUE
29 | bus_LV_6252-38_1_5_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_6252-38_1_5_node_85 | 0.4 | n |  | TRUE
31 | bus_LV_6252-38_1_5_node_77 | 0.4 | n |  | TRUE
32 | bus_LV_6252-38_1_5_node_79 | 0.4 | n |  | TRUE
33 | bus_LV_6252-38_1_5_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_6252-38_1_5_node_81 | 0.4 | n |  | TRUE
35 | bus_LV_6252-38_1_5_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_6252-38_1_5_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_6252-38_1_5_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_6252-38_1_5_node_93 | 0.4 | n |  | TRUE
39 | bus_LV_6252-38_1_5_node_88 | 0.4 | n |  | TRUE
40 | bus_LV_6252-38_1_5_node_89 | 0.4 | n |  | TRUE
41 | bus_LV_6252-38_1_5_node_91 | 0.4 | n |  | TRUE
42 | bus_LV_6252-38_1_5_node_94 | 0.4 | n |  | TRUE
43 | bus_LV_6252-38_1_5_node_92 | 0.4 | n |  | TRUE
44 | bus_MV_0_node_80 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6252-38_1_5_load_16 | 0 | 0.00079008 | 0.00019801 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6252-38_1_5_load_17 | 1 | 0.00069148 | 0.0001733 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6252-38_1_5_load_19 | 3 | 0.00072479 | 0.00018165 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6252-38_1_5_load_21 | 5 | 0.00093677 | 0.00023478 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6252-38_1_5_load_78 | 6 | 0.00061824 | 0.00015495 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6252-38_1_5_load_22 | 7 | 0.0044837 | 0.0011237 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6252-38_1_5_load_23 | 8 | 0.00086404 | 0.00021655 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6252-38_1_5_load_26 | 11 | 0.0033725 | 0.00084523 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6252-38_1_5_load_72 | 12 | 0.0050059 | 0.0012546 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6252-38_1_5_load_60 | 13 | 0.0004751 | 0.00011907 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6252-38_1_5_load_61 | 14 | 0.0010289 | 0.00025786 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6252-38_1_5_load_62 | 15 | 0.00055309 | 0.00013862 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6252-38_1_5_load_63 | 16 | 0.00049814 | 0.00012485 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6252-38_1_5_load_64 | 18 | 0.00043146 | 0.00010813 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6252-38_1_5_load_66 | 19 | 0.00036839 | 9.2328e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6252-38_1_5_load_74 | 20 | 0.00072584 | 0.00018191 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6252-38_1_5_load_67 | 21 | 0.00060921 | 0.00015268 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6252-38_1_5_load_68 | 22 | 0.00080536 | 0.00020184 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6252-38_1_5_load_69 | 23 | 0.00069476 | 0.00017412 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6252-38_1_5_load_70 | 24 | 0.0010487 | 0.00026282 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6252-38_1_5_load_71 | 25 | 0.0010978 | 0.00027514 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6252-38_1_5_load_73 | 26 | 0.001529 | 0.00038319 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6252-38_1_5_load_86 | 27 | 0.0061696 | 0.0015463 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6252-38_1_5_load_75 | 28 | 0.00070515 | 0.00017673 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6252-38_1_5_load_76 | 29 | 0.003508 | 0.00087919 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6252-38_1_5_load_85 | 30 | 0.0031347 | 0.00078562 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6252-38_1_5_load_77 | 31 | 0.00074553 | 0.00018685 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6252-38_1_5_load_81 | 34 | 0.00079639 | 0.0001996 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6252-38_1_5_load_90 | 35 | 0.00059782 | 0.00014983 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6252-38_1_5_load_87 | 36 | 0.00070183 | 0.0001759 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6252-38_1_5_load_83 | 37 | 0.0010348 | 0.00025934 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6252-38_1_5_load_93 | 38 | 0.0034394 | 0.000862 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6252-38_1_5_load_88 | 39 | 0.00063905 | 0.00016016 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6252-38_1_5_load_89 | 40 | 0.00062647 | 0.00015701 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6252-38_1_5_load_91 | 41 | 0.00071996 | 0.00018044 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6252-38_1_5_load_94 | 42 | 0.00059612 | 0.0001494 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6252-38_1_5_load_92 | 43 | 0.00085368 | 0.00021395 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6252-38_1_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.013978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_6252-38_1_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_6252-38_1_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.040546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_6252-38_1_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_6252-38_1_5_line_4 | NAYY 4x150 SE | 3 | 5 | 0.062221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_6252-38_1_5_line_5 | NAYY 4x150 SE | 4 | 6 | 0.21683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_6252-38_1_5_line_6 | NAYY 4x150 SE | 5 | 7 | 0.019678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_6252-38_1_5_line_7 | NAYY 4x150 SE | 6 | 33 | 0.057247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_6252-38_1_5_line_8 | NAYY 4x150 SE | 6 | 31 | 0.013618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6252-38_1_5_line_9 | NAYY 4x150 SE | 7 | 8 | 0.092939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_6252-38_1_5_line_10 | NAYY 4x150 SE | 8 | 9 | 0.028463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_6252-38_1_5_line_11 | NAYY 4x150 SE | 9 | 10 | 0.065169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_6252-38_1_5_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0053292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6252-38_1_5_line_13 | NAYY 4x150 SE | 10 | 12 | 0.23272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_6252-38_1_5_line_14 | NAYY 4x150 SE | 12 | 15 | 0.13515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6252-38_1_5_line_15 | NAYY 4x150 SE | 12 | 25 | 0.037812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_6252-38_1_5_line_16 | NAYY 4x150 SE | 13 | 14 | 0.0039058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6252-38_1_5_line_17 | NAYY 4x150 SE | 13 | 15 | 0.023964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6252-38_1_5_line_18 | NAYY 4x150 SE | 14 | 16 | 0.041436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6252-38_1_5_line_19 | NAYY 4x150 SE | 16 | 17 | 0.050897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6252-38_1_5_line_20 | NAYY 4x150 SE | 17 | 18 | 0.11619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6252-38_1_5_line_21 | NAYY 4x150 SE | 19 | 20 | 0.12472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6252-38_1_5_line_22 | NAYY 4x150 SE | 20 | 28 | 0.081105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6252-38_1_5_line_23 | NAYY 4x150 SE | 20 | 24 | 0.06254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6252-38_1_5_line_24 | NAYY 4x150 SE | 21 | 22 | 0.056497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6252-38_1_5_line_25 | NAYY 4x150 SE | 21 | 23 | 0.062939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_6252-38_1_5_line_26 | NAYY 4x150 SE | 22 | 24 | 0.054428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6252-38_1_5_line_27 | NAYY 4x150 SE | 23 | 25 | 0.012397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_6252-38_1_5_line_28 | NAYY 4x150 SE | 26 | 27 | 0.11264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6252-38_1_5_line_29 | NAYY 4x150 SE | 27 | 38 | 0.020033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6252-38_1_5_line_30 | NAYY 4x150 SE | 27 | 30 | 0.016957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_6252-38_1_5_line_31 | NAYY 4x150 SE | 28 | 29 | 0.036577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_6252-38_1_5_line_32 | NAYY 4x150 SE | 29 | 30 | 0.092159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_6252-38_1_5_line_33 | NAYY 4x150 SE | 31 | 32 | 0.017098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6252-38_1_5_line_34 | NAYY 4x150 SE | 32 | 34 | 0.0079163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6252-38_1_5_line_35 | NAYY 4x150 SE | 33 | 35 | 0.038914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6252-38_1_5_line_36 | NAYY 4x150 SE | 33 | 36 | 0.0054957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6252-38_1_5_line_37 | NAYY 4x150 SE | 34 | 37 | 0.038567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_6252-38_1_5_line_38 | NAYY 4x150 SE | 35 | 42 | 0.019649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6252-38_1_5_line_39 | NAYY 4x150 SE | 36 | 39 | 0.01246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_6252-38_1_5_line_40 | NAYY 4x150 SE | 39 | 40 | 0.0050502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6252-38_1_5_line_41 | NAYY 4x150 SE | 40 | 41 | 0.01819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6252-38_1_5_line_42 | NAYY 4x150 SE | 41 | 43 | 0.023343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6252-38_1_5_trafo_80 | 0.25 MVA 20/0.4 kV | 44 | 33 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2611861.0954 | 1115061.1659 | 2611861.1272 | 1115062.2395 | 2611859.8726 | 1115075.0823
1 | 2611856.7105 | 1115090.1669 | 2611859.4335 | 1115079.5781 | 2611859.8726 | 1115075.0823
2 | 2611861.0954 | 1115061.1659 | 2611860.5694 | 1115043.3958 | 2611858.907 | 1115032.7206 | 2611860.2066 | 1115020.8276
3 | 2611856.7105 | 1115090.1669 | 2611841.7006 | 1115078.4542 | 2611841.3402 | 1115077.1973
4 | 2611869.1442 | 1114959.2899 | 2611868.3832 | 1114968.0627 | 2611864.1477 | 1114998.0471 | 2611860.8016 | 1115015.3824 | 2611860.2066 | 1115020.8276
5 | 2611653.6718 | 1115185.8022 | 2611841.3402 | 1115077.1973
6 | 2611869.1442 | 1114959.2899 | 2611869.6548 | 1114953.4024 | 2611868.2141 | 1114947.8302 | 2611862.2108 | 1114945.962 | 2611860.4874 | 1114945.8662
7 | 2611616.9813 | 1115180.294 | 2611624.3538 | 1115172.6598 | 2611639.2692 | 1115169.2866 | 2611648.2819 | 1115167.9588 | 2611654.5924 | 1115170.6611 | 2611655.2941 | 1115179.2222 | 2611653.6718 | 1115185.8022
8 | 2611650.4119 | 1115199.0242 | 2611653.6718 | 1115185.8022
9 | 2611860.4874 | 1114945.8662 | 2611835.8399 | 1114856.2554
10 | 2611839.2373 | 1114828.4261 | 2611840.5024 | 1114833.0308 | 2611835.8399 | 1114856.2554
11 | 2611801.3128 | 1114783.3747 | 2611802.5304 | 1114796.5836 | 2611808.0913 | 1114811.6685 | 2611818.3527 | 1114819.759 | 2611828.8744 | 1114824.9709 | 2611834.2155 | 1114825.9929 | 2611839.2373 | 1114828.4261
12 | 2611801.3128 | 1114783.3747 | 2611802.0796 | 1114778.101
13 | 2611584.9431 | 1114869.0766 | 2611801.3128 | 1114783.3747
14 | 2611584.9431 | 1114869.0766 | 2611455.0824 | 1114831.6378
15 | 2611584.9431 | 1114869.0766 | 2611585.9443 | 1114879.5977 | 2611585.2057 | 1114906.8315
16 | 2611431.5633 | 1114827.4325 | 2611427.8022 | 1114826.379
17 | 2611431.5633 | 1114827.4325 | 2611439.1271 | 1114829.5512 | 2611453.2068 | 1114831.6343 | 2611455.0824 | 1114831.6378
18 | 2611401.1015 | 1114798.0881 | 2611401.8179 | 1114804.8247 | 2611407.4767 | 1114813.5952 | 2611414.9157 | 1114820.0123 | 2611426.5018 | 1114826.0147 | 2611427.8022 | 1114826.379
19 | 2611368.1458 | 1114775.6252 | 2611371.9759 | 1114771.3413 | 2611377.7136 | 1114770.9518 | 2611384.5133 | 1114772.443 | 2611390.9221 | 1114776.4903 | 2611396.9262 | 1114782.3044 | 2611400.27 | 1114790.2702 | 2611401.1015 | 1114798.0881
20 | 2611368.1458 | 1114775.6252 | 2611366.6762 | 1114785.2605 | 2611365.4229 | 1114819.7196 | 2611365.5913 | 1114837.0285 | 2611363.5997 | 1114845.0843 | 2611359.4479 | 1114852.1578 | 2611349.759 | 1114863.9344 | 2611344.9987 | 1114874.3529 | 2611340.2462 | 1114884.7715
21 | 2611466.1815 | 1115112.2789 | 2611343.761 | 1115088.4252
22 | 2611466.1815 | 1115112.2789 | 2611459.7569 | 1115133.9623 | 2611458.6047 | 1115184.1849 | 2611458.1109 | 1115192.4237
23 | 2611492.7417 | 1115056.5941 | 2611483.2188 | 1115069.4191 | 2611475.4296 | 1115081.0657 | 2611466.1815 | 1115112.2789
24 | 2611558.2215 | 1114968.6817 | 2611537.4301 | 1114986.6251 | 2611527.388 | 1114997.2447 | 2611519.7837 | 1115009.4936
25 | 2611558.2215 | 1114968.6817 | 2611565.3334 | 1114962.5439 | 2611579.8002 | 1114951.6772 | 2611587.7637 | 1114941.9542 | 2611585.2636 | 1114919.208
26 | 2611519.7837 | 1115009.4936 | 2611502.1174 | 1115037.9504 | 2611494.9072 | 1115053.6778 | 2611492.7417 | 1115056.5941
27 | 2611585.2057 | 1114906.8315 | 2611584.9479 | 1114916.3362 | 2611585.2636 | 1114919.208
28 | 2611449.6248 | 1115337.8092 | 2611337.0197 | 1115335.1106
29 | 2611449.9272 | 1115357.7977 | 2611449.2705 | 1115352.4281 | 2611449.6248 | 1115337.8092
30 | 2611450.0355 | 1115320.8574 | 2611449.6248 | 1115337.8092
31 | 2611455.9223 | 1115228.9355 | 2611458.1109 | 1115192.4237
32 | 2611455.9223 | 1115228.9355 | 2611455.1134 | 1115242.4293 | 2611450.8608 | 1115286.7987 | 2611450.0355 | 1115320.8574
33 | 2611644.054 | 1115214.8071 | 2611647.8898 | 1115207.4886 | 2611649.9795 | 1115200.7782 | 2611650.4119 | 1115199.0242
34 | 2611644.054 | 1115214.8071 | 2611644.6589 | 1115222.7003
35 | 2611616.9813 | 1115180.294 | 2611598.4289 | 1115192.12 | 2611588.4921 | 1115205.8054
36 | 2611616.9813 | 1115180.294 | 2611615.2672 | 1115185.5156
37 | 2611647.6578 | 1115260.9208 | 2611648.3394 | 1115246.9089 | 2611645.4702 | 1115233.2856 | 2611644.6589 | 1115222.7003
38 | 2611588.4921 | 1115205.8054 | 2611586.9024 | 1115207.9948 | 2611584.2395 | 1115224.7276
39 | 2611615.2672 | 1115185.5156 | 2611612.7178 | 1115193.2812 | 2611612.2482 | 1115197.5418
40 | 2611611.6948 | 1115202.5616 | 2611612.2482 | 1115197.5418
41 | 2611611.6948 | 1115202.5616 | 2611609.9759 | 1115218.1549 | 2611609.4322 | 1115220.5977
42 | 2611604.7326 | 1115243.4528 | 2611605.5915 | 1115237.8562 | 2611609.4322 | 1115220.5977

## bus_geodata
| x | y | coords
0 | 2611859.8726 | 1115075.0823
1 | 2611861.0954 | 1115061.1659
2 | 2611856.7105 | 1115090.1669
3 | 2611860.2066 | 1115020.8276
4 | 2611841.3402 | 1115077.1973
5 | 2611869.1442 | 1114959.2899
6 | 2611653.6718 | 1115185.8022
7 | 2611860.4874 | 1114945.8662
8 | 2611835.8399 | 1114856.2554
9 | 2611839.2373 | 1114828.4261
10 | 2611801.3128 | 1114783.3747
11 | 2611802.0796 | 1114778.101
12 | 2611584.9431 | 1114869.0766
13 | 2611431.5633 | 1114827.4325
14 | 2611427.8022 | 1114826.379
15 | 2611455.0824 | 1114831.6378
16 | 2611401.1015 | 1114798.0881
17 | 2611368.1458 | 1114775.6252
18 | 2611340.2462 | 1114884.7715
19 | 2611343.761 | 1115088.4252
20 | 2611466.1815 | 1115112.2789
21 | 2611558.2215 | 1114968.6817
22 | 2611519.7837 | 1115009.4936
23 | 2611585.2636 | 1114919.208
24 | 2611492.7417 | 1115056.5941
25 | 2611585.2057 | 1114906.8315
26 | 2611337.0197 | 1115335.1106
27 | 2611449.6248 | 1115337.8092
28 | 2611458.1109 | 1115192.4237
29 | 2611455.9223 | 1115228.9355
30 | 2611450.0355 | 1115320.8574
31 | 2611650.4119 | 1115199.0242
32 | 2611644.054 | 1115214.8071
33 | 2611616.9813 | 1115180.294
34 | 2611644.6589 | 1115222.7003
35 | 2611588.4921 | 1115205.8054
36 | 2611615.2672 | 1115185.5156
37 | 2611647.6578 | 1115260.9208
38 | 2611449.9272 | 1115357.7977
39 | 2611612.2482 | 1115197.5418
40 | 2611611.6948 | 1115202.5616
41 | 2611609.4322 | 1115220.5977
42 | 2611584.2395 | 1115224.7276
43 | 2611604.7326 | 1115243.4528
44 | 2611616.9813 | 1115180.294

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1