## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6252-70_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6252-70_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6252-70_0_4_node_10 | 0.4 | n |  | TRUE
3 | bus_LV_6252-70_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6252-70_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_6252-70_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_6252-70_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_6252-70_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_6252-70_0_4_node_68 | 0.4 | n |  | TRUE
9 | bus_LV_6252-70_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_6252-70_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_6252-70_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_6252-70_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_6252-70_0_4_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_6252-70_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_6252-70_0_4_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_6252-70_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_6252-70_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_6252-70_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_6252-70_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_6252-70_0_4_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_6252-70_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_6252-70_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_6252-70_0_4_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_6252-70_0_4_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_6252-70_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_6252-70_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_6252-70_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_6252-70_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_6252-70_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_6252-70_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_6252-70_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_6252-70_0_4_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_6252-70_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_6252-70_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_6252-70_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_6252-70_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_6252-70_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_6252-70_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_6252-70_0_4_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_6252-70_0_4_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_6252-70_0_4_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_6252-70_0_4_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_6252-70_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_6252-70_0_4_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_6252-70_0_4_node_63 | 0.4 | n |  | TRUE
46 | bus_LV_6252-70_0_4_node_62 | 0.4 | n |  | TRUE
47 | bus_LV_6252-70_0_4_node_33 | 0.4 | n |  | TRUE
48 | bus_LV_6252-70_0_4_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_6252-70_0_4_node_57 | 0.4 | n |  | TRUE
50 | bus_LV_6252-70_0_4_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_6252-70_0_4_node_59 | 0.4 | n |  | TRUE
52 | bus_LV_6252-70_0_4_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_6252-70_0_4_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_6252-70_0_4_node_65 | 0.4 | n |  | TRUE
55 | bus_LV_6252-70_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_6252-70_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_6252-70_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_6252-70_0_4_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_6252-70_0_4_node_64 | 0.4 | n |  | TRUE
60 | bus_LV_6252-70_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_6252-70_0_4_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_6252-70_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_6252-70_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_6252-70_0_4_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_6252-70_0_4_node_66 | 0.4 | n |  | TRUE
66 | bus_LV_6252-70_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_MV_206_0_node_155 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6252-70_0_4_load_0 | 0 | 0.0048647 | 0.0012192 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6252-70_0_4_load_1 | 1 | 0.002155 | 0.0005401 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6252-70_0_4_load_10 | 2 | 0.0038615 | 0.00096779 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6252-70_0_4_load_7 | 6 | 0.011608 | 0.0029092 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6252-70_0_4_load_13 | 7 | 0.0036721 | 0.00092031 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6252-70_0_4_load_68 | 8 | 0.0050231 | 0.0012589 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6252-70_0_4_load_5 | 10 | 0.0067816 | 0.0016996 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6252-70_0_4_load_23 | 13 | 0.0082384 | 0.0020647 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6252-70_0_4_load_12 | 16 | 0.0059228 | 0.0014844 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6252-70_0_4_load_9 | 17 | 0.0091569 | 0.0022949 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6252-70_0_4_load_26 | 18 | 0.008781 | 0.0022007 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6252-70_0_4_load_37 | 20 | 0.0078039 | 0.0019559 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6252-70_0_4_load_21 | 21 | 0.0036977 | 0.00092673 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6252-70_0_4_load_27 | 23 | 0.0065003 | 0.0016291 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6252-70_0_4_load_38 | 24 | 0.0036864 | 0.0009239 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6252-70_0_4_load_16 | 26 | 0.0026406 | 0.0006618 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6252-70_0_4_load_18 | 28 | 0.0029394 | 0.00073668 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6252-70_0_4_load_19 | 29 | 0.0052547 | 0.001317 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6252-70_0_4_load_24 | 30 | 0.0063163 | 0.001583 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6252-70_0_4_load_35 | 31 | 0.0048256 | 0.0012094 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6252-70_0_4_load_36 | 32 | 0.0025904 | 0.00064923 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6252-70_0_4_load_28 | 33 | 0.0066153 | 0.0016579 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6252-70_0_4_load_29 | 34 | 0.0052801 | 0.0013233 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6252-70_0_4_load_30 | 35 | 0.0038234 | 0.00095823 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6252-70_0_4_load_31 | 36 | 0.0031251 | 0.00078322 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6252-70_0_4_load_51 | 37 | 0.0037679 | 0.00094433 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6252-70_0_4_load_32 | 38 | 0.0031175 | 0.00078133 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6252-70_0_4_load_52 | 39 | 0.0029509 | 0.00073958 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6252-70_0_4_load_53 | 41 | 0.0022714 | 0.00056926 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6252-70_0_4_load_54 | 42 | 0.0031189 | 0.00078167 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6252-70_0_4_load_55 | 43 | 0.0076551 | 0.0019185 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6252-70_0_4_load_63 | 45 | 0.002038 | 0.00051076 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6252-70_0_4_load_62 | 46 | 0.002335 | 0.00058521 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6252-70_0_4_load_33 | 47 | 0.0051695 | 0.0012956 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6252-70_0_4_load_34 | 48 | 0.012464 | 0.0031238 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6252-70_0_4_load_57 | 49 | 0.0045572 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6252-70_0_4_load_58 | 50 | 0.0022528 | 0.0005646 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6252-70_0_4_load_59 | 51 | 0.0049642 | 0.0012441 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6252-70_0_4_load_67 | 52 | 0.0031495 | 0.00078935 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6252-70_0_4_load_60 | 53 | 0.0035969 | 0.00090146 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6252-70_0_4_load_65 | 54 | 0.0024854 | 0.00062289 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6252-70_0_4_load_43 | 56 | 0.0063588 | 0.0015937 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6252-70_0_4_load_45 | 57 | 0.0033759 | 0.00084609 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6252-70_0_4_load_47 | 58 | 0.0022621 | 0.00056692 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6252-70_0_4_load_64 | 59 | 0.0018377 | 0.00046057 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6252-70_0_4_load_42 | 60 | 0.0037076 | 0.00092922 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6252-70_0_4_load_39 | 61 | 0.0045075 | 0.0011297 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6252-70_0_4_load_49 | 62 | 0.0045922 | 0.0011509 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6252-70_0_4_load_50 | 63 | 0.0061001 | 0.0015288 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6252-70_0_4_load_44 | 64 | 0.0037142 | 0.00093086 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6252-70_0_4_load_46 | 66 | 0.0045422 | 0.0011384 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6252-70_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0036799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_6252-70_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.072244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_6252-70_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.03947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_6252-70_0_4_line_3 | NAYY 4x150 SE | 2 | 6 | 0.041973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_6252-70_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.04189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_6252-70_0_4_line_5 | NAYY 4x150 SE | 3 | 4 | 0.007363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_6252-70_0_4_line_6 | NAYY 4x150 SE | 4 | 5 | 0.025314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_6252-70_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.11333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_6252-70_0_4_line_8 | NAYY 4x150 SE | 6 | 13 | 0.03917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_6252-70_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.016291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_6252-70_0_4_line_10 | NAYY 4x150 SE | 7 | 9 | 0.023176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_6252-70_0_4_line_11 | NAYY 4x150 SE | 9 | 25 | 0.051539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_6252-70_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0065805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_6252-70_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.00666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_6252-70_0_4_line_14 | NAYY 4x150 SE | 12 | 16 | 0.016003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_6252-70_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.026857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_6252-70_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0065292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_6252-70_0_4_line_17 | NAYY 4x150 SE | 14 | 18 | 0.013624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_6252-70_0_4_line_18 | NAYY 4x150 SE | 15 | 30 | 0.019427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_6252-70_0_4_line_19 | NAYY 4x150 SE | 15 | 21 | 0.037075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_6252-70_0_4_line_20 | NAYY 4x150 SE | 16 | 19 | 0.044955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_6252-70_0_4_line_21 | NAYY 4x150 SE | 17 | 18 | 0.041781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_6252-70_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.040646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_6252-70_0_4_line_23 | NAYY 4x150 SE | 19 | 23 | 0.054098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_6252-70_0_4_line_24 | NAYY 4x150 SE | 21 | 22 | 0.011269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_6252-70_0_4_line_25 | NAYY 4x150 SE | 22 | 29 | 0.013068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_6252-70_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0056914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_6252-70_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.0127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_6252-70_0_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.035012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_6252-70_0_4_line_29 | NAYY 4x150 SE | 27 | 28 | 0.0059683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_6252-70_0_4_line_30 | NAYY 4x150 SE | 30 | 31 | 0.10304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_6252-70_0_4_line_31 | NAYY 4x150 SE | 31 | 32 | 0.022523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_6252-70_0_4_line_32 | NAYY 4x150 SE | 32 | 61 | 0.07235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_6252-70_0_4_line_33 | NAYY 4x150 SE | 33 | 34 | 0.029831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_6252-70_0_4_line_34 | NAYY 4x150 SE | 33 | 35 | 0.014634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_6252-70_0_4_line_35 | NAYY 4x150 SE | 34 | 36 | 0.0024963 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_6252-70_0_4_line_36 | NAYY 4x150 SE | 34 | 37 | 0.061399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_6252-70_0_4_line_37 | NAYY 4x150 SE | 36 | 38 | 0.0010337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
38 | LV_6252-70_0_4_line_38 | NAYY 4x150 SE | 37 | 39 | 0.034041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_6252-70_0_4_line_39 | NAYY 4x150 SE | 38 | 47 | 0.047666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_6252-70_0_4_line_40 | NAYY 4x150 SE | 39 | 40 | 0.01316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_6252-70_0_4_line_41 | NAYY 4x150 SE | 40 | 46 | 0.016355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_6252-70_0_4_line_42 | NAYY 4x150 SE | 40 | 44 | 0.010538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_6252-70_0_4_line_43 | NAYY 4x150 SE | 41 | 42 | 0.019635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_6252-70_0_4_line_44 | NAYY 4x150 SE | 41 | 43 | 0.031354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_6252-70_0_4_line_45 | NAYY 4x150 SE | 42 | 44 | 0.0073991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_6252-70_0_4_line_46 | NAYY 4x150 SE | 44 | 45 | 0.0075231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_6252-70_0_4_line_47 | NAYY 4x150 SE | 47 | 48 | 0.013799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_6252-70_0_4_line_48 | NAYY 4x150 SE | 48 | 55 | 0.037685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_6252-70_0_4_line_49 | NAYY 4x150 SE | 48 | 56 | 0.034734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_6252-70_0_4_line_50 | NAYY 4x150 SE | 49 | 50 | 0.025804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_6252-70_0_4_line_51 | NAYY 4x150 SE | 50 | 51 | 0.0085528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_6252-70_0_4_line_52 | NAYY 4x150 SE | 50 | 52 | 0.06335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_6252-70_0_4_line_53 | NAYY 4x150 SE | 51 | 53 | 0.036907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_6252-70_0_4_line_54 | NAYY 4x150 SE | 52 | 54 | 0.03135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_6252-70_0_4_line_55 | NAYY 4x150 SE | 54 | 59 | 0.11628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_6252-70_0_4_line_56 | NAYY 4x150 SE | 55 | 60 | 0.0473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_6252-70_0_4_line_57 | NAYY 4x150 SE | 56 | 57 | 0.033179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_6252-70_0_4_line_58 | NAYY 4x150 SE | 57 | 58 | 0.027523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_6252-70_0_4_line_59 | NAYY 4x150 SE | 59 | 65 | 0.069046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_6252-70_0_4_line_60 | NAYY 4x150 SE | 60 | 64 | 0.036121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_6252-70_0_4_line_61 | NAYY 4x150 SE | 61 | 62 | 0.042741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_6252-70_0_4_line_62 | NAYY 4x150 SE | 62 | 63 | 0.027127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_6252-70_0_4_line_63 | NAYY 4x150 SE | 63 | 66 | 0.022456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_6252-70_0_4_line_64 | NAYY 4x150 SE | 64 | 66 | 0.024862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_6252-70_0_4_line_65 | NAYY 4x150 SE | 65 | 66 | 0.09629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6252-70_0_4_trafo_24 | 0.25 MVA 20/0.4 kV | 67 | 30 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2611241.1824 | 1118406.399 | 2611237.5544 | 1118407.0149
1 | 2611312.0418 | 1118420.4757 | 2611241.1824 | 1118406.399
2 | 2611206.918 | 1118382.5131 | 2611214.1035 | 1118386.028 | 2611237.5544 | 1118407.0149 | 2611237.5544 | 1118407.0149
3 | 2611302.3125 | 1118461.3058 | 2611312.0418 | 1118420.4757
4 | 2611206.918 | 1118382.5131 | 2611205.7816 | 1118387.8136 | 2611201.4163 | 1118411.6951 | 2611198.7646 | 1118423.5949
5 | 2611206.918 | 1118382.5131 | 2611208.4514 | 1118375.3123
6 | 2611208.4514 | 1118375.3123 | 2611210.6931 | 1118364.8335 | 2611215.5877 | 1118351.0802
7 | 2611167.4201 | 1118439.2128 | 2611176.7875 | 1118443.7211 | 2611182.1977 | 1118439.0621 | 2611189.0975 | 1118409.0822 | 2611200.1506 | 1118378.2096 | 2611210.6443 | 1118353.6168 | 2611215.5877 | 1118351.0802
8 | 2611333.1436 | 1118485.4672 | 2611302.3125 | 1118461.3058
9 | 2611302.3125 | 1118461.3058 | 2611292.0508 | 1118472.9925 | 2611291.4661 | 1118473.4434
10 | 2611193.2274 | 1118446.0747 | 2611194.6936 | 1118441.8642 | 2611198.7646 | 1118423.5949
11 | 2611169.6928 | 1118491.7095 | 2611169.7413 | 1118490.4867 | 2611184.0169 | 1118465.3672 | 2611190.8923 | 1118452.807 | 2611193.2274 | 1118446.0747
12 | 2611286.2551 | 1118477.4618 | 2611291.4661 | 1118473.4434
13 | 2611286.2551 | 1118477.4618 | 2611280.9771 | 1118481.5429
14 | 2611280.9771 | 1118481.5429 | 2611281.2275 | 1118492.1597 | 2611278.6707 | 1118496.8971
15 | 2611322.0776 | 1118509.5885 | 2611324.6212 | 1118506.9586 | 2611328.2681 | 1118496.1378 | 2611332.3064 | 1118486.4961 | 2611333.1436 | 1118485.4672
16 | 2611337.2641 | 1118480.4024 | 2611333.1436 | 1118485.4672
17 | 2611322.0776 | 1118509.5885 | 2611320.9901 | 1118513.4439 | 2611317.947 | 1118522.5674
18 | 2611337.2641 | 1118480.4024 | 2611336.7749 | 1118499.823
19 | 2611337.2641 | 1118480.4024 | 2611342.8705 | 1118461.6036 | 2611352.1223 | 1118446.7989
20 | 2611243.6133 | 1118523.3276 | 2611250.7234 | 1118521.6399 | 2611265.8988 | 1118510.7849 | 2611277.1159 | 1118499.778 | 2611278.6707 | 1118496.8971
21 | 2611317.947 | 1118522.5674 | 2611276.2508 | 1118525.2334
22 | 2611317.947 | 1118522.5674 | 2611316.6213 | 1118526.5422 | 2611312.0394 | 1118542.2081 | 2611307.8773 | 1118552.1052 | 2611303.4291 | 1118560.3824
23 | 2611273.8227 | 1118568.2052 | 2611243.6133 | 1118523.3276
24 | 2611358.0946 | 1118437.2422 | 2611352.1223 | 1118446.7989
25 | 2611358.0946 | 1118437.2422 | 2611363.192 | 1118438.9859 | 2611368.8413 | 1118434.4609 | 2611369.0782 | 1118434.0873
26 | 2611270.1674 | 1118572.5676 | 2611273.8227 | 1118568.2052
27 | 2611169.6928 | 1118491.7095 | 2611160.2522 | 1118493.4486 | 2611157.3397 | 1118494.5124
28 | 2611124.5003 | 1118506.6341 | 2611125.3963 | 1118506.1799 | 2611157.3397 | 1118494.5124
29 | 2611124.5003 | 1118506.6341 | 2611119.6362 | 1118503.1756
30 | 2611336.7749 | 1118499.823 | 2611335.9976 | 1118530.6803 | 2611323.9029 | 1118569.5213 | 2611310.0481 | 1118597.8029
31 | 2611300.1393 | 1118618.0296 | 2611310.0481 | 1118597.8029
32 | 2611300.1393 | 1118618.0296 | 2611281.7194 | 1118655.6298 | 2611270.5485 | 1118683.9891
33 | 2611383.4644 | 1118475.8193 | 2611382.0091 | 1118482.3201 | 2611383.2823 | 1118490.6043 | 2611387.0316 | 1118504.9093
34 | 2611388.4901 | 1118462.2112 | 2611385.0439 | 1118468.7636 | 2611383.4644 | 1118475.8193
35 | 2611387.0316 | 1118504.9093 | 2611387.55 | 1118506.887 | 2611387.678 | 1118507.3203
36 | 2611387.0316 | 1118504.9093 | 2611446.5042 | 1118489.6482
37 | 2611387.9709 | 1118508.3117 | 2611387.678 | 1118507.3203
38 | 2611446.5042 | 1118489.6482 | 2611452.5132 | 1118479.5398 | 2611459.4061 | 1118470.2815 | 2611465.8768 | 1118461.7111
39 | 2611387.9709 | 1118508.3117 | 2611389.8274 | 1118514.595 | 2611391.6723 | 1118522.4579 | 2611387.9191 | 1118536.4355 | 2611378.4503 | 1118549.1241 | 2611376.638 | 1118551.1691
40 | 2611472.901 | 1118450.6084 | 2611468.4494 | 1118458.3038 | 2611465.8768 | 1118461.7111
41 | 2611472.901 | 1118450.6084 | 2611475.2146 | 1118439.0404 | 2611476.0627 | 1118434.5621
42 | 2611472.901 | 1118450.6084 | 2611479.7761 | 1118442.6063
43 | 2611471.6109 | 1118468.0025 | 2611474.2514 | 1118462.8947 | 2611479.1203 | 1118449.8912
44 | 2611460.6363 | 1118497.2304 | 2611465.4214 | 1118480.4201 | 2611469.4805 | 1118472.1236 | 2611471.6109 | 1118468.0025
45 | 2611479.7761 | 1118442.6063 | 2611479.7501 | 1118448.209 | 2611479.1203 | 1118449.8912
46 | 2611479.7761 | 1118442.6063 | 2611484.678 | 1118436.8994
47 | 2611376.638 | 1118551.1691 | 2611373.2771 | 1118554.9617 | 2611369.155 | 1118562.6591
48 | 2611351.1473 | 1118595.7516 | 2611357.1853 | 1118585.48 | 2611366.0989 | 1118568.366 | 2611369.155 | 1118562.6591
49 | 2611369.155 | 1118562.6591 | 2611386.5541 | 1118592.7209
50 | 2611502.9027 | 1118555.9184 | 2611510.3223 | 1118542.7131 | 2611515.6237 | 1118533.4679
51 | 2611515.6237 | 1118533.4679 | 2611519.8783 | 1118526.0483
52 | 2611515.6237 | 1118533.4679 | 2611565.4696 | 1118572.5656
53 | 2611536.9884 | 1118493.4427 | 2611534.8283 | 1118498.8157 | 2611528.0727 | 1118512.9321 | 2611520.1857 | 1118525.5122 | 2611519.8783 | 1118526.0483
54 | 2611565.4696 | 1118572.5656 | 2611561.1834 | 1118594.735 | 2611556.2003 | 1118601.9514
55 | 2611462.228 | 1118666.8341 | 2611473.3132 | 1118653.5756 | 2611488.8679 | 1118638.0306 | 2611512.6996 | 1118619.9111 | 2611540.6635 | 1118607.9026 | 2611556.2003 | 1118601.9514 | 2611556.2003 | 1118601.9514
56 | 2611351.1473 | 1118595.7516 | 2611343.6791 | 1118607.4434 | 2611338.0834 | 1118616.4263 | 2611331.4792 | 1118624.1178 | 2611321.1563 | 1118631.5244
57 | 2611386.5541 | 1118592.7209 | 2611389.1543 | 1118589.764 | 2611401.7718 | 1118580.9389 | 2611412.668 | 1118572.3995 | 2611412.668 | 1118572.3995
58 | 2611412.668 | 1118572.3995 | 2611421.4215 | 1118562.5666 | 2611426.741 | 1118552.8607 | 2611427.5793 | 1118549.6786
59 | 2611420.7222 | 1118721.4545 | 2611435.2316 | 1118707.6527 | 2611442.1895 | 1118696.527 | 2611455.5796 | 1118674.7859 | 2611462.228 | 1118666.8341
60 | 2611321.1563 | 1118631.5244 | 2611354.6018 | 1118645.1686
61 | 2611270.5485 | 1118683.9891 | 2611308.6783 | 1118703.3005
62 | 2611308.6783 | 1118703.3005 | 2611309.1797 | 1118702.526 | 2611318.0712 | 1118692.9822 | 2611326.8851 | 1118683.2092
63 | 2611326.8851 | 1118683.2092 | 2611330.412 | 1118679.2985 | 2611341.743 | 1118666.372
64 | 2611341.743 | 1118666.372 | 2611343.9057 | 1118663.9049 | 2611353.2414 | 1118647.9367 | 2611354.6018 | 1118645.1686
65 | 2611341.743 | 1118666.372 | 2611420.7222 | 1118721.4545

## bus_geodata
| x | y | coords
0 | 2611241.1824 | 1118406.399
1 | 2611237.5544 | 1118407.0149
2 | 2611312.0418 | 1118420.4757
3 | 2611206.918 | 1118382.5131
4 | 2611208.4514 | 1118375.3123
5 | 2611215.5877 | 1118351.0802
6 | 2611302.3125 | 1118461.3058
7 | 2611198.7646 | 1118423.5949
8 | 2611167.4201 | 1118439.2128
9 | 2611193.2274 | 1118446.0747
10 | 2611291.4661 | 1118473.4434
11 | 2611286.2551 | 1118477.4618
12 | 2611280.9771 | 1118481.5429
13 | 2611333.1436 | 1118485.4672
14 | 2611322.0776 | 1118509.5885
15 | 2611337.2641 | 1118480.4024
16 | 2611278.6707 | 1118496.8971
17 | 2611276.2508 | 1118525.2334
18 | 2611317.947 | 1118522.5674
19 | 2611243.6133 | 1118523.3276
20 | 2611303.4291 | 1118560.3824
21 | 2611352.1223 | 1118446.7989
22 | 2611358.0946 | 1118437.2422
23 | 2611273.8227 | 1118568.2052
24 | 2611270.1674 | 1118572.5676
25 | 2611169.6928 | 1118491.7095
26 | 2611157.3397 | 1118494.5124
27 | 2611124.5003 | 1118506.6341
28 | 2611119.6362 | 1118503.1756
29 | 2611369.0782 | 1118434.0873
30 | 2611336.7749 | 1118499.823
31 | 2611310.0481 | 1118597.8029
32 | 2611300.1393 | 1118618.0296
33 | 2611383.4644 | 1118475.8193
34 | 2611387.0316 | 1118504.9093
35 | 2611388.4901 | 1118462.2112
36 | 2611387.678 | 1118507.3203
37 | 2611446.5042 | 1118489.6482
38 | 2611387.9709 | 1118508.3117
39 | 2611465.8768 | 1118461.7111
40 | 2611472.901 | 1118450.6084
41 | 2611471.6109 | 1118468.0025
42 | 2611479.1203 | 1118449.8912
43 | 2611460.6363 | 1118497.2304
44 | 2611479.7761 | 1118442.6063
45 | 2611484.678 | 1118436.8994
46 | 2611476.0627 | 1118434.5621
47 | 2611376.638 | 1118551.1691
48 | 2611369.155 | 1118562.6591
49 | 2611502.9027 | 1118555.9184
50 | 2611515.6237 | 1118533.4679
51 | 2611519.8783 | 1118526.0483
52 | 2611565.4696 | 1118572.5656
53 | 2611536.9884 | 1118493.4427
54 | 2611556.2003 | 1118601.9514
55 | 2611351.1473 | 1118595.7516
56 | 2611386.5541 | 1118592.7209
57 | 2611412.668 | 1118572.3995
58 | 2611427.5793 | 1118549.6786
59 | 2611462.228 | 1118666.8341
60 | 2611321.1563 | 1118631.5244
61 | 2611270.5485 | 1118683.9891
62 | 2611308.6783 | 1118703.3005
63 | 2611326.8851 | 1118683.2092
64 | 2611354.6018 | 1118645.1686
65 | 2611420.7222 | 1118721.4545
66 | 2611341.743 | 1118666.372
67 | 2611337.2641 | 1118480.4024

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1