## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_762-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_762-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_762-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_762-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_762-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_762-5_0_3_node_312 | 0.4 | n |  | TRUE
6 | bus_LV_762-5_0_3_node_293 | 0.4 | n |  | TRUE
7 | bus_LV_762-5_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_762-5_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_762-5_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_762-5_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_762-5_0_3_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_762-5_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_762-5_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_762-5_0_3_node_301 | 0.4 | n |  | TRUE
15 | bus_LV_762-5_0_3_node_306 | 0.4 | n |  | TRUE
16 | bus_LV_762-5_0_3_node_175 | 0.4 | n |  | TRUE
17 | bus_LV_762-5_0_3_node_313 | 0.4 | n |  | TRUE
18 | bus_LV_762-5_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_762-5_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_762-5_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_762-5_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_762-5_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_762-5_0_3_node_310 | 0.4 | n |  | TRUE
24 | bus_LV_762-5_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_762-5_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_762-5_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_762-5_0_3_node_286 | 0.4 | n |  | TRUE
28 | bus_LV_762-5_0_3_node_281 | 0.4 | n |  | TRUE
29 | bus_LV_762-5_0_3_node_295 | 0.4 | n |  | TRUE
30 | bus_LV_762-5_0_3_node_280 | 0.4 | n |  | TRUE
31 | bus_LV_762-5_0_3_node_277 | 0.4 | n |  | TRUE
32 | bus_LV_762-5_0_3_node_287 | 0.4 | n |  | TRUE
33 | bus_LV_762-5_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_762-5_0_3_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_762-5_0_3_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_762-5_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_762-5_0_3_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_762-5_0_3_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_762-5_0_3_node_282 | 0.4 | n |  | TRUE
40 | bus_LV_762-5_0_3_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_762-5_0_3_node_291 | 0.4 | n |  | TRUE
42 | bus_LV_762-5_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_762-5_0_3_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_762-5_0_3_node_149 | 0.4 | n |  | TRUE
45 | bus_LV_762-5_0_3_node_150 | 0.4 | n |  | TRUE
46 | bus_LV_762-5_0_3_node_151 | 0.4 | n |  | TRUE
47 | bus_LV_762-5_0_3_node_300 | 0.4 | n |  | TRUE
48 | bus_LV_762-5_0_3_node_292 | 0.4 | n |  | TRUE
49 | bus_LV_762-5_0_3_node_299 | 0.4 | n |  | TRUE
50 | bus_LV_762-5_0_3_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_762-5_0_3_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_762-5_0_3_node_302 | 0.4 | n |  | TRUE
53 | bus_LV_762-5_0_3_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_762-5_0_3_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_762-5_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_762-5_0_3_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_762-5_0_3_node_215 | 0.4 | n |  | TRUE
58 | bus_LV_762-5_0_3_node_214 | 0.4 | n |  | TRUE
59 | bus_LV_762-5_0_3_node_134 | 0.4 | n |  | TRUE
60 | bus_LV_762-5_0_3_node_133 | 0.4 | n |  | TRUE
61 | bus_LV_762-5_0_3_node_204 | 0.4 | n |  | TRUE
62 | bus_LV_762-5_0_3_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_762-5_0_3_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_762-5_0_3_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_762-5_0_3_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_762-5_0_3_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_762-5_0_3_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_762-5_0_3_node_275 | 0.4 | n |  | TRUE
69 | bus_LV_762-5_0_3_node_274 | 0.4 | n |  | TRUE
70 | bus_LV_762-5_0_3_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_762-5_0_3_node_270 | 0.4 | n |  | TRUE
72 | bus_LV_762-5_0_3_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_762-5_0_3_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_762-5_0_3_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_762-5_0_3_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_762-5_0_3_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_762-5_0_3_node_247 | 0.4 | n |  | TRUE
78 | bus_LV_762-5_0_3_node_88 | 0.4 | n |  | TRUE
79 | bus_LV_762-5_0_3_node_89 | 0.4 | n |  | TRUE
80 | bus_LV_762-5_0_3_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_762-5_0_3_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_762-5_0_3_node_50 | 0.4 | n |  | TRUE
83 | bus_LV_762-5_0_3_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_762-5_0_3_node_136 | 0.4 | n |  | TRUE
85 | bus_LV_762-5_0_3_node_279 | 0.4 | n |  | TRUE
86 | bus_LV_762-5_0_3_node_135 | 0.4 | n |  | TRUE
87 | bus_LV_762-5_0_3_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_762-5_0_3_node_244 | 0.4 | n |  | TRUE
89 | bus_LV_762-5_0_3_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_762-5_0_3_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_762-5_0_3_node_55 | 0.4 | n |  | TRUE
92 | bus_LV_762-5_0_3_node_56 | 0.4 | n |  | TRUE
93 | bus_LV_762-5_0_3_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_762-5_0_3_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_762-5_0_3_node_61 | 0.4 | n |  | TRUE
96 | bus_LV_762-5_0_3_node_62 | 0.4 | n |  | TRUE
97 | bus_LV_762-5_0_3_node_63 | 0.4 | n |  | TRUE
98 | bus_LV_762-5_0_3_node_64 | 0.4 | n |  | TRUE
99 | bus_LV_762-5_0_3_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_762-5_0_3_node_67 | 0.4 | n |  | TRUE
101 | bus_LV_762-5_0_3_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_762-5_0_3_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_762-5_0_3_node_309 | 0.4 | n |  | TRUE
104 | bus_LV_762-5_0_3_node_320 | 0.4 | n |  | TRUE
105 | bus_LV_762-5_0_3_node_253 | 0.4 | n |  | TRUE
106 | bus_LV_762-5_0_3_node_308 | 0.4 | n |  | TRUE
107 | bus_LV_762-5_0_3_node_69 | 0.4 | n |  | TRUE
108 | bus_LV_762-5_0_3_node_71 | 0.4 | n |  | TRUE
109 | bus_LV_762-5_0_3_node_74 | 0.4 | n |  | TRUE
110 | bus_LV_762-5_0_3_node_78 | 0.4 | n |  | TRUE
111 | bus_LV_762-5_0_3_node_79 | 0.4 | n |  | TRUE
112 | bus_LV_762-5_0_3_node_273 | 0.4 | n |  | TRUE
113 | bus_LV_762-5_0_3_node_271 | 0.4 | n |  | TRUE
114 | bus_LV_762-5_0_3_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_762-5_0_3_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_762-5_0_3_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_762-5_0_3_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_762-5_0_3_node_102 | 0.4 | n |  | TRUE
119 | bus_LV_762-5_0_3_node_314 | 0.4 | n |  | TRUE
120 | bus_LV_762-5_0_3_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_762-5_0_3_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_762-5_0_3_node_94 | 0.4 | n |  | TRUE
123 | bus_LV_762-5_0_3_node_96 | 0.4 | n |  | TRUE
124 | bus_LV_762-5_0_3_node_97 | 0.4 | n |  | TRUE
125 | bus_LV_762-5_0_3_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_762-5_0_3_node_122 | 0.4 | n |  | TRUE
127 | bus_LV_762-5_0_3_node_123 | 0.4 | n |  | TRUE
128 | bus_LV_762-5_0_3_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_762-5_0_3_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_762-5_0_3_node_126 | 0.4 | n |  | TRUE
131 | bus_LV_762-5_0_3_node_132 | 0.4 | n |  | TRUE
132 | bus_LV_762-5_0_3_node_146 | 0.4 | n |  | TRUE
133 | bus_LV_762-5_0_3_node_131 | 0.4 | n |  | TRUE
134 | bus_LV_762-5_0_3_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_762-5_0_3_node_127 | 0.4 | n |  | TRUE
136 | bus_LV_762-5_0_3_node_128 | 0.4 | n |  | TRUE
137 | bus_LV_762-5_0_3_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_762-5_0_3_node_147 | 0.4 | n |  | TRUE
139 | bus_LV_762-5_0_3_node_148 | 0.4 | n |  | TRUE
140 | bus_LV_762-5_0_3_node_252 | 0.4 | n |  | TRUE
141 | bus_LV_762-5_0_3_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_762-5_0_3_node_138 | 0.4 | n |  | TRUE
143 | bus_LV_762-5_0_3_node_139 | 0.4 | n |  | TRUE
144 | bus_LV_762-5_0_3_node_141 | 0.4 | n |  | TRUE
145 | bus_LV_762-5_0_3_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_762-5_0_3_node_143 | 0.4 | n |  | TRUE
147 | bus_LV_762-5_0_3_node_193 | 0.4 | n |  | TRUE
148 | bus_LV_762-5_0_3_node_203 | 0.4 | n |  | TRUE
149 | bus_LV_762-5_0_3_node_144 | 0.4 | n |  | TRUE
150 | bus_LV_762-5_0_3_node_194 | 0.4 | n |  | TRUE
151 | bus_LV_762-5_0_3_node_201 | 0.4 | n |  | TRUE
152 | bus_LV_762-5_0_3_node_145 | 0.4 | n |  | TRUE
153 | bus_LV_762-5_0_3_node_159 | 0.4 | n |  | TRUE
154 | bus_LV_762-5_0_3_node_158 | 0.4 | n |  | TRUE
155 | bus_LV_762-5_0_3_node_157 | 0.4 | n |  | TRUE
156 | bus_LV_762-5_0_3_node_152 | 0.4 | n |  | TRUE
157 | bus_LV_762-5_0_3_node_160 | 0.4 | n |  | TRUE
158 | bus_LV_762-5_0_3_node_161 | 0.4 | n |  | TRUE
159 | bus_LV_762-5_0_3_node_172 | 0.4 | n |  | TRUE
160 | bus_LV_762-5_0_3_node_169 | 0.4 | n |  | TRUE
161 | bus_LV_762-5_0_3_node_153 | 0.4 | n |  | TRUE
162 | bus_LV_762-5_0_3_node_154 | 0.4 | n |  | TRUE
163 | bus_LV_762-5_0_3_node_155 | 0.4 | n |  | TRUE
164 | bus_LV_762-5_0_3_node_156 | 0.4 | n |  | TRUE
165 | bus_LV_762-5_0_3_node_168 | 0.4 | n |  | TRUE
166 | bus_LV_762-5_0_3_node_163 | 0.4 | n |  | TRUE
167 | bus_LV_762-5_0_3_node_167 | 0.4 | n |  | TRUE
168 | bus_LV_762-5_0_3_node_184 | 0.4 | n |  | TRUE
169 | bus_LV_762-5_0_3_node_207 | 0.4 | n |  | TRUE
170 | bus_LV_762-5_0_3_node_162 | 0.4 | n |  | TRUE
171 | bus_LV_762-5_0_3_node_173 | 0.4 | n |  | TRUE
172 | bus_LV_762-5_0_3_node_206 | 0.4 | n |  | TRUE
173 | bus_LV_762-5_0_3_node_164 | 0.4 | n |  | TRUE
174 | bus_LV_762-5_0_3_node_165 | 0.4 | n |  | TRUE
175 | bus_LV_762-5_0_3_node_166 | 0.4 | n |  | TRUE
176 | bus_LV_762-5_0_3_node_170 | 0.4 | n |  | TRUE
177 | bus_LV_762-5_0_3_node_272 | 0.4 | n |  | TRUE
178 | bus_LV_762-5_0_3_node_294 | 0.4 | n |  | TRUE
179 | bus_LV_762-5_0_3_node_171 | 0.4 | n |  | TRUE
180 | bus_LV_762-5_0_3_node_205 | 0.4 | n |  | TRUE
181 | bus_LV_762-5_0_3_node_179 | 0.4 | n |  | TRUE
182 | bus_LV_762-5_0_3_node_208 | 0.4 | n |  | TRUE
183 | bus_LV_762-5_0_3_node_174 | 0.4 | n |  | TRUE
184 | bus_LV_762-5_0_3_node_187 | 0.4 | n |  | TRUE
185 | bus_LV_762-5_0_3_node_186 | 0.4 | n |  | TRUE
186 | bus_LV_762-5_0_3_node_176 | 0.4 | n |  | TRUE
187 | bus_LV_762-5_0_3_node_177 | 0.4 | n |  | TRUE
188 | bus_LV_762-5_0_3_node_178 | 0.4 | n |  | TRUE
189 | bus_LV_762-5_0_3_node_180 | 0.4 | n |  | TRUE
190 | bus_LV_762-5_0_3_node_185 | 0.4 | n |  | TRUE
191 | bus_LV_762-5_0_3_node_181 | 0.4 | n |  | TRUE
192 | bus_LV_762-5_0_3_node_182 | 0.4 | n |  | TRUE
193 | bus_LV_762-5_0_3_node_183 | 0.4 | n |  | TRUE
194 | bus_LV_762-5_0_3_node_210 | 0.4 | n |  | TRUE
195 | bus_LV_762-5_0_3_node_211 | 0.4 | n |  | TRUE
196 | bus_LV_762-5_0_3_node_209 | 0.4 | n |  | TRUE
197 | bus_LV_762-5_0_3_node_188 | 0.4 | n |  | TRUE
198 | bus_LV_762-5_0_3_node_189 | 0.4 | n |  | TRUE
199 | bus_LV_762-5_0_3_node_190 | 0.4 | n |  | TRUE
200 | bus_LV_762-5_0_3_node_191 | 0.4 | n |  | TRUE
201 | bus_LV_762-5_0_3_node_192 | 0.4 | n |  | TRUE
202 | bus_LV_762-5_0_3_node_195 | 0.4 | n |  | TRUE
203 | bus_LV_762-5_0_3_node_283 | 0.4 | n |  | TRUE
204 | bus_LV_762-5_0_3_node_196 | 0.4 | n |  | TRUE
205 | bus_LV_762-5_0_3_node_284 | 0.4 | n |  | TRUE
206 | bus_LV_762-5_0_3_node_212 | 0.4 | n |  | TRUE
207 | bus_LV_762-5_0_3_node_197 | 0.4 | n |  | TRUE
208 | bus_LV_762-5_0_3_node_198 | 0.4 | n |  | TRUE
209 | bus_LV_762-5_0_3_node_199 | 0.4 | n |  | TRUE
210 | bus_LV_762-5_0_3_node_200 | 0.4 | n |  | TRUE
211 | bus_LV_762-5_0_3_node_202 | 0.4 | n |  | TRUE
212 | bus_LV_762-5_0_3_node_242 | 0.4 | n |  | TRUE
213 | bus_LV_762-5_0_3_node_243 | 0.4 | n |  | TRUE
214 | bus_LV_762-5_0_3_node_245 | 0.4 | n |  | TRUE
215 | bus_LV_762-5_0_3_node_246 | 0.4 | n |  | TRUE
216 | bus_LV_762-5_0_3_node_285 | 0.4 | n |  | TRUE
217 | bus_LV_762-5_0_3_node_288 | 0.4 | n |  | TRUE
218 | bus_LV_762-5_0_3_node_289 | 0.4 | n |  | TRUE
219 | bus_LV_762-5_0_3_node_290 | 0.4 | n |  | TRUE
220 | bus_MV_208_0_node_209 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_762-5_0_3_load_0 | 0 | 0.0005119 | 0.00012829 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_762-5_0_3_load_1 | 1 | 0.00047502 | 0.00011905 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_762-5_0_3_load_4 | 4 | 0.00072368 | 0.00018137 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_762-5_0_3_load_312 | 5 | 0.00046272 | 0.00011597 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_762-5_0_3_load_5 | 8 | 0.00046309 | 0.00011606 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_762-5_0_3_load_14 | 11 | 0.00052982 | 0.00013278 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_762-5_0_3_load_6 | 12 | 0.00061111 | 0.00015316 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_762-5_0_3_load_306 | 15 | 0.00045479 | 0.00011398 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_762-5_0_3_load_175 | 16 | 0.0013835 | 0.00034675 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_762-5_0_3_load_313 | 17 | 0.00038045 | 9.5349e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_762-5_0_3_load_15 | 18 | 0.00062833 | 0.00015747 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_762-5_0_3_load_8 | 19 | 0.00055751 | 0.00013972 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_762-5_0_3_load_310 | 23 | 0.00055522 | 0.00013915 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_762-5_0_3_load_19 | 25 | 0.0005663 | 0.00014193 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_762-5_0_3_load_17 | 26 | 0.00036512 | 9.1507e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_762-5_0_3_load_286 | 27 | 0.00094719 | 0.00023739 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_762-5_0_3_load_295 | 29 | 0.00027401 | 6.8673e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_762-5_0_3_load_280 | 30 | 0.00020863 | 5.2286e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_762-5_0_3_load_277 | 31 | 0.0012846 | 0.00032194 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_762-5_0_3_load_287 | 32 | 0.0039566 | 0.00099163 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_762-5_0_3_load_26 | 33 | 0.0014532 | 0.00036421 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_762-5_0_3_load_27 | 34 | 0.00025494 | 6.3894e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_762-5_0_3_load_29 | 36 | 0.00023446 | 5.876e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_762-5_0_3_load_282 | 39 | 0.00052038 | 0.00013042 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_762-5_0_3_load_291 | 41 | 0.00024449 | 6.1276e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_762-5_0_3_load_35 | 42 | 0.00076421 | 0.00019153 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_762-5_0_3_load_32 | 43 | 0.00066688 | 0.00016714 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_762-5_0_3_load_149 | 44 | 0.00082537 | 0.00020686 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_762-5_0_3_load_150 | 45 | 0.00053215 | 0.00013337 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_762-5_0_3_load_151 | 46 | 0.00087065 | 0.00021821 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_762-5_0_3_load_300 | 47 | 0.0006988 | 0.00017514 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_762-5_0_3_load_292 | 48 | 0.0015276 | 0.00038284 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_762-5_0_3_load_299 | 49 | 0.000122 | 3.0577e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_762-5_0_3_load_33 | 50 | 0.00036755 | 9.2116e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_762-5_0_3_load_302 | 52 | 0.00066831 | 0.00016749 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_762-5_0_3_load_41 | 55 | 0.00016919 | 4.2403e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_762-5_0_3_load_37 | 56 | 0.00010011 | 2.5091e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_762-5_0_3_load_215 | 57 | 0.0001182 | 2.9623e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_762-5_0_3_load_214 | 58 | 0.00040183 | 0.00010071 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_762-5_0_3_load_134 | 59 | 0.00023429 | 5.8718e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_762-5_0_3_load_133 | 60 | 0.00057148 | 0.00014323 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_762-5_0_3_load_204 | 61 | 0.00011424 | 2.863e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_762-5_0_3_load_43 | 62 | 0.00020557 | 5.1521e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_762-5_0_3_load_44 | 63 | 0.00011742 | 2.9429e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_762-5_0_3_load_48 | 67 | 0.00017103 | 4.2865e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_762-5_0_3_load_275 | 68 | 8.5546e-05 | 2.144e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_762-5_0_3_load_274 | 69 | 0.00051999 | 0.00013032 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_762-5_0_3_load_103 | 70 | 0.00045593 | 0.00011427 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_762-5_0_3_load_270 | 71 | 0.0020834 | 0.00052215 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_762-5_0_3_load_75 | 74 | 0.00019835 | 4.971e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_762-5_0_3_load_73 | 75 | 0.00028023 | 7.0233e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_762-5_0_3_load_49 | 76 | 0.00012369 | 3.1001e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_762-5_0_3_load_247 | 77 | 0.00027906 | 6.9939e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_762-5_0_3_load_88 | 78 | 0.00042921 | 0.00010757 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_762-5_0_3_load_89 | 79 | 0.00016081 | 4.0302e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_762-5_0_3_load_86 | 80 | 0.00017652 | 4.424e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_762-5_0_3_load_50 | 82 | 7.3147e-05 | 1.8332e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_762-5_0_3_load_54 | 83 | 7.9446e-05 | 1.9911e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_762-5_0_3_load_135 | 86 | 0.0001123 | 2.8145e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_762-5_0_3_load_53 | 87 | 7.8379e-05 | 1.9644e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_762-5_0_3_load_90 | 89 | 0.00017005 | 4.2617e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_762-5_0_3_load_55 | 91 | 0.00017397 | 4.36e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_762-5_0_3_load_56 | 92 | 7.6609e-05 | 1.92e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_762-5_0_3_load_77 | 93 | 0.00021497 | 5.3876e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_762-5_0_3_load_76 | 94 | 0.0003174 | 7.9549e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_762-5_0_3_load_61 | 95 | 7.4518e-05 | 1.8676e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_762-5_0_3_load_62 | 96 | 0.00038306 | 9.6004e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_762-5_0_3_load_66 | 99 | 0.00020641 | 5.1732e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_762-5_0_3_load_87 | 102 | 0.00033269 | 8.3379e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_762-5_0_3_load_309 | 103 | 0.00012081 | 3.0278e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_762-5_0_3_load_320 | 104 | 0.00016499 | 4.1349e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_762-5_0_3_load_308 | 106 | 0.00016165 | 4.0513e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_762-5_0_3_load_69 | 107 | 0.00016994 | 4.259e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_762-5_0_3_load_74 | 109 | 7.4261e-05 | 1.8612e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_762-5_0_3_load_79 | 111 | 9.5376e-05 | 2.3903e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_762-5_0_3_load_273 | 112 | 0.00020047 | 5.0243e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_762-5_0_3_load_271 | 113 | 0.0013288 | 0.00033304 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_762-5_0_3_load_93 | 116 | 0.00018973 | 4.7551e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_762-5_0_3_load_102 | 118 | 0.00017741 | 4.4463e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_762-5_0_3_load_314 | 119 | 0.0002206 | 5.5288e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_762-5_0_3_load_101 | 121 | 0.000225 | 5.6389e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_762-5_0_3_load_94 | 122 | 0.00010302 | 2.5818e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_762-5_0_3_load_97 | 124 | 0.00026512 | 6.6446e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_762-5_0_3_load_99 | 125 | 0.00015047 | 3.7712e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_762-5_0_3_load_122 | 126 | 0.00034346 | 8.608e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_762-5_0_3_load_123 | 127 | 0.00042582 | 0.00010672 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_762-5_0_3_load_124 | 128 | 0.00015595 | 3.9085e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_762-5_0_3_load_125 | 129 | 0.00048263 | 0.00012096 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_762-5_0_3_load_126 | 130 | 0.00015633 | 3.9181e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_762-5_0_3_load_132 | 131 | 0.00045871 | 0.00011496 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_762-5_0_3_load_146 | 132 | 0.00013671 | 3.4263e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_762-5_0_3_load_131 | 133 | 0.00084768 | 0.00021245 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_762-5_0_3_load_127 | 135 | 0.00061072 | 0.00015306 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_762-5_0_3_load_130 | 137 | 0.00030157 | 7.5579e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_762-5_0_3_load_147 | 138 | 0.00027463 | 6.883e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_762-5_0_3_load_252 | 140 | 8.0915e-05 | 2.0279e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_762-5_0_3_load_137 | 141 | 0.00035845 | 8.9837e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_762-5_0_3_load_138 | 142 | 0.00025223 | 6.3214e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_762-5_0_3_load_141 | 144 | 0.00016643 | 4.171e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_762-5_0_3_load_142 | 145 | 0.0004556 | 0.00011418 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_762-5_0_3_load_143 | 146 | 0.0015711 | 0.00039376 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_762-5_0_3_load_193 | 147 | 0.00077282 | 0.00019369 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_762-5_0_3_load_203 | 148 | 0.0001957 | 4.9046e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_762-5_0_3_load_144 | 149 | 0.00022973 | 5.7575e-05 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_762-5_0_3_load_194 | 150 | 0.00044386 | 0.00011124 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_762-5_0_3_load_201 | 151 | 0.00018165 | 4.5526e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_762-5_0_3_load_159 | 153 | 0.00039725 | 9.956e-05 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_762-5_0_3_load_158 | 154 | 0.00017162 | 4.3013e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_762-5_0_3_load_157 | 155 | 0.0003946 | 9.8895e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_762-5_0_3_load_172 | 159 | 0.00080391 | 0.00020148 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_762-5_0_3_load_169 | 160 | 0.0007857 | 0.00019691 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_762-5_0_3_load_153 | 161 | 0.00045475 | 0.00011397 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_762-5_0_3_load_154 | 162 | 0.0018455 | 0.00046252 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_762-5_0_3_load_155 | 163 | 0.0014016 | 0.00035128 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_762-5_0_3_load_168 | 165 | 0.00032895 | 8.2442e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_762-5_0_3_load_163 | 166 | 0.0025759 | 0.00064558 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_762-5_0_3_load_167 | 167 | 0.0013282 | 0.00033287 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_762-5_0_3_load_207 | 169 | 0.00051481 | 0.00012902 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_762-5_0_3_load_162 | 170 | 0.00098655 | 0.00024725 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_762-5_0_3_load_173 | 171 | 0.0012328 | 0.00030896 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_762-5_0_3_load_206 | 172 | 0.00039373 | 9.8678e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_762-5_0_3_load_165 | 174 | 0.0012046 | 0.00030191 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_762-5_0_3_load_170 | 176 | 0.00036558 | 9.1624e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_762-5_0_3_load_272 | 177 | 0.00012523 | 3.1386e-05 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_762-5_0_3_load_294 | 178 | 0.00025281 | 6.3359e-05 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_762-5_0_3_load_171 | 179 | 0.0016376 | 0.00041043 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_762-5_0_3_load_205 | 180 | 0.00032285 | 8.0914e-05 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_762-5_0_3_load_179 | 181 | 0.00052285 | 0.00013104 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_762-5_0_3_load_174 | 183 | 0.00083613 | 0.00020955 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_762-5_0_3_load_186 | 185 | 0.00058879 | 0.00014757 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_762-5_0_3_load_176 | 186 | 0.00086268 | 0.00021621 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_762-5_0_3_load_177 | 187 | 0.0005207 | 0.0001305 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_762-5_0_3_load_178 | 188 | 0.00041638 | 0.00010436 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_762-5_0_3_load_180 | 189 | 0.00077839 | 0.00019508 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_762-5_0_3_load_185 | 190 | 0.00039697 | 9.9489e-05 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_762-5_0_3_load_181 | 191 | 0.00072829 | 0.00018253 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_762-5_0_3_load_182 | 192 | 0.0013775 | 0.00034524 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_762-5_0_3_load_210 | 194 | 0.0015346 | 0.0003846 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_762-5_0_3_load_209 | 196 | 0.00037898 | 9.4982e-05 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_762-5_0_3_load_188 | 197 | 0.00076347 | 0.00019134 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_762-5_0_3_load_189 | 198 | 0.0018759 | 0.00047014 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_762-5_0_3_load_190 | 199 | 0.00075799 | 0.00018997 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_762-5_0_3_load_191 | 200 | 0.0012699 | 0.00031826 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_762-5_0_3_load_192 | 201 | 0.00088267 | 0.00022122 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_762-5_0_3_load_195 | 202 | 0.0012574 | 0.00031515 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_762-5_0_3_load_283 | 203 | 0.0018798 | 0.00047111 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_762-5_0_3_load_196 | 204 | 0.0016525 | 0.00041416 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_762-5_0_3_load_284 | 205 | 0.0015479 | 0.00038793 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_762-5_0_3_load_212 | 206 | 0.00010757 | 2.6961e-05 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_762-5_0_3_load_197 | 207 | 0.00099029 | 0.00024819 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_762-5_0_3_load_198 | 208 | 0.0018518 | 0.00046411 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_762-5_0_3_load_199 | 209 | 0.0017807 | 0.00044628 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_762-5_0_3_load_200 | 210 | 0.00032309 | 8.0975e-05 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_762-5_0_3_load_202 | 211 | 0.0001482 | 3.7142e-05 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_762-5_0_3_load_242 | 212 | 9.9188e-05 | 2.4859e-05 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_762-5_0_3_load_243 | 213 | 8.2399e-05 | 2.0651e-05 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_762-5_0_3_load_245 | 214 | 0.00021964 | 5.5047e-05 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_762-5_0_3_load_246 | 215 | 0.00059956 | 0.00015026 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_762-5_0_3_load_285 | 216 | 0.00075622 | 0.00018953 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_762-5_0_3_load_288 | 217 | 0.0012068 | 0.00030246 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_762-5_0_3_load_290 | 219 | 0.00099865 | 0.00025029 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 184 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_762-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.11363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_762-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.016118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_762-5_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.063771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_762-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.079439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_762-5_0_3_line_4 | NAYY 4x150 SE | 3 | 7 | 0.09579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_762-5_0_3_line_5 | NAYY 4x150 SE | 3 | 8 | 0.062831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_762-5_0_3_line_6 | NAYY 4x150 SE | 4 | 9 | 0.34602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_762-5_0_3_line_7 | NAYY 4x150 SE | 5 | 6 | 0.23018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_762-5_0_3_line_8 | NAYY 4x150 SE | 6 | 48 | 0.29025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_762-5_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.35277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_762-5_0_3_line_10 | NAYY 4x150 SE | 7 | 11 | 0.1708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_762-5_0_3_line_11 | NAYY 4x150 SE | 8 | 12 | 0.02325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_762-5_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.31555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_762-5_0_3_line_13 | NAYY 4x150 SE | 10 | 17 | 0.072055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_762-5_0_3_line_14 | NAYY 4x150 SE | 11 | 18 | 0.046142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_762-5_0_3_line_15 | NAYY 4x150 SE | 13 | 27 | 0.55458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_762-5_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.24585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_762-5_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.19474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_762-5_0_3_line_18 | NAYY 4x150 SE | 15 | 40 | 0.089003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_762-5_0_3_line_19 | NAYY 4x150 SE | 16 | 157 | 0.038496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_762-5_0_3_line_20 | NAYY 4x150 SE | 18 | 22 | 0.075402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_762-5_0_3_line_21 | NAYY 4x150 SE | 19 | 20 | 0.029114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_762-5_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.005274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_762-5_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.034589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_762-5_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.029045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_762-5_0_3_line_25 | NAYY 4x150 SE | 21 | 24 | 0.042501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_762-5_0_3_line_26 | NAYY 4x150 SE | 22 | 25 | 0.049126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_762-5_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.0085304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_762-5_0_3_line_28 | NAYY 4x150 SE | 27 | 30 | 0.60847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_762-5_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.17248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_762-5_0_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.13746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_762-5_0_3_line_31 | NAYY 4x150 SE | 29 | 47 | 0.15042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_762-5_0_3_line_32 | NAYY 4x150 SE | 31 | 32 | 0.21803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_762-5_0_3_line_33 | NAYY 4x150 SE | 32 | 217 | 0.08534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_762-5_0_3_line_34 | NAYY 4x150 SE | 32 | 216 | 0.024669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_762-5_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.34766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_762-5_0_3_line_36 | NAYY 4x150 SE | 33 | 35 | 0.083745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_762-5_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.0097409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_762-5_0_3_line_38 | NAYY 4x150 SE | 35 | 37 | 0.23815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_762-5_0_3_line_39 | NAYY 4x150 SE | 35 | 38 | 0.007262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_762-5_0_3_line_40 | NAYY 4x150 SE | 36 | 39 | 0.01683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_762-5_0_3_line_41 | NAYY 4x150 SE | 37 | 40 | 0.054897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_762-5_0_3_line_42 | NAYY 4x150 SE | 37 | 41 | 0.1881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_762-5_0_3_line_43 | NAYY 4x150 SE | 38 | 42 | 0.060022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_762-5_0_3_line_44 | NAYY 4x150 SE | 38 | 43 | 0.03937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_762-5_0_3_line_45 | NAYY 4x150 SE | 39 | 47 | 2.693e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_762-5_0_3_line_46 | NAYY 4x150 SE | 41 | 48 | 0.16866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_762-5_0_3_line_47 | NAYY 4x150 SE | 42 | 49 | 0.085053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_762-5_0_3_line_48 | NAYY 4x150 SE | 43 | 50 | 0.048437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_762-5_0_3_line_49 | NAYY 4x150 SE | 44 | 45 | 0.063588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_762-5_0_3_line_50 | NAYY 4x150 SE | 44 | 46 | 0.0020092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_762-5_0_3_line_51 | NAYY 4x150 SE | 45 | 156 | 0.0056463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_762-5_0_3_line_52 | NAYY 4x150 SE | 46 | 59 | 0.0012887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_762-5_0_3_line_53 | NAYY 4x150 SE | 49 | 55 | 0.024425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_762-5_0_3_line_54 | NAYY 4x150 SE | 51 | 52 | 0.07986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_762-5_0_3_line_55 | NAYY 4x150 SE | 51 | 53 | 0.008377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_762-5_0_3_line_56 | NAYY 4x150 SE | 53 | 56 | 0.024834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_762-5_0_3_line_57 | NAYY 4x150 SE | 54 | 55 | 0.092335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_762-5_0_3_line_58 | NAYY 4x150 SE | 54 | 56 | 0.055698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_762-5_0_3_line_59 | NAYY 4x150 SE | 57 | 58 | 0.0083747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_762-5_0_3_line_60 | NAYY 4x150 SE | 58 | 61 | 0.036861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_762-5_0_3_line_61 | NAYY 4x150 SE | 59 | 60 | 0.039601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_762-5_0_3_line_62 | NAYY 4x150 SE | 60 | 133 | 0.038396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_762-5_0_3_line_63 | NAYY 4x150 SE | 61 | 211 | 0.0082899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_762-5_0_3_line_64 | NAYY 4x150 SE | 62 | 63 | 0.021247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_762-5_0_3_line_65 | NAYY 4x150 SE | 62 | 64 | 0.18196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_762-5_0_3_line_66 | NAYY 4x150 SE | 63 | 65 | 0.047958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_762-5_0_3_line_67 | NAYY 4x150 SE | 64 | 66 | 0.011698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_762-5_0_3_line_68 | NAYY 4x150 SE | 64 | 67 | 0.0023936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_762-5_0_3_line_69 | NAYY 4x150 SE | 65 | 72 | 0.011539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_762-5_0_3_line_70 | NAYY 4x150 SE | 65 | 73 | 0.27336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_762-5_0_3_line_71 | NAYY 4x150 SE | 66 | 74 | 0.014696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_762-5_0_3_line_72 | NAYY 4x150 SE | 66 | 75 | 0.05359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_762-5_0_3_line_73 | NAYY 4x150 SE | 67 | 76 | 0.031062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_762-5_0_3_line_74 | NAYY 4x150 SE | 68 | 69 | 0.083316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_762-5_0_3_line_75 | NAYY 4x150 SE | 68 | 70 | 0.22016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_762-5_0_3_line_76 | NAYY 4x150 SE | 68 | 71 | 0.19388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_762-5_0_3_line_77 | NAYY 4x150 SE | 70 | 121 | 0.0093679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_762-5_0_3_line_78 | NAYY 4x150 SE | 71 | 195 | 0.096356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_762-5_0_3_line_79 | NAYY 4x150 SE | 72 | 77 | 0.22569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_762-5_0_3_line_80 | NAYY 4x150 SE | 73 | 78 | 0.071384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_762-5_0_3_line_81 | NAYY 4x150 SE | 73 | 79 | 0.13517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_762-5_0_3_line_82 | NAYY 4x150 SE | 73 | 80 | 0.12467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_762-5_0_3_line_83 | NAYY 4x150 SE | 75 | 81 | 0.11058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_762-5_0_3_line_84 | NAYY 4x150 SE | 76 | 82 | 0.0203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_762-5_0_3_line_85 | NAYY 4x150 SE | 77 | 88 | 0.0088073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_762-5_0_3_line_86 | NAYY 4x150 SE | 79 | 89 | 0.019983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_762-5_0_3_line_87 | NAYY 4x150 SE | 80 | 90 | 0.083984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_762-5_0_3_line_88 | NAYY 4x150 SE | 81 | 107 | 0.019609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_762-5_0_3_line_89 | NAYY 4x150 SE | 82 | 83 | 0.15984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_762-5_0_3_line_90 | NAYY 4x150 SE | 83 | 87 | 0.02428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_762-5_0_3_line_91 | NAYY 4x150 SE | 84 | 85 | 0.2167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_762-5_0_3_line_92 | NAYY 4x150 SE | 84 | 86 | 0.2581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_762-5_0_3_line_93 | NAYY 4x150 SE | 85 | 106 | 0.022867 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_762-5_0_3_line_94 | NAYY 4x150 SE | 85 | 100 | 0.17033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_762-5_0_3_line_95 | NAYY 4x150 SE | 87 | 91 | 0.098826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_762-5_0_3_line_96 | NAYY 4x150 SE | 88 | 212 | 0.0091402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_762-5_0_3_line_97 | NAYY 4x150 SE | 89 | 114 | 0.062481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_762-5_0_3_line_98 | NAYY 4x150 SE | 90 | 102 | 0.049352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_762-5_0_3_line_99 | NAYY 4x150 SE | 90 | 97 | 0.23277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_762-5_0_3_line_100 | NAYY 4x150 SE | 91 | 92 | 0.11327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_762-5_0_3_line_101 | NAYY 4x150 SE | 92 | 93 | 0.070597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_762-5_0_3_line_102 | NAYY 4x150 SE | 93 | 94 | 0.02497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_762-5_0_3_line_103 | NAYY 4x150 SE | 94 | 110 | 0.122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_762-5_0_3_line_104 | NAYY 4x150 SE | 95 | 96 | 0.019248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_762-5_0_3_line_105 | NAYY 4x150 SE | 95 | 97 | 0.072449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_762-5_0_3_line_106 | NAYY 4x150 SE | 96 | 98 | 0.083483 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_762-5_0_3_line_107 | NAYY 4x150 SE | 97 | 99 | 0.022613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_762-5_0_3_line_108 | NAYY 4x150 SE | 98 | 100 | 0.075813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_762-5_0_3_line_109 | NAYY 4x150 SE | 98 | 101 | 0.019373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_762-5_0_3_line_110 | NAYY 4x150 SE | 100 | 103 | 0.024371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_762-5_0_3_line_111 | NAYY 4x150 SE | 101 | 104 | 0.023225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_762-5_0_3_line_112 | NAYY 4x150 SE | 103 | 105 | 0.27851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_762-5_0_3_line_113 | NAYY 4x150 SE | 105 | 140 | 0.0057207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_762-5_0_3_line_114 | NAYY 4x150 SE | 107 | 108 | 0.010568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_762-5_0_3_line_115 | NAYY 4x150 SE | 108 | 109 | 0.12519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_762-5_0_3_line_116 | NAYY 4x150 SE | 110 | 111 | 0.22849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_762-5_0_3_line_117 | NAYY 4x150 SE | 112 | 113 | 0.039738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_762-5_0_3_line_118 | NAYY 4x150 SE | 113 | 177 | 0.078683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_762-5_0_3_line_119 | NAYY 4x150 SE | 114 | 115 | 0.033342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_762-5_0_3_line_120 | NAYY 4x150 SE | 114 | 116 | 0.014463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_762-5_0_3_line_121 | NAYY 4x150 SE | 115 | 117 | 0.056086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_762-5_0_3_line_122 | NAYY 4x150 SE | 115 | 118 | 0.058174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_762-5_0_3_line_123 | NAYY 4x150 SE | 117 | 119 | 0.026279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_762-5_0_3_line_124 | NAYY 4x150 SE | 117 | 120 | 0.2042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_762-5_0_3_line_125 | NAYY 4x150 SE | 118 | 121 | 0.059751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_762-5_0_3_line_126 | NAYY 4x150 SE | 120 | 124 | 0.025453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_762-5_0_3_line_127 | NAYY 4x150 SE | 120 | 122 | 0.046613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_762-5_0_3_line_128 | NAYY 4x150 SE | 122 | 123 | 0.019661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_762-5_0_3_line_129 | NAYY 4x150 SE | 123 | 125 | 0.063682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_762-5_0_3_line_130 | NAYY 4x150 SE | 126 | 127 | 0.00033145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_762-5_0_3_line_131 | NAYY 4x150 SE | 126 | 128 | 0.064774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_762-5_0_3_line_132 | NAYY 4x150 SE | 127 | 129 | 0.030191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_762-5_0_3_line_133 | NAYY 4x150 SE | 128 | 130 | 0.0056215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_762-5_0_3_line_134 | NAYY 4x150 SE | 129 | 131 | 0.020796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_762-5_0_3_line_135 | NAYY 4x150 SE | 130 | 132 | 0.018219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_762-5_0_3_line_136 | NAYY 4x150 SE | 131 | 133 | 0.021632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_762-5_0_3_line_137 | NAYY 4x150 SE | 132 | 134 | 0.0045183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_762-5_0_3_line_138 | NAYY 4x150 SE | 134 | 146 | 0.060285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_762-5_0_3_line_139 | NAYY 4x150 SE | 134 | 142 | 0.011836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_762-5_0_3_line_140 | NAYY 4x150 SE | 135 | 136 | 0.018482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_762-5_0_3_line_141 | NAYY 4x150 SE | 136 | 137 | 0.011262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_762-5_0_3_line_142 | NAYY 4x150 SE | 137 | 138 | 0.054438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_762-5_0_3_line_143 | NAYY 4x150 SE | 138 | 139 | 0.042246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_762-5_0_3_line_144 | NAYY 4x150 SE | 139 | 155 | 0.063942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_762-5_0_3_line_145 | NAYY 4x150 SE | 139 | 154 | 0.027454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_762-5_0_3_line_146 | NAYY 4x150 SE | 141 | 142 | 0.035921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
147 | LV_762-5_0_3_line_147 | NAYY 4x150 SE | 141 | 143 | 0.15822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
148 | LV_762-5_0_3_line_148 | NAYY 4x150 SE | 143 | 144 | 0.048522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
149 | LV_762-5_0_3_line_149 | NAYY 4x150 SE | 143 | 145 | 0.021076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
150 | LV_762-5_0_3_line_150 | NAYY 4x150 SE | 144 | 147 | 0.069885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
151 | LV_762-5_0_3_line_151 | NAYY 4x150 SE | 145 | 148 | 0.008063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
152 | LV_762-5_0_3_line_152 | NAYY 4x150 SE | 146 | 149 | 0.026333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
153 | LV_762-5_0_3_line_153 | NAYY 4x150 SE | 147 | 150 | 0.012405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
154 | LV_762-5_0_3_line_154 | NAYY 4x150 SE | 148 | 151 | 0.0017595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
155 | LV_762-5_0_3_line_155 | NAYY 4x150 SE | 149 | 152 | 0.013815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
156 | LV_762-5_0_3_line_156 | NAYY 4x150 SE | 150 | 206 | 0.013014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
157 | LV_762-5_0_3_line_157 | NAYY 4x150 SE | 151 | 210 | 0.042524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
158 | LV_762-5_0_3_line_158 | NAYY 4x150 SE | 152 | 153 | 0.026974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
159 | LV_762-5_0_3_line_159 | NAYY 4x150 SE | 152 | 154 | 0.0656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
160 | LV_762-5_0_3_line_160 | NAYY 4x150 SE | 156 | 157 | 0.008162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
161 | LV_762-5_0_3_line_161 | NAYY 4x150 SE | 156 | 158 | 0.057181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
162 | LV_762-5_0_3_line_162 | NAYY 4x150 SE | 157 | 159 | 0.01239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
163 | LV_762-5_0_3_line_163 | NAYY 4x150 SE | 158 | 160 | 0.033006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
164 | LV_762-5_0_3_line_164 | NAYY 4x150 SE | 159 | 171 | 0.049384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
165 | LV_762-5_0_3_line_165 | NAYY 4x150 SE | 160 | 172 | 0.004044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
166 | LV_762-5_0_3_line_166 | NAYY 4x150 SE | 161 | 162 | 0.027157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
167 | LV_762-5_0_3_line_167 | NAYY 4x150 SE | 162 | 163 | 0.027194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
168 | LV_762-5_0_3_line_168 | NAYY 4x150 SE | 163 | 164 | 0.039846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
169 | LV_762-5_0_3_line_169 | NAYY 4x150 SE | 164 | 165 | 0.042231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
170 | LV_762-5_0_3_line_170 | NAYY 4x150 SE | 164 | 166 | 0.090405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
171 | LV_762-5_0_3_line_171 | NAYY 4x150 SE | 164 | 167 | 0.014774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
172 | LV_762-5_0_3_line_172 | NAYY 4x150 SE | 165 | 168 | 0.031237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
173 | LV_762-5_0_3_line_173 | NAYY 4x150 SE | 165 | 169 | 0.010099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
174 | LV_762-5_0_3_line_174 | NAYY 4x150 SE | 166 | 170 | 0.0088944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
175 | LV_762-5_0_3_line_175 | NAYY 4x150 SE | 168 | 180 | 0.021526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
176 | LV_762-5_0_3_line_176 | NAYY 4x150 SE | 168 | 181 | 0.0085683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
177 | LV_762-5_0_3_line_177 | NAYY 4x150 SE | 169 | 182 | 0.067881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
178 | LV_762-5_0_3_line_178 | NAYY 4x150 SE | 170 | 173 | 0.025084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
179 | LV_762-5_0_3_line_179 | NAYY 4x150 SE | 171 | 183 | 0.0086277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
180 | LV_762-5_0_3_line_180 | NAYY 4x150 SE | 172 | 180 | 0.017686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
181 | LV_762-5_0_3_line_181 | NAYY 4x150 SE | 173 | 174 | 0.056452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
182 | LV_762-5_0_3_line_182 | NAYY 4x150 SE | 173 | 175 | 0.16628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
183 | LV_762-5_0_3_line_183 | NAYY 4x150 SE | 174 | 176 | 0.10292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
184 | LV_762-5_0_3_line_184 | NAYY 4x150 SE | 175 | 177 | 0.080229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
185 | LV_762-5_0_3_line_185 | NAYY 4x150 SE | 175 | 178 | 0.081654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
186 | LV_762-5_0_3_line_186 | NAYY 4x150 SE | 176 | 179 | 0.018228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
187 | LV_762-5_0_3_line_187 | NAYY 4x150 SE | 181 | 187 | 0.0038077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
188 | LV_762-5_0_3_line_188 | NAYY 4x150 SE | 182 | 196 | 0.024856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
189 | LV_762-5_0_3_line_189 | NAYY 4x150 SE | 182 | 193 | 0.055913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
190 | LV_762-5_0_3_line_190 | NAYY 4x150 SE | 184 | 185 | 0.026091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
191 | LV_762-5_0_3_line_191 | NAYY 4x150 SE | 185 | 190 | 0.029467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
192 | LV_762-5_0_3_line_192 | NAYY 4x150 SE | 186 | 187 | 0.0094245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
193 | LV_762-5_0_3_line_193 | NAYY 4x150 SE | 186 | 188 | 0.014103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
194 | LV_762-5_0_3_line_194 | NAYY 4x150 SE | 188 | 189 | 0.0054131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
195 | LV_762-5_0_3_line_195 | NAYY 4x150 SE | 189 | 190 | 0.015575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
196 | LV_762-5_0_3_line_196 | NAYY 4x150 SE | 191 | 192 | 0.017909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
197 | LV_762-5_0_3_line_197 | NAYY 4x150 SE | 192 | 193 | 0.023178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
198 | LV_762-5_0_3_line_198 | NAYY 4x150 SE | 193 | 194 | 0.027048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
199 | LV_762-5_0_3_line_199 | NAYY 4x150 SE | 194 | 195 | 0.033405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
200 | LV_762-5_0_3_line_200 | NAYY 4x150 SE | 195 | 209 | 0.062808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
201 | LV_762-5_0_3_line_201 | NAYY 4x150 SE | 197 | 198 | 0.017333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
202 | LV_762-5_0_3_line_202 | NAYY 4x150 SE | 197 | 199 | 0.0067468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
203 | LV_762-5_0_3_line_203 | NAYY 4x150 SE | 198 | 200 | 0.034318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
204 | LV_762-5_0_3_line_204 | NAYY 4x150 SE | 199 | 201 | 0.049793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
205 | LV_762-5_0_3_line_205 | NAYY 4x150 SE | 200 | 202 | 0.0047701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
206 | LV_762-5_0_3_line_206 | NAYY 4x150 SE | 201 | 203 | 0.018718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
207 | LV_762-5_0_3_line_207 | NAYY 4x150 SE | 202 | 204 | 0.031029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
208 | LV_762-5_0_3_line_208 | NAYY 4x150 SE | 203 | 205 | 0.0080028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
209 | LV_762-5_0_3_line_209 | NAYY 4x150 SE | 204 | 207 | 0.020909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
210 | LV_762-5_0_3_line_210 | NAYY 4x150 SE | 205 | 216 | 0.026551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
211 | LV_762-5_0_3_line_211 | NAYY 4x150 SE | 207 | 208 | 0.017367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
212 | LV_762-5_0_3_line_212 | NAYY 4x150 SE | 208 | 209 | 0.044527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
213 | LV_762-5_0_3_line_213 | NAYY 4x150 SE | 210 | 211 | 0.053992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
214 | LV_762-5_0_3_line_214 | NAYY 4x150 SE | 212 | 213 | 0.012863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
215 | LV_762-5_0_3_line_215 | NAYY 4x150 SE | 213 | 214 | 0.071912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
216 | LV_762-5_0_3_line_216 | NAYY 4x150 SE | 213 | 215 | 0.077134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
217 | LV_762-5_0_3_line_217 | NAYY 4x150 SE | 217 | 218 | 0.081519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
218 | LV_762-5_0_3_line_218 | NAYY 4x150 SE | 218 | 219 | 0.033084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_762-5_0_3_trafo_187 | 0.25 MVA 20/0.4 kV | 220 | 184 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2607878.2382 | 1164992.2954 | 2607868.9243 | 1164988.4814 | 2607860.5923 | 1164983.268 | 2607854.0221 | 1164977.5233 | 2607845.5264 | 1164974.5219 | 2607834.7229 | 1164973.8187 | 2607824.5777 | 1164973.272 | 2607810.1931 | 1164976.5328 | 2607801.4441 | 1164979.9121 | 2607797.0422 | 1164985.109 | 2607791.983 | 1164989.3157 | 2607786.355 | 1164989.1862 | 2607778.142 | 1164986.7189 | 2607774.9077 | 1164986.0976
1 | 2607760.5178 | 1164990.4426 | 2607765.4085 | 1164986.3024 | 2607770.2186 | 1164985.1969 | 2607774.9077 | 1164986.0976
2 | 2607760.5178 | 1164990.4426 | 2607764.6741 | 1165015.5826 | 2607764.449 | 1165053.8569
3 | 2607760.5178 | 1164990.4426 | 2607758.9221 | 1164980.8247 | 2607746.9149 | 1164945.3583 | 2607740.0306 | 1164933.6548 | 2607733.8871 | 1164929.5005 | 2607722.695 | 1164930.6531
4 | 2607773.1331 | 1165148.6374 | 2607764.1342 | 1165108.2614 | 2607764.449 | 1165053.8569
5 | 2607764.449 | 1165053.8569 | 2607759.1723 | 1165048.5253 | 2607750.964 | 1165042.3784 | 2607738.1216 | 1165031.4232 | 2607729.5013 | 1165024.0419 | 2607722.1076 | 1165021.5757 | 2607713.0878 | 1165020.8182
6 | 2607438.8529 | 1164814.552 | 2607475.7869 | 1164850.293 | 2607489.8166 | 1164874.0666 | 2607498.1071 | 1164882.192 | 2607542.3358 | 1164888.6945 | 2607588.045 | 1164880.8365 | 2607618.1212 | 1164870.2801 | 2607633.0607 | 1164870.3989 | 2607646.7622 | 1164874.5849 | 2607661.8152 | 1164887.8661 | 2607689.7288 | 1164928.2548 | 2607700.8337 | 1164932.9046 | 2607722.695 | 1164930.6531
7 | 2608665.3684 | 1164043.9763 | 2608622.1131 | 1164270.0603
8 | 2608665.3684 | 1164043.9763 | 2608655.3034 | 1164023.8186 | 2608645.8093 | 1163995.2575 | 2608627.8731 | 1163936.1248 | 2608619.3437 | 1163896.8487 | 2608611.2179 | 1163885.9984 | 2608575.4406 | 1163850.7302 | 2608566.042 | 1163835.4648 | 2608556.1601 | 1163804.4132 | 2608553.985 | 1163783.1949
9 | 2607773.1331 | 1165148.6374 | 2607769.7028 | 1165160.5945 | 2607771.6484 | 1165177.8945 | 2607776.1281 | 1165195.5535 | 2607767.8946 | 1165197.2994 | 2607760.2071 | 1165197.1672 | 2607749.9423 | 1165194.6973 | 2607739.2763 | 1165188.5362 | 2607729.0103 | 1165186.8889 | 2607716.2845 | 1165180.7252 | 2607705.1994 | 1165172.9406 | 2607687.0218 | 1165160.7559 | 2607672.7739 | 1165153.2452 | 2607656.2244 | 1165149.2445 | 2607646.0794 | 1165148.6981 | 2607636.5136 | 1165144.3061 | 2607630.9033 | 1165136.3951 | 2607623.1122 | 1165121.2444 | 2607603.0078 | 1165106.4785 | 2607587.4037 | 1165099.4888 | 2607570.9848 | 1165094.9661 | 2607554.567 | 1165083.4843 | 2607523.2531 | 1165061.868 | 2607521.7391 | 1165053.9622
10 | 2607773.1331 | 1165148.6374 | 2607788.504 | 1165146.2115 | 2607803.3484 | 1165154.2235 | 2607819.776 | 1165169.4856 | 2607839.3187 | 1165173.9019 | 2607932.0835 | 1165149.5214
11 | 2607691.7239 | 1165015.4007 | 2607695.1263 | 1165019.3736 | 2607707.3231 | 1165020.3341 | 2607713.0878 | 1165020.8182
12 | 2607438.8529 | 1164814.552 | 2607422.5128 | 1164795.0223 | 2607409.8923 | 1164776.9646 | 2607400.7414 | 1164758.3108 | 2607383.9079 | 1164734.9231 | 2607346.5127 | 1164705.9967 | 2607319.3529 | 1164666.3886 | 2607314.5634 | 1164650.2192 | 2607314.853 | 1164625.9964 | 2607315.1437 | 1164594.5033 | 2607300.9815 | 1164552.4876 | 2607300.3344 | 1164549.3186 | 2607300.9048 | 1164546.1844
13 | 2607576.7099 | 1165011.1649 | 2607566.0266 | 1165018.5219 | 2607556.2842 | 1165020.4329 | 2607549.173 | 1165024.6372 | 2607540.1243 | 1165035.2757 | 2607530.6646 | 1165043.8571 | 2607523.392 | 1165048.6394 | 2607521.7391 | 1165053.9622
14 | 2607973.7649 | 1165130.2002 | 2607941.8051 | 1165146.9664 | 2607932.0835 | 1165149.5214
15 | 2607300.9048 | 1164546.1844 | 2607532.5075 | 1164042.2832
16 | 2608587.1039 | 1163354.5226 | 2608447.0514 | 1163556.5786
17 | 2608587.1039 | 1163354.5226 | 2608578.0881 | 1163338.7909 | 2608570.7118 | 1163322.8058 | 2608559.8505 | 1163301.2798 | 2608552.4933 | 1163277.113 | 2608541.0463 | 1163236.3433 | 2608540.4412 | 1163225.4815 | 2608541.0914 | 1163204.3941 | 2608541.3577 | 1163200.2147 | 2608539.3845 | 1163169.1597
18 | 2608387.1656 | 1163502.7939 | 2608394.837 | 1163510.575 | 2608402.4294 | 1163520.0347 | 2608414.7475 | 1163534.937 | 2608427.1586 | 1163549.1279 | 2608430.2754 | 1163554.924 | 2608434.6491 | 1163560.1883 | 2608439.0281 | 1163561.6173 | 2608443.0585 | 1163560.3779 | 2608447.0514 | 1163556.5786
19 | 2608547.2742 | 1163132.7562 | 2608543.8673 | 1163137.0091 | 2608541.8022 | 1163140.2856 | 2608540.7689 | 1163145.1977 | 2608539.1196 | 1163152.3767 | 2608539.2371 | 1163166.8396 | 2608539.3845 | 1163169.1597
20 | 2608041.1995 | 1165096.5723 | 2608023.9459 | 1165103.8753 | 2607973.7649 | 1165130.2002
21 | 2608073.1324 | 1165083.0636 | 2608076.9396 | 1165076.0875 | 2608079.1242 | 1165068.5978 | 2608079.9676 | 1165056.315 | 2608079.9154 | 1165055.2637
22 | 2608073.1324 | 1165083.0636 | 2608076.8487 | 1165086.8149
23 | 2608073.1324 | 1165083.0636 | 2608041.1995 | 1165096.5723
24 | 2608076.8487 | 1165086.8149 | 2608079.9299 | 1165084.5734 | 2608104.8674 | 1165080.2268
25 | 2608097.973 | 1165122.4942 | 2608090.4448 | 1165100.5399 | 2608076.8487 | 1165086.8149
26 | 2608018.639 | 1165058.001 | 2608016.6927 | 1165064.8352 | 2608017.7931 | 1165072.3293 | 2608022.421 | 1165081.6289 | 2608031.0424 | 1165087.7767 | 2608037.4836 | 1165092.4209 | 2608041.1995 | 1165096.5723
27 | 2608097.973 | 1165122.4942 | 2608099.5272 | 1165130.8818
28 | 2608050.4187 | 1163722.905 | 2607532.5075 | 1164042.2832
29 | 2608294.3409 | 1163868.0699 | 2608124.713 | 1163836.8133
30 | 2608124.713 | 1163836.8133 | 2608118.1095 | 1163815.1603 | 2608101.4599 | 1163791.9043 | 2608083.203 | 1163773.4263 | 2608055.1539 | 1163729.1892 | 2608050.4187 | 1163722.905
31 | 2608347.067 | 1163727.1944 | 2608294.3409 | 1163868.0699
32 | 2609041.5628 | 1163517.9388 | 2609226.2255 | 1163402.0308
33 | 2609041.5628 | 1163517.9388 | 2609047.8404 | 1163526.4675 | 2609083.037 | 1163565.3506 | 2609095.7739 | 1163580.7662 | 2609096.5327 | 1163582.9443
34 | 2609026.9392 | 1163498.0713 | 2609041.5628 | 1163517.9388
35 | 2608161.7493 | 1163432.1058 | 2608164.5319 | 1163438.1356 | 2608175.1053 | 1163446.843 | 2608185.9974 | 1163451.9714 | 2608221.1659 | 1163465.2144 | 2608242.0163 | 1163475.0143 | 2608254.4515 | 1163488.6936 | 2608260.1926 | 1163502.3637 | 2608282.0684 | 1163557.4876 | 2608291.5231 | 1163588.5382 | 2608293.0635 | 1163599.0899 | 2608293.672 | 1163613.3645 | 2608294.2747 | 1163626.2495 | 2608295.9801 | 1163633.7 | 2608298.9244 | 1163642.5529 | 2608306.0693 | 1163654.3574 | 2608310.727 | 1163664.7579 | 2608312.586 | 1163671.9084 | 2608313.6617 | 1163680.592 | 2608315.363 | 1163690.9995 | 2608319.2388 | 1163701.8657 | 2608324.6745 | 1163709.0101 | 2608326.4133 | 1163710.6228
36 | 2608168.9113 | 1163354.1776 | 2608163.1102 | 1163362.0959 | 2608161.199 | 1163370.7754 | 2608166.0099 | 1163381.4872 | 2608166.9304 | 1163391.8825 | 2608164.891 | 1163399.0278 | 2608160.2175 | 1163405.6914 | 2608158.0198 | 1163416.705 | 2608158.9417 | 1163426.022 | 2608161.7493 | 1163432.1058
37 | 2608326.4133 | 1163710.6228 | 2608333.5554 | 1163717.2466
38 | 2608168.9113 | 1163354.1776 | 2608184.5309 | 1163358.2562 | 2608210.2332 | 1163371.353 | 2608231.8688 | 1163389.7693 | 2608275.6927 | 1163447.7689 | 2608304.3036 | 1163473.065 | 2608334.6067 | 1163498.4637 | 2608341.7364 | 1163504.7433 | 2608345.6302 | 1163508.1725
39 | 2608168.9113 | 1163354.1776 | 2608161.8672 | 1163352.3338
40 | 2608347.0464 | 1163727.177 | 2608341.1612 | 1163722.2282 | 2608335.4062 | 1163718.9631 | 2608333.5554 | 1163717.2466
41 | 2608345.6302 | 1163508.1725 | 2608354.3238 | 1163496.701 | 2608358.2044 | 1163493.049 | 2608363.4165 | 1163490.2437 | 2608368.3118 | 1163489.4945 | 2608373.4817 | 1163489.5239 | 2608380.5509 | 1163495.2254 | 2608387.1656 | 1163502.7939
42 | 2608345.6302 | 1163508.1725 | 2608361.06 | 1163521.745 | 2608367.9469 | 1163537.3956 | 2608374.0723 | 1163583.1156 | 2608386.4622 | 1163606.9891 | 2608402.8746 | 1163624.2092 | 2608441.9522 | 1163656.235 | 2608444.2063 | 1163658.3852
43 | 2608161.8672 | 1163352.3338 | 2608156.5769 | 1163350.6481 | 2608135.8681 | 1163343.3278 | 2608104.994 | 1163333.1617
44 | 2608161.8672 | 1163352.3338 | 2608148.0746 | 1163368.0008 | 2608134.9061 | 1163380.9896
45 | 2608347.067 | 1163727.1944 | 2608347.0464 | 1163727.177
46 | 2608444.2063 | 1163658.3852 | 2608474.3982 | 1163687.1846 | 2608532.3902 | 1163742.5156 | 2608547.6912 | 1163765.2374 | 2608553.1911 | 1163775.4502 | 2608553.985 | 1163783.1949
47 | 2608104.994 | 1163333.1617 | 2608100.6812 | 1163331.7416 | 2608059.7484 | 1163309.5093 | 2608030.2626 | 1163292.7186
48 | 2608134.9061 | 1163380.9896 | 2608099.1425 | 1163394.1482 | 2608088.848 | 1163393.2934
49 | 2608486.312 | 1163105.0052 | 2608490.3776 | 1163111.4879 | 2608500.738 | 1163124.5867 | 2608514.1589 | 1163134.655 | 2608526.6734 | 1163135.5841 | 2608535.4285 | 1163130.944
50 | 2608485.2445 | 1163103.3031 | 2608486.312 | 1163105.0052
51 | 2608540.4174 | 1163128.2999 | 2608535.4285 | 1163130.944
52 | 2608485.2445 | 1163103.3031 | 2608484.5598 | 1163102.2114
53 | 2608009.0379 | 1163280.6322 | 2608030.2626 | 1163292.7186
54 | 2607893.8072 | 1163144.9093 | 2607882.7544 | 1163139.0254 | 2607877.285 | 1163139.3406 | 2607867.7313 | 1163129.1899 | 2607862.1356 | 1163120.6006 | 2607851.7976 | 1163089.1271 | 2607852.7953 | 1163084.6961
55 | 2607893.8072 | 1163144.9093 | 2607901.6929 | 1163147.7988
56 | 2607901.6929 | 1163147.7988 | 2607914.7609 | 1163168.9159
57 | 2607944.321 | 1163216.1217 | 2607947.0803 | 1163220.4942 | 2607975.2978 | 1163255.5486 | 2607998.7181 | 1163274.7557 | 2608009.0379 | 1163280.6322
58 | 2607944.321 | 1163216.1217 | 2607926.1825 | 1163187.3726 | 2607914.7609 | 1163168.9159
59 | 2608149.2032 | 1162830.7025 | 2608157.1551 | 1162833.3297
60 | 2608192.1832 | 1162844.7945 | 2608190.9623 | 1162844.499 | 2608157.1551 | 1162833.3297
61 | 2608484.5598 | 1163102.2114 | 2608466.3109 | 1163073.113 | 2608463.5971 | 1163068.6146
62 | 2608443.7913 | 1163035.7218 | 2608444.0802 | 1163036.2637 | 2608463.5971 | 1163068.6146
63 | 2608192.1832 | 1162844.7945 | 2608196.9198 | 1162845.9411 | 2608200.3362 | 1162845.9235
64 | 2609487.3705 | 1162745.263 | 2609489.4714 | 1162751.4255 | 2609494.8998 | 1162762.8508 | 2609495.8682 | 1162764.6998
65 | 2609430.9233 | 1162580.4937 | 2609429.5442 | 1162600.3125 | 2609428.4794 | 1162624.8897 | 2609430.527 | 1162633.2859 | 2609435.9119 | 1162638.3524 | 2609443.2516 | 1162642.5214 | 2609450.2195 | 1162649.2912 | 2609456.1664 | 1162657.4935 | 2609460.4707 | 1162667.7497 | 2609478.3159 | 1162718.7029 | 2609487.3705 | 1162745.263
66 | 2609512.444 | 1162805.1326 | 2609515.7306 | 1162799.9241 | 2609516.5169 | 1162796.8127 | 2609516.1226 | 1162794.1997 | 2609514.0066 | 1162790.5056 | 2609510.0379 | 1162786.1305 | 2609504.8621 | 1162779.697 | 2609500.5055 | 1162773.5538 | 2609495.8682 | 1162764.6998
67 | 2609430.9233 | 1162580.4937 | 2609441.2792 | 1162585.9903
68 | 2609430.9233 | 1162580.4937 | 2609431.0124 | 1162578.1017
69 | 2609512.444 | 1162805.1326 | 2609521.7708 | 1162811.9618
70 | 2609276.3826 | 1162681.0826 | 2609284.5327 | 1162686.3199 | 2609304.3016 | 1162697.6114 | 2609362.9217 | 1162729.4954 | 2609380.1351 | 1162738.7711 | 2609386.6093 | 1162742.8164 | 2609392.9751 | 1162747.5731 | 2609400.9456 | 1162754.8891 | 2609433.0074 | 1162786.5769 | 2609438.5694 | 1162791.0434 | 2609444.2104 | 1162793.8869 | 2609450.9175 | 1162795.9095 | 2609456.5998 | 1162796.7966 | 2609464.0371 | 1162797.2418 | 2609472.6018 | 1162796.7771 | 2609483.3729 | 1162796.0714 | 2609487.999 | 1162796.4233 | 2609493.7344 | 1162797.7107 | 2609501.3219 | 1162800.0126 | 2609512.444 | 1162805.1326
71 | 2609445.371 | 1162599.9258 | 2609442.096 | 1162592.7505 | 2609441.2792 | 1162585.9903
72 | 2609441.2792 | 1162585.9903 | 2609451.5462 | 1162589.4859 | 2609472.6899 | 1162603.448 | 2609488.1495 | 1162611.4474
73 | 2609431.0124 | 1162578.1017 | 2609431.451 | 1162566.3208 | 2609429.6093 | 1162558.5363 | 2609425.9778 | 1162549.037 | 2609425.4598 | 1162548.0619
74 | 2609056.5329 | 1163119.4142 | 2609054.1658 | 1163117.5073 | 2609034.8959 | 1163095.7455 | 2609023.837 | 1163074.0738 | 2609016.6098 | 1163048.1851
75 | 2609016.6098 | 1163048.1851 | 2609175.9757 | 1162896.2808
76 | 2608858.3608 | 1163160.1945 | 2609016.6098 | 1163048.1851
77 | 2609175.9757 | 1162896.2808 | 2609172.69 | 1162890.951 | 2609170.7403 | 1162888.5322
78 | 2608810.573 | 1163233.5723 | 2608809.777 | 1163227.9128 | 2608807.9308 | 1163222.7853 | 2608805.887 | 1163216.646 | 2608806.1861 | 1163211.1326 | 2608809.2739 | 1163205.2008 | 2608815.7787 | 1163198.6292 | 2608858.3608 | 1163160.1945
79 | 2609521.7708 | 1162811.9618 | 2609524.1177 | 1162824.7274 | 2609525.7556 | 1162830.4661 | 2609528.8258 | 1162836.2071 | 2609534.5688 | 1162842.3526 | 2609541.5383 | 1162852.8132 | 2609561.7438 | 1162887.7179 | 2609566.5295 | 1162898.5197 | 2609570.6289 | 1162907.3417 | 2609575.9601 | 1162912.2637 | 2609583.346 | 1162920.8797 | 2609585.9947 | 1162931.5336 | 2609584.34 | 1162941.3581 | 2609578.4862 | 1162952.043 | 2609568.1965 | 1162963.299 | 2609546.6786 | 1162978.7727 | 2609537.552 | 1162985.9841 | 2609529.9497 | 1162995.6082
80 | 2609276.3826 | 1162681.0826 | 2609282.1042 | 1162691.4299 | 2609285.7167 | 1162698.45 | 2609288.0357 | 1162704.8011 | 2609289.0544 | 1162709.8608 | 2609291.3012 | 1162718.2795 | 2609294.0667 | 1162728.122 | 2609297.2338 | 1162735.8973 | 2609304.8175 | 1162745.7472
81 | 2609276.3826 | 1162681.0826 | 2609261.7195 | 1162677.0137 | 2609256.3135 | 1162675.6159 | 2609250.3019 | 1162674.5617 | 2609242.9407 | 1162674.3281 | 2609234.4908 | 1162674.8266 | 2609228.3302 | 1162675.9845 | 2609222.5134 | 1162677.7543 | 2609216.0136 | 1162680.3456 | 2609210.7078 | 1162683.5614 | 2609202.3413 | 1162689.5961 | 2609190.0148 | 1162705.5853 | 2609177.2541 | 1162730.0892 | 2609176.3322 | 1162738.7972
82 | 2609276.3826 | 1162681.0826 | 2609272.2846 | 1162670.938 | 2609262.1973 | 1162650.1233 | 2609252.5962 | 1162631.8774 | 2609245.888 | 1162620.4504 | 2609234.7085 | 1162602.391 | 2609219.6416 | 1162581.6911 | 2609213.964 | 1162573.5915
83 | 2609546.0382 | 1162564.077 | 2609545.0602 | 1162572.224 | 2609543.7945 | 1162592.7099 | 2609539.6609 | 1162610.3121 | 2609534.3036 | 1162621.7761 | 2609528.1303 | 1162626.0685 | 2609521.9625 | 1162626.8814 | 2609515.1854 | 1162625.4367 | 2609488.1495 | 1162611.4474
84 | 2609425.4598 | 1162548.0619 | 2609420.8603 | 1162539.4021 | 2609415.8822 | 1162530.1632
85 | 2609524.4583 | 1163002.4939 | 2609529.1938 | 1162996.5651 | 2609529.9497 | 1162995.6082
86 | 2609174.6367 | 1162758.6806 | 2609174.503 | 1162756.0757 | 2609176.3322 | 1162738.7972
87 | 2609171.6031 | 1162501.1116 | 2609179.9692 | 1162515.6759 | 2609190.8249 | 1162535.2799 | 2609204.2867 | 1162558.8565 | 2609213.1826 | 1162572.4767 | 2609213.964 | 1162573.5915
88 | 2609546.0382 | 1162564.077 | 2609544.8881 | 1162555.0263 | 2609540.1701 | 1162549.694 | 2609537.1021 | 1162548.3108
89 | 2609415.8822 | 1162530.1632 | 2609415.4829 | 1162529.4221 | 2609402.793 | 1162497.6533 | 2609394.0002 | 1162467.1245 | 2609384.4243 | 1162417.9519 | 2609380.1565 | 1162388.8642 | 2609380.2918 | 1162375.3401
90 | 2609380.0759 | 1162351.0644 | 2609380.3921 | 1162365.3085 | 2609380.2918 | 1162375.3401
91 | 2608917.5041 | 1162190.4226 | 2609131.1886 | 1162154.4009
92 | 2608917.5041 | 1162190.4226 | 2608894.1324 | 1162241.5247 | 2608871.1903 | 1162287.3248 | 2608822.6943 | 1162342.3702 | 2608770.2722 | 1162379.6237 | 2608759.3479 | 1162386.6863
93 | 2609153.0346 | 1162161.3595 | 2609131.1886 | 1162154.4009
94 | 2609131.1886 | 1162154.4009 | 2609140.3783 | 1162136.3169 | 2609142.5616 | 1162131.3288 | 2609144.4535 | 1162126.4626 | 2609153.401 | 1162096.3945 | 2609164.9779 | 1162050.0446 | 2609166.2635 | 1162045.9445 | 2609171.4866 | 1162031.9233 | 2609173.6097 | 1162026.2237 | 2609186.8745 | 1162033.9698 | 2609203.0456 | 1162044.922
95 | 2609388.029 | 1162252.7821 | 2609383.6042 | 1162284.818 | 2609379.4326 | 1162322.0856 | 2609380.0759 | 1162351.0644
96 | 2609524.4583 | 1163002.4939 | 2609515.9431 | 1163005.8155
97 | 2609192.7014 | 1162817.9118 | 2609183.6173 | 1162797.2433 | 2609175.314 | 1162771.8737 | 2609174.6367 | 1162758.6806
98 | 2609179.0921 | 1162457.5791 | 2609172.5138 | 1162461.2599 | 2609169.4284 | 1162465.146 | 2609167.7727 | 1162470.8797 | 2609167.7634 | 1162477.016 | 2609172.3314 | 1162495.6655 | 2609172.4426 | 1162498.1225 | 2609171.6031 | 1162501.1116
99 | 2609176.937 | 1162282.3223 | 2609171.5672 | 1162327.6144 | 2609169.5224 | 1162337.3494 | 2609167.6269 | 1162344.6057 | 2609164.7805 | 1162352.5053 | 2609157.9831 | 1162369.2367 | 2609156.5489 | 1162375.4376 | 2609155.8807 | 1162381.6174 | 2609155.8492 | 1162387.2646 | 2609156.5384 | 1162392.5016 | 2609160.4766 | 1162417.3532 | 2609160.546 | 1162422.1112 | 2609159.819 | 1162426.7013 | 2609158.7404 | 1162430.7239 | 2609156.8344 | 1162434.8564 | 2609148.9093 | 1162447.7063 | 2609147.0949 | 1162452.0502 | 2609146.3837 | 1162456.2512 | 2609146.424 | 1162460.042 | 2609146.9246 | 1162463.3333 | 2609147.9234 | 1162466.4475 | 2609149.4662 | 1162469.5291 | 2609151.9655 | 1162473.2458 | 2609160.4286 | 1162484.5086 | 2609171.6031 | 1162501.1116
100 | 2609388.029 | 1162252.7821 | 2609388.3845 | 1162250.2083 | 2609393.1318 | 1162231.9844 | 2609401.3738 | 1162217.8679 | 2609412.5382 | 1162206.3462 | 2609428.5415 | 1162191.6972 | 2609438.4246 | 1162176.5495 | 2609442.9611 | 1162165.9069 | 2609445.2332 | 1162158.1288 | 2609445.2332 | 1162158.1288
101 | 2609445.2332 | 1162158.1288 | 2609443.6043 | 1162151.3673 | 2609440.9367 | 1162147.4724 | 2609435.24 | 1162145.5403 | 2609430.3112 | 1162142.4644 | 2609423.1243 | 1162138.1511 | 2609419.0283 | 1162131.597 | 2609415.9353 | 1162105.646 | 2609416.6454 | 1162100.8478
102 | 2609429.3531 | 1162080.5601 | 2609426.4496 | 1162083.7404 | 2609420.0674 | 1162089.0554 | 2609417.3909 | 1162095.8101 | 2609416.6454 | 1162100.8478
103 | 2609510.91 | 1161997.1963 | 2609495.8822 | 1162000.0074 | 2609485.7548 | 1162004.5716 | 2609478.3462 | 1162009.6736 | 2609471.9632 | 1162020.3133 | 2609467.4739 | 1162030.0667 | 2609462.7329 | 1162039.0749 | 2609448.9398 | 1162055.8505 | 2609436.5334 | 1162072.6951 | 2609429.3531 | 1162080.5601
104 | 2609198.2682 | 1162214.3209 | 2609199.1949 | 1162209.4533 | 2609199.4695 | 1162195.1628
105 | 2609176.937 | 1162282.3223 | 2609179.2774 | 1162259.5812 | 2609180.4824 | 1162253.0131 | 2609181.9079 | 1162247.557 | 2609183.8163 | 1162241.946 | 2609186.2371 | 1162236.9361 | 2609192.311 | 1162227.5518 | 2609194.9834 | 1162223.2982 | 2609196.8361 | 1162219.0989 | 2609198.2682 | 1162214.3209
106 | 2609219.4014 | 1162115.7042 | 2609216.864 | 1162126.8058 | 2609215.361 | 1162132.7843 | 2609213.8072 | 1162136.9729 | 2609211.9475 | 1162140.7164 | 2609204.5208 | 1162152.9556 | 2609202.3535 | 1162157.5546 | 2609201.2681 | 1162160.9768 | 2609200.4886 | 1162164.7108 | 2609199.9103 | 1162172.2137 | 2609199.4695 | 1162195.1628
107 | 2609166.5887 | 1162301.694 | 2609171.0872 | 1162290.4508 | 2609173.8088 | 1162284.0851 | 2609176.937 | 1162282.3223
108 | 2609219.4014 | 1162115.7042 | 2609220.0399 | 1162098.8857 | 2609219.316 | 1162081.187 | 2609218.2205 | 1162071.147 | 2609216.4461 | 1162064.1519 | 2609214.5009 | 1162058.6574 | 2609211.8733 | 1162053.5397 | 2609208.8528 | 1162049.8889 | 2609203.0456 | 1162044.922
109 | 2609223.4564 | 1162134.2307 | 2609223.8025 | 1162128.3283 | 2609222.9364 | 1162123.5579 | 2609219.4014 | 1162115.7042
110 | 2609192.0851 | 1162023.1613 | 2609197.0866 | 1162034.0298 | 2609203.0456 | 1162044.922
111 | 2609223.4564 | 1162134.2307 | 2609215.7162 | 1162156.1297
112 | 2609192.0851 | 1162023.1613 | 2609009.7972 | 1161812.5942
113 | 2609009.7972 | 1161812.5942 | 2609011.1776 | 1161807.0425
114 | 2609527.0227 | 1162546.1827 | 2609532.0788 | 1162546.0461 | 2609537.1021 | 1162548.3108
115 | 2609527.0227 | 1162546.1827 | 2609516.562 | 1162534.2937 | 2609510.2098 | 1162525.6794 | 2609505.0835 | 1162516.867 | 2609486.4631 | 1162466.6573 | 2609485.2445 | 1162457.2285 | 2609485.3975 | 1162437.8302 | 2609484.1818 | 1162431.955
116 | 2609510.91 | 1161997.1963 | 2609514.1496 | 1162002.7708 | 2609517.9946 | 1162017.9288 | 2609522.4766 | 1162042.1034 | 2609526.8193 | 1162057.4067 | 2609550.5796 | 1162103.7337 | 2609558.5123 | 1162120.8214 | 2609560.6023 | 1162131.4077 | 2609556.2721 | 1162142.2507 | 2609550.7091 | 1162152.6915 | 2609548.1673 | 1162166.272 | 2609551.6196 | 1162192.2904 | 2609555.6531 | 1162212.5369
117 | 2608737.4885 | 1162616.0602 | 2608725.3463 | 1162632.4286 | 2608720.0012 | 1162636.5118 | 2608708.3522 | 1162641.3952
118 | 2608708.3522 | 1162641.3952 | 2608706.8406 | 1162642.0289 | 2608703.1366 | 1162644.8917 | 2608700.6641 | 1162648.979 | 2608699.2237 | 1162654.5131 | 2608697.7923 | 1162716.3638
119 | 2609192.7014 | 1162817.9118 | 2609210.7977 | 1162845.9421
120 | 2609192.7014 | 1162817.9118 | 2609186.3259 | 1162819.4918 | 2609181.0034 | 1162813.6252
121 | 2609241.7569 | 1162892.7569 | 2609210.7977 | 1162845.9421
122 | 2609210.7977 | 1162845.9421 | 2609196.3852 | 1162848.5993 | 2609178.6177 | 1162851.2403 | 2609164.6428 | 1162853.2646 | 2609158.6846 | 1162852.444 | 2609153.9701 | 1162849.7689 | 2609153.9701 | 1162849.7689
123 | 2609241.7569 | 1162892.7569 | 2609230.5119 | 1162882.8904 | 2609220.9923 | 1162876.6839
124 | 2609241.7569 | 1162892.7569 | 2609364.5612 | 1163056.1266
125 | 2609170.7403 | 1162888.5322 | 2609161.6191 | 1162877.2163 | 2609151.9758 | 1162866.7521 | 2609146.0326 | 1162861.0069 | 2609142.9525 | 1162856.5001 | 2609142.9574 | 1162853.2207 | 2609143.8959 | 1162850.5763 | 2609145.6379 | 1162848.5224 | 2609149.0389 | 1162848.5386 | 2609153.9701 | 1162849.7689
126 | 2609364.5612 | 1163056.1266 | 2609344.1703 | 1163071.4361
127 | 2609364.5612 | 1163056.1266 | 2609392.6309 | 1163093.3406
128 | 2609404.4704 | 1163109.037 | 2609392.6309 | 1163093.3406
129 | 2609404.4704 | 1163109.037 | 2609436.1758 | 1163164.2656
130 | 2608408.7501 | 1162972.1297 | 2608408.5833 | 1162971.8433
131 | 2608370.6734 | 1162919.387 | 2608403.8828 | 1162963.7718 | 2608408.5833 | 1162971.8433
132 | 2608408.7501 | 1162972.1297 | 2608422.1539 | 1162995.1461 | 2608423.8273 | 1162998.2843
133 | 2608370.6734 | 1162919.387 | 2608367.3056 | 1162914.8859
134 | 2608433.6126 | 1163016.6341 | 2608423.8273 | 1162998.2843
135 | 2608357.5801 | 1162899.4803 | 2608367.3056 | 1162914.8859 | 2608367.3056 | 1162914.8859
136 | 2608443.7913 | 1163035.7218 | 2608433.6126 | 1163016.6341
137 | 2608355.1682 | 1162895.6596 | 2608357.5801 | 1162899.4803
138 | 2608355.1682 | 1162895.6596 | 2608360.631 | 1162889.1528 | 2608360.1248 | 1162873.0107 | 2608359.1466 | 1162860.2475 | 2608362.4051 | 1162841.4093 | 2608363.9189 | 1162838.0109
139 | 2608355.1682 | 1162895.6596 | 2608347.6005 | 1162886.5594
140 | 2608456.1954 | 1162615.6053 | 2608473.0924 | 1162622.2322 | 2608473.3818 | 1162622.394
141 | 2608456.1954 | 1162615.6053 | 2608451.264 | 1162625.7305
142 | 2608451.264 | 1162625.7305 | 2608444.9792 | 1162638.6344 | 2608433.7309 | 1162677.109
143 | 2608418.1216 | 1162716.3356 | 2608432.1793 | 1162682.4161 | 2608433.7309 | 1162677.109
144 | 2608418.1216 | 1162716.3356 | 2608431.865 | 1162715.5765 | 2608441.3871 | 1162715.2007 | 2608454.2596 | 1162718.2646 | 2608481.3693 | 1162723.4273
145 | 2608418.1216 | 1162716.3356 | 2608406.9498 | 1162741.4133
146 | 2608347.6005 | 1162886.5594 | 2608329.5038 | 1162864.7978 | 2608325.0152 | 1162858.6421
147 | 2608233.6237 | 1162729.6554 | 2608242.1511 | 1162745.3525 | 2608281.9709 | 1162799.6115 | 2608325.0152 | 1162858.6421
148 | 2608233.6237 | 1162729.6554 | 2608235.4569 | 1162711.0264 | 2608240.8884 | 1162681.722
149 | 2608233.6237 | 1162729.6554 | 2608227.4081 | 1162732.0815 | 2608223.1574 | 1162737.2227 | 2608220.1985 | 1162744.3667
150 | 2608240.8884 | 1162681.722 | 2608241.4451 | 1162678.7186 | 2608242.4908 | 1162658.9213 | 2608228.9693 | 1162626.0088 | 2608225.6458 | 1162615.0792
151 | 2608220.1985 | 1162744.3667 | 2608218.5193 | 1162752.2529
152 | 2608363.9189 | 1162838.0109 | 2608374.6335 | 1162813.9563
153 | 2608222.0369 | 1162603.2109 | 2608225.6458 | 1162615.0792
154 | 2608218.1528 | 1162753.9739 | 2608218.5193 | 1162752.2529
155 | 2608380.2547 | 1162801.3363 | 2608374.6335 | 1162813.9563
156 | 2608222.0369 | 1162603.2109 | 2608221.1981 | 1162600.4523 | 2608219.7077 | 1162590.4321
157 | 2608209.6931 | 1162795.6408 | 2608211.7265 | 1162783.8859 | 2608216.9683 | 1162759.5365 | 2608218.1528 | 1162753.9739
158 | 2608380.2547 | 1162801.3363 | 2608389.0125 | 1162799.6921 | 2608397.302 | 1162798.7031 | 2608405.2424 | 1162800.9374 | 2608406.5851 | 1162801.5256
159 | 2608380.2547 | 1162801.3363 | 2608406.9498 | 1162741.4133
160 | 2608540.4174 | 1163128.2999 | 2608547.2742 | 1163132.7562
161 | 2608540.4174 | 1163128.2999 | 2608550.813 | 1163116.442 | 2608565.1793 | 1163102.4665 | 2608582.5386 | 1163089.8626
162 | 2608547.2742 | 1163132.7562 | 2608550.7178 | 1163134.9955 | 2608557.6994 | 1163137.8735 | 2608558.3184 | 1163138.262
163 | 2608582.5386 | 1163089.8626 | 2608586.0429 | 1163092.6244 | 2608590.2209 | 1163095.5207 | 2608594.3245 | 1163096.9606 | 2608598.3606 | 1163097.3554 | 2608604.5246 | 1163098.7982 | 2608613.2502 | 1163098.7094
164 | 2608558.3184 | 1163138.262 | 2608564.1966 | 1163141.9513 | 2608572.0766 | 1163143.2187 | 2608583.581 | 1163143.4351 | 2608597.8907 | 1163142.4104 | 2608606.328 | 1163144.1255
165 | 2608613.2502 | 1163098.7094 | 2608617.294 | 1163098.6683
166 | 2608559.5165 | 1163050.5104 | 2608560.4141 | 1163054.2914 | 2608565.1396 | 1163054.7094 | 2608583.0041 | 1163049.7981
167 | 2608606.3441 | 1163059.3404 | 2608604.9947 | 1163059.068 | 2608596.6469 | 1163052.7308 | 2608589.599 | 1163047.9851 | 2608583.0041 | 1163049.7981
168 | 2608645.0361 | 1163067.0067 | 2608631.976 | 1163061.7855 | 2608611.1513 | 1163060.3107 | 2608606.3441 | 1163059.3404
169 | 2608645.0361 | 1163067.0067 | 2608655.9512 | 1163072.3361 | 2608674.401 | 1163090.1046 | 2608676.8696 | 1163093.91
170 | 2608645.0361 | 1163067.0067 | 2608646.5983 | 1163061.8842 | 2608645.9898 | 1163048.1321 | 2608644.4589 | 1163020.6162 | 2608639.7861 | 1162999.3435 | 2608636.6188 | 1162977.6271
171 | 2608645.0361 | 1163067.0067 | 2608632.3278 | 1163074.5409
172 | 2608676.8696 | 1163093.91 | 2608669.6406 | 1163098.0684 | 2608664.0917 | 1163100.3171 | 2608659.6509 | 1163104.4239 | 2608655.4623 | 1163108.9091 | 2608652.9901 | 1163112.9965
173 | 2608676.8696 | 1163093.91 | 2608682.3582 | 1163102.3869
174 | 2608635.3351 | 1162968.8259 | 2608636.6188 | 1162977.6271
175 | 2608652.9901 | 1163112.9965 | 2608648.5415 | 1163111.7895 | 2608639.8569 | 1163105.4073 | 2608634.2096 | 1163102.9995
176 | 2608652.9901 | 1163112.9965 | 2608652.854 | 1163117.1205 | 2608655.0314 | 1163120.9922 | 2608655.0314 | 1163120.9922
177 | 2608723.3274 | 1163156.4522 | 2608696.4453 | 1163122.3189 | 2608689.8088 | 1163113.8941 | 2608682.3582 | 1163102.3869
178 | 2608631.7149 | 1162944.0045 | 2608635.3351 | 1162968.8259
179 | 2608606.328 | 1163144.1255 | 2608613.0906 | 1163145.5002 | 2608614.707 | 1163146.1078
180 | 2608634.2096 | 1163102.9995 | 2608628.7648 | 1163100.678 | 2608621.7821 | 1163098.6226 | 2608617.294 | 1163098.6683
181 | 2608631.7149 | 1162944.0045 | 2608642.9696 | 1162937.0616 | 2608666.1992 | 1162922.9655 | 2608679.3532 | 1162916.2255 | 2608680.5351 | 1162915.7446
182 | 2608698.415 | 1162796.2155 | 2608665.7318 | 1162842.7584 | 2608640.8937 | 1162883.3653 | 2608632.0713 | 1162914.3014 | 2608631.7149 | 1162944.0045
183 | 2608680.5351 | 1162915.7446 | 2608686.8413 | 1162913.1791 | 2608691.7681 | 1162912.1635 | 2608697.4427 | 1162913.1721 | 2608702.8611 | 1162916.4815 | 2608707.9023 | 1162921.18 | 2608715.4967 | 1162929.3839 | 2608734.1664 | 1162948.8649 | 2608756.1339 | 1162974.7006
184 | 2608698.415 | 1162796.2155 | 2608696.5606 | 1162791.2993 | 2608696.1529 | 1162787.2078 | 2608697.7923 | 1162716.3638
185 | 2608698.415 | 1162796.2155 | 2608725.7469 | 1162763.7387 | 2608757.3541 | 1162740.5412
186 | 2608764.9219 | 1162990.4855 | 2608761.5257 | 1162981.8985 | 2608756.3118 | 1162974.9097 | 2608756.1339 | 1162974.7006
187 | 2608655.0314 | 1163120.9922 | 2608657.5015 | 1163123.8901
188 | 2608723.3274 | 1163156.4522 | 2608726.9438 | 1163166.3735 | 2608732.1867 | 1163179.6765
189 | 2608723.3274 | 1163156.4522 | 2608765.6626 | 1163193.1093
190 | 2608711.6072 | 1163205.0372 | 2608711.4057 | 1163201.3462 | 2608708.6171 | 1163196.4509 | 2608701.5674 | 1163187.8143 | 2608697.9634 | 1163183.5127
191 | 2608686.3793 | 1163157.7683 | 2608690.5048 | 1163162.6081 | 2608690.4986 | 1163166.9102 | 2608690.9046 | 1163172.2357 | 2608693.1562 | 1163177.775 | 2608697.9634 | 1163183.5127
192 | 2608663.6153 | 1163131.0625 | 2608657.5015 | 1163123.8901
193 | 2608672.7642 | 1163141.7956 | 2608663.6153 | 1163131.0625
194 | 2608676.2757 | 1163145.9152 | 2608672.7642 | 1163141.7956
195 | 2608676.2757 | 1163145.9152 | 2608686.3793 | 1163157.7683
196 | 2608777.6461 | 1163212.5611 | 2608779.6782 | 1163215.185 | 2608782.3387 | 1163218.6795 | 2608783.5671 | 1163221.9495 | 2608785.1252 | 1163225.0089 | 2608786.9845 | 1163227.7007
197 | 2608765.6626 | 1163193.1093 | 2608766.8811 | 1163197.9468 | 2608769.4255 | 1163202.2748 | 2608774.2654 | 1163208.1959 | 2608777.6461 | 1163212.5611
198 | 2608765.6626 | 1163193.1093 | 2608775.9824 | 1163202.0509 | 2608785.8821 | 1163211.0722
199 | 2608810.573 | 1163233.5723 | 2608785.8821 | 1163211.0722
200 | 2608810.573 | 1163233.5723 | 2608856.9923 | 1163275.8821
201 | 2608951.5103 | 1163395.7183 | 2608960.0365 | 1163407.1777 | 2608961.8441 | 1163409.6336
202 | 2608965.8435 | 1163415.0671 | 2608961.8441 | 1163409.6336
203 | 2608931.025 | 1163368.1854 | 2608951.5103 | 1163395.7183
204 | 2608995.3605 | 1163455.1686 | 2608965.8435 | 1163415.0671
205 | 2608931.025 | 1163368.1854 | 2608928.1775 | 1163364.3584
206 | 2609006.4564 | 1163470.2435 | 2608995.3605 | 1163455.1686
207 | 2608928.1775 | 1163364.3584 | 2608909.6557 | 1163339.4644
208 | 2609006.4564 | 1163470.2435 | 2609011.2004 | 1163476.6886
209 | 2608897.1743 | 1163322.6891 | 2608909.6557 | 1163339.4644
210 | 2609011.2004 | 1163476.6886 | 2609026.9392 | 1163498.0713
211 | 2608897.1743 | 1163322.6891 | 2608887.9822 | 1163310.3346 | 2608886.7675 | 1163308.7862
212 | 2608886.7675 | 1163308.7862 | 2608870.8953 | 1163288.5543 | 2608856.9923 | 1163275.8821
213 | 2608209.6931 | 1162795.6408 | 2608208.8235 | 1162800.6681 | 2608209.6054 | 1162828.5274 | 2608209.6737 | 1162834.6861 | 2608206.5097 | 1162840.607 | 2608200.3362 | 1162845.9235 | 2608200.3362 | 1162845.9235
214 | 2609503.4973 | 1163004.9177 | 2609508.5498 | 1163006.8266 | 2609515.9431 | 1163005.8155
215 | 2609503.4973 | 1163004.9177 | 2609497.463 | 1162999.0275 | 2609488.528 | 1162986.6741 | 2609483.8154 | 1162978.0624 | 2609481.7661 | 1162975.8025 | 2609479.2987 | 1162976.4212 | 2609477.2391 | 1162980.709 | 2609476.1951 | 1162987.0661 | 2609477.4174 | 1162994.027 | 2609479.8768 | 1162998.5331 | 2609485.3196 | 1163006.2238
216 | 2609525.7963 | 1162935.9408 | 2609512.2056 | 1162951.894 | 2609502.1106 | 1162970.9209 | 2609499.6226 | 1162984.646 | 2609500.6333 | 1162994.6748 | 2609503.4973 | 1163004.9177
217 | 2609119.3043 | 1163660.9192 | 2609116.4793 | 1163655.101 | 2609112.2362 | 1163639.8425 | 2609109.9245 | 1163623.6977 | 2609105.1232 | 1163607.8604 | 2609100.7919 | 1163595.1698 | 2609096.5327 | 1163582.9443
218 | 2609119.3043 | 1163660.9192 | 2609130.6961 | 1163684.4147 | 2609133.7265 | 1163690.6937

## bus_geodata
| x | y | coords
0 | 2607774.9077 | 1164986.0976
1 | 2607878.2382 | 1164992.2954
2 | 2607760.5178 | 1164990.4426
3 | 2607764.449 | 1165053.8569
4 | 2607722.695 | 1164930.6531
5 | 2608622.1131 | 1164270.0603
6 | 2608665.3684 | 1164043.9763
7 | 2607773.1331 | 1165148.6374
8 | 2607713.0878 | 1165020.8182
9 | 2607438.8529 | 1164814.552
10 | 2607521.7391 | 1165053.9622
11 | 2607932.0835 | 1165149.5214
12 | 2607691.7239 | 1165015.4007
13 | 2607300.9048 | 1164546.1844
14 | 2608587.1039 | 1163354.5226
15 | 2608447.0514 | 1163556.5786
16 | 2608539.3845 | 1163169.1597
17 | 2607576.7099 | 1165011.1649
18 | 2607973.7649 | 1165130.2002
19 | 2608079.9154 | 1165055.2637
20 | 2608073.1324 | 1165083.0636
21 | 2608076.8487 | 1165086.8149
22 | 2608041.1994 | 1165096.5723
23 | 2608104.8674 | 1165080.2268
24 | 2608097.973 | 1165122.4942
25 | 2608018.639 | 1165058.001
26 | 2608099.5272 | 1165130.8818
27 | 2607532.5075 | 1164042.2832
28 | 2608124.713 | 1163836.8133
29 | 2608294.3409 | 1163868.0698
30 | 2608050.4187 | 1163722.905
31 | 2609226.2255 | 1163402.0308
32 | 2609041.5628 | 1163517.9388
33 | 2608161.7493 | 1163432.1058
34 | 2608326.4133 | 1163710.6228
35 | 2608168.9113 | 1163354.1776
36 | 2608333.5554 | 1163717.2466
37 | 2608345.6302 | 1163508.1725
38 | 2608161.8672 | 1163352.3338
39 | 2608347.0464 | 1163727.177
40 | 2608387.1656 | 1163502.7939
41 | 2608444.2063 | 1163658.3852
42 | 2608104.994 | 1163333.1617
43 | 2608134.9061 | 1163380.9896
44 | 2608486.312 | 1163105.0052
45 | 2608535.4285 | 1163130.944
46 | 2608485.2445 | 1163103.3031
47 | 2608347.067 | 1163727.1944
48 | 2608553.985 | 1163783.1949
49 | 2608030.2626 | 1163292.7186
50 | 2608088.848 | 1163393.2934
51 | 2607893.8072 | 1163144.9093
52 | 2607852.7953 | 1163084.6961
53 | 2607901.6929 | 1163147.7988
54 | 2607944.321 | 1163216.1217
55 | 2608009.0379 | 1163280.6322
56 | 2607914.7609 | 1163168.9159
57 | 2608149.2032 | 1162830.7025
58 | 2608157.1551 | 1162833.3297
59 | 2608484.5598 | 1163102.2114
60 | 2608463.5971 | 1163068.6146
61 | 2608192.1832 | 1162844.7945
62 | 2609487.3705 | 1162745.263
63 | 2609495.8682 | 1162764.6998
64 | 2609430.9233 | 1162580.4937
65 | 2609512.444 | 1162805.1326
66 | 2609441.2792 | 1162585.9903
67 | 2609431.0124 | 1162578.1017
68 | 2609016.6098 | 1163048.1851
69 | 2609056.5329 | 1163119.4142
70 | 2609175.9757 | 1162896.2808
71 | 2608858.3608 | 1163160.1945
72 | 2609521.7708 | 1162811.9618
73 | 2609276.3826 | 1162681.0826
74 | 2609445.371 | 1162599.9258
75 | 2609488.1495 | 1162611.4474
76 | 2609425.4598 | 1162548.0619
77 | 2609529.9497 | 1162995.6082
78 | 2609304.8175 | 1162745.7472
79 | 2609176.3322 | 1162738.7972
80 | 2609213.964 | 1162573.5915
81 | 2609546.0382 | 1162564.077
82 | 2609415.8822 | 1162530.1632
83 | 2609380.2918 | 1162375.3401
84 | 2608917.5041 | 1162190.4226
85 | 2609131.1886 | 1162154.4009
86 | 2608759.3479 | 1162386.6863
87 | 2609380.0759 | 1162351.0644
88 | 2609524.4583 | 1163002.4939
89 | 2609174.6367 | 1162758.6806
90 | 2609171.6031 | 1162501.1116
91 | 2609388.029 | 1162252.7821
92 | 2609445.2332 | 1162158.1288
93 | 2609416.6454 | 1162100.8478
94 | 2609429.3531 | 1162080.5601
95 | 2609198.2682 | 1162214.3209
96 | 2609199.4695 | 1162195.1628
97 | 2609176.937 | 1162282.3223
98 | 2609219.4014 | 1162115.7042
99 | 2609166.5887 | 1162301.694
100 | 2609203.0456 | 1162044.922
101 | 2609223.4564 | 1162134.2307
102 | 2609179.0921 | 1162457.5791
103 | 2609192.0851 | 1162023.1613
104 | 2609215.7162 | 1162156.1297
105 | 2609009.7972 | 1161812.5942
106 | 2609153.0346 | 1162161.3595
107 | 2609537.1021 | 1162548.3108
108 | 2609527.0227 | 1162546.1827
109 | 2609484.1818 | 1162431.955
110 | 2609510.91 | 1161997.1963
111 | 2609555.6531 | 1162212.5369
112 | 2608737.4885 | 1162616.0602
113 | 2608708.3522 | 1162641.3952
114 | 2609192.7014 | 1162817.9118
115 | 2609210.7977 | 1162845.9421
116 | 2609181.0034 | 1162813.6252
117 | 2609241.7569 | 1162892.7569
118 | 2609153.9701 | 1162849.7689
119 | 2609220.9923 | 1162876.6839
120 | 2609364.5612 | 1163056.1266
121 | 2609170.7403 | 1162888.5322
122 | 2609392.6309 | 1163093.3406
123 | 2609404.4704 | 1163109.037
124 | 2609344.1703 | 1163071.4361
125 | 2609436.1758 | 1163164.2656
126 | 2608408.5833 | 1162971.8433
127 | 2608408.7501 | 1162972.1297
128 | 2608370.6734 | 1162919.387
129 | 2608423.8273 | 1162998.2843
130 | 2608367.3056 | 1162914.8859
131 | 2608433.6126 | 1163016.6341
132 | 2608357.5801 | 1162899.4803
133 | 2608443.7913 | 1163035.7218
134 | 2608355.1682 | 1162895.6596
135 | 2608473.3818 | 1162622.394
136 | 2608456.1954 | 1162615.6053
137 | 2608451.264 | 1162625.7305
138 | 2608433.7309 | 1162677.109
139 | 2608418.1216 | 1162716.3356
140 | 2609011.1776 | 1161807.0425
141 | 2608325.0152 | 1162858.6421
142 | 2608347.6005 | 1162886.5594
143 | 2608233.6237 | 1162729.6554
144 | 2608240.8884 | 1162681.722
145 | 2608220.1985 | 1162744.3667
146 | 2608363.9189 | 1162838.0109
147 | 2608225.6458 | 1162615.0792
148 | 2608218.5193 | 1162752.2529
149 | 2608374.6335 | 1162813.9563
150 | 2608222.0369 | 1162603.2109
151 | 2608218.1528 | 1162753.9739
152 | 2608380.2547 | 1162801.3363
153 | 2608406.5851 | 1162801.5256
154 | 2608406.9498 | 1162741.4133
155 | 2608481.3693 | 1162723.4273
156 | 2608540.4174 | 1163128.2999
157 | 2608547.2742 | 1163132.7562
158 | 2608582.5386 | 1163089.8626
159 | 2608558.3184 | 1163138.262
160 | 2608613.2502 | 1163098.7094
161 | 2608559.5165 | 1163050.5104
162 | 2608583.0041 | 1163049.7981
163 | 2608606.3441 | 1163059.3404
164 | 2608645.036 | 1163067.0067
165 | 2608676.8696 | 1163093.91
166 | 2608636.6188 | 1162977.6271
167 | 2608632.3278 | 1163074.5409
168 | 2608652.9901 | 1163112.9965
169 | 2608682.3582 | 1163102.3869
170 | 2608635.3351 | 1162968.8259
171 | 2608606.328 | 1163144.1255
172 | 2608617.294 | 1163098.6683
173 | 2608631.7149 | 1162944.0045
174 | 2608680.5351 | 1162915.7446
175 | 2608698.415 | 1162796.2155
176 | 2608756.1339 | 1162974.7006
177 | 2608697.7923 | 1162716.3638
178 | 2608757.3541 | 1162740.5412
179 | 2608764.9219 | 1162990.4855
180 | 2608634.2096 | 1163102.9995
181 | 2608655.0314 | 1163120.9922
182 | 2608723.3274 | 1163156.4522
183 | 2608614.707 | 1163146.1078
184 | 2608711.6072 | 1163205.0372
185 | 2608697.9634 | 1163183.5127
186 | 2608663.6153 | 1163131.0625
187 | 2608657.5015 | 1163123.8901
188 | 2608672.7642 | 1163141.7956
189 | 2608676.2757 | 1163145.9152
190 | 2608686.3793 | 1163157.7683
191 | 2608786.9845 | 1163227.7007
192 | 2608777.6461 | 1163212.5611
193 | 2608765.6626 | 1163193.1093
194 | 2608785.8821 | 1163211.0722
195 | 2608810.573 | 1163233.5723
196 | 2608732.1867 | 1163179.6765
197 | 2608961.8441 | 1163409.6336
198 | 2608951.5103 | 1163395.7183
199 | 2608965.8435 | 1163415.0671
200 | 2608931.025 | 1163368.1854
201 | 2608995.3605 | 1163455.1686
202 | 2608928.1775 | 1163364.3584
203 | 2609006.4564 | 1163470.2435
204 | 2608909.6557 | 1163339.4644
205 | 2609011.2004 | 1163476.6886
206 | 2608219.7077 | 1162590.4321
207 | 2608897.1743 | 1163322.6891
208 | 2608886.7675 | 1163308.7862
209 | 2608856.9923 | 1163275.8821
210 | 2608209.6931 | 1162795.6408
211 | 2608200.3362 | 1162845.9235
212 | 2609515.9431 | 1163005.8155
213 | 2609503.4973 | 1163004.9177
214 | 2609485.3196 | 1163006.2238
215 | 2609525.7963 | 1162935.9408
216 | 2609026.9392 | 1163498.0713
217 | 2609096.5327 | 1163582.9443
218 | 2609119.3043 | 1163660.9192
219 | 2609133.7265 | 1163690.6937
220 | 2608652.9901 | 1163112.9965

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1