## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_763-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_763-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_763-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_763-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_763-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_763-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_763-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_763-3_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_763-3_0_3_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_763-3_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_763-3_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_763-3_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_763-3_0_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_763-3_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_763-3_0_3_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_763-3_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_763-3_0_3_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_763-3_0_3_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_763-3_0_3_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_763-3_0_3_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_763-3_0_3_node_50 | 0.4 | n |  | TRUE
21 | bus_LV_763-3_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_763-3_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_763-3_0_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_763-3_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_763-3_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_763-3_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_763-3_0_3_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_763-3_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_763-3_0_3_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_763-3_0_3_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_763-3_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_763-3_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_763-3_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_763-3_0_3_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_763-3_0_3_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_763-3_0_3_node_76 | 0.4 | n |  | TRUE
37 | bus_LV_763-3_0_3_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_763-3_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_763-3_0_3_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_763-3_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_763-3_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_763-3_0_3_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_763-3_0_3_node_66 | 0.4 | n |  | TRUE
44 | bus_LV_763-3_0_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_763-3_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_763-3_0_3_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_763-3_0_3_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_763-3_0_3_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_763-3_0_3_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_763-3_0_3_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_763-3_0_3_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_763-3_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_763-3_0_3_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_763-3_0_3_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_763-3_0_3_node_64 | 0.4 | n |  | TRUE
56 | bus_LV_763-3_0_3_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_763-3_0_3_node_63 | 0.4 | n |  | TRUE
58 | bus_LV_763-3_0_3_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_763-3_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_763-3_0_3_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_763-3_0_3_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_763-3_0_3_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_763-3_0_3_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_763-3_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_763-3_0_3_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_763-3_0_3_node_70 | 0.4 | n |  | TRUE
67 | bus_LV_763-3_0_3_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_763-3_0_3_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_763-3_0_3_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_763-3_0_3_node_74 | 0.4 | n |  | TRUE
71 | bus_MV_208_0_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_763-3_0_3_load_0 | 0 | 0.0033296 | 0.00083447 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_763-3_0_3_load_1 | 1 | 0.0010532 | 0.00026395 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_763-3_0_3_load_3 | 3 | 0.0028036 | 0.00070266 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_763-3_0_3_load_6 | 6 | 0.0091433 | 0.0022915 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_763-3_0_3_load_16 | 7 | 0.0018105 | 0.00045376 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_763-3_0_3_load_23 | 8 | 0.0053099 | 0.0013308 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_763-3_0_3_load_29 | 10 | 0.00095462 | 0.00023925 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_763-3_0_3_load_7 | 11 | 0.00070153 | 0.00017582 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_763-3_0_3_load_14 | 12 | 0.0067908 | 0.0017019 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_763-3_0_3_load_21 | 13 | 0.0015447 | 0.00038715 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_763-3_0_3_load_13 | 14 | 0.0028312 | 0.00070955 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_763-3_0_3_load_9 | 15 | 0.0050025 | 0.0012537 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_763-3_0_3_load_27 | 16 | 0.0010284 | 0.00025775 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_763-3_0_3_load_8 | 17 | 0.0017526 | 0.00043925 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_763-3_0_3_load_48 | 19 | 0.0035595 | 0.0008921 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_763-3_0_3_load_50 | 20 | 0.00097282 | 0.00024381 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_763-3_0_3_load_19 | 22 | 0.0023456 | 0.00058787 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_763-3_0_3_load_36 | 23 | 0.0062389 | 0.0015636 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_763-3_0_3_load_18 | 24 | 0.0012042 | 0.0003018 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_763-3_0_3_load_15 | 25 | 0.0017832 | 0.00044691 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_763-3_0_3_load_20 | 26 | 0.0023776 | 0.00059587 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_763-3_0_3_load_22 | 27 | 0.0020589 | 0.00051602 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_763-3_0_3_load_24 | 28 | 0.0014409 | 0.00036114 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_763-3_0_3_load_72 | 29 | 0.0024675 | 0.00061841 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_763-3_0_3_load_73 | 30 | 0.0042643 | 0.0010687 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_763-3_0_3_load_25 | 31 | 0.0016238 | 0.00040696 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_763-3_0_3_load_26 | 32 | 0.0014346 | 0.00035954 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_763-3_0_3_load_68 | 34 | 0.0046208 | 0.0011581 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_763-3_0_3_load_35 | 35 | 0.012007 | 0.0030092 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_763-3_0_3_load_76 | 36 | 0.010916 | 0.0027359 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_763-3_0_3_load_33 | 37 | 0.0035437 | 0.00088814 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_763-3_0_3_load_30 | 38 | 0.0092183 | 0.0023103 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_763-3_0_3_load_31 | 39 | 0.0054817 | 0.0013738 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_763-3_0_3_load_32 | 40 | 0.0010888 | 0.00027287 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_763-3_0_3_load_39 | 42 | 0.00051819 | 0.00012987 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_763-3_0_3_load_66 | 43 | 0.00065323 | 0.00016371 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_763-3_0_3_load_40 | 44 | 0.00083135 | 0.00020836 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_763-3_0_3_load_41 | 45 | 0.0013674 | 0.00034269 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_763-3_0_3_load_44 | 48 | 0.0067892 | 0.0017015 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_763-3_0_3_load_53 | 50 | 0.0018198 | 0.00045607 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_763-3_0_3_load_45 | 51 | 0.0015873 | 0.00039782 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_763-3_0_3_load_46 | 52 | 0.0010513 | 0.00026348 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_763-3_0_3_load_47 | 53 | 0.00059919 | 0.00015017 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_763-3_0_3_load_49 | 54 | 0.00059289 | 0.00014859 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_763-3_0_3_load_63 | 57 | 0.00042869 | 0.00010744 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_763-3_0_3_load_51 | 58 | 0.003201 | 0.00080224 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_763-3_0_3_load_54 | 59 | 0.0027662 | 0.00069326 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_763-3_0_3_load_57 | 60 | 0.017224 | 0.0043169 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_763-3_0_3_load_60 | 63 | 0.026165 | 0.0065576 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_763-3_0_3_load_69 | 64 | 0.0027423 | 0.00068729 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_763-3_0_3_load_61 | 65 | 0.0014433 | 0.00036172 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_763-3_0_3_load_70 | 66 | 0.001329 | 0.00033308 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_763-3_0_3_load_62 | 67 | 0.0066943 | 0.0016778 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_763-3_0_3_load_65 | 68 | 0.0021405 | 0.00053647 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_763-3_0_3_load_71 | 69 | 0.003462 | 0.00086765 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_763-3_0_3_load_74 | 70 | 0.0037081 | 0.00092935 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_763-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0083426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_763-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.018177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_763-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0036835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_763-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_763-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.012019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_763-3_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0087091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_763-3_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0085703 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_763-3_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.019528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_763-3_0_3_line_8 | NAYY 4x150 SE | 5 | 9 | 0.01726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_763-3_0_3_line_9 | NAYY 4x150 SE | 5 | 10 | 0.0094827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_763-3_0_3_line_10 | NAYY 4x150 SE | 6 | 11 | 0.0002448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_763-3_0_3_line_11 | NAYY 4x150 SE | 7 | 12 | 0.005826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_763-3_0_3_line_12 | NAYY 4x150 SE | 8 | 13 | 0.0083056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_763-3_0_3_line_13 | NAYY 4x150 SE | 9 | 14 | 0.0090095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_763-3_0_3_line_14 | NAYY 4x150 SE | 9 | 15 | 0.0078469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_763-3_0_3_line_15 | NAYY 4x150 SE | 10 | 16 | 0.0056038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_763-3_0_3_line_16 | NAYY 4x150 SE | 11 | 17 | 0.0077266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_763-3_0_3_line_17 | NAYY 4x150 SE | 12 | 25 | 0.033776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_763-3_0_3_line_18 | NAYY 4x150 SE | 13 | 26 | 0.010534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_763-3_0_3_line_19 | NAYY 4x150 SE | 14 | 24 | 0.018543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_763-3_0_3_line_20 | NAYY 4x150 SE | 16 | 31 | 0.030008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_763-3_0_3_line_21 | NAYY 4x150 SE | 17 | 18 | 0.013617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_763-3_0_3_line_22 | NAYY 4x150 SE | 18 | 19 | 0.013088 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_763-3_0_3_line_23 | NAYY 4x150 SE | 18 | 20 | 0.013288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_763-3_0_3_line_24 | NAYY 4x150 SE | 19 | 52 | 0.0040055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_763-3_0_3_line_25 | NAYY 4x150 SE | 20 | 58 | 0.03735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_763-3_0_3_line_26 | NAYY 4x150 SE | 21 | 22 | 0.017029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_763-3_0_3_line_27 | NAYY 4x150 SE | 21 | 23 | 0.048059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_763-3_0_3_line_28 | NAYY 4x150 SE | 22 | 24 | 0.0078343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_763-3_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.022309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_763-3_0_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.0019304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_763-3_0_3_line_31 | NAYY 4x150 SE | 28 | 29 | 0.014604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_763-3_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.036728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_763-3_0_3_line_33 | NAYY 4x150 SE | 30 | 70 | 0.030312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_763-3_0_3_line_34 | NAYY 4x150 SE | 31 | 32 | 0.0020966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_763-3_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0047175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_763-3_0_3_line_36 | NAYY 4x150 SE | 33 | 34 | 0.011944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_763-3_0_3_line_37 | NAYY 4x150 SE | 33 | 35 | 0.039167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_763-3_0_3_line_38 | NAYY 4x150 SE | 34 | 36 | 0.014619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_763-3_0_3_line_39 | NAYY 4x150 SE | 35 | 37 | 0.0057652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_763-3_0_3_line_40 | NAYY 4x150 SE | 36 | 69 | 0.0069343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_763-3_0_3_line_41 | NAYY 4x150 SE | 37 | 39 | 0.029146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_763-3_0_3_line_42 | NAYY 4x150 SE | 38 | 39 | 0.023544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_763-3_0_3_line_43 | NAYY 4x150 SE | 38 | 40 | 0.011562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_763-3_0_3_line_44 | NAYY 4x150 SE | 40 | 41 | 0.005436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_763-3_0_3_line_45 | NAYY 4x150 SE | 41 | 42 | 0.021658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_763-3_0_3_line_46 | NAYY 4x150 SE | 42 | 43 | 0.0050423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_763-3_0_3_line_47 | NAYY 4x150 SE | 44 | 45 | 0.049641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_763-3_0_3_line_48 | NAYY 4x150 SE | 44 | 46 | 0.010497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_763-3_0_3_line_49 | NAYY 4x150 SE | 45 | 47 | 0.0037591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_763-3_0_3_line_50 | NAYY 4x150 SE | 46 | 48 | 0.035034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_763-3_0_3_line_51 | NAYY 4x150 SE | 47 | 49 | 0.01644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_763-3_0_3_line_52 | NAYY 4x150 SE | 49 | 50 | 0.012078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_763-3_0_3_line_53 | NAYY 4x150 SE | 50 | 59 | 0.010206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_763-3_0_3_line_54 | NAYY 4x150 SE | 51 | 52 | 0.0086176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_763-3_0_3_line_55 | NAYY 4x150 SE | 51 | 53 | 0.0084949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_763-3_0_3_line_56 | NAYY 4x150 SE | 53 | 54 | 0.0031099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_763-3_0_3_line_57 | NAYY 4x150 SE | 54 | 55 | 0.048343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_763-3_0_3_line_58 | NAYY 4x150 SE | 55 | 56 | 0.037784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_763-3_0_3_line_59 | NAYY 4x150 SE | 55 | 57 | 0.035895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_763-3_0_3_line_60 | NAYY 4x150 SE | 56 | 59 | 0.035006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_763-3_0_3_line_61 | NAYY 4x150 SE | 57 | 68 | 0.017097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_763-3_0_3_line_62 | NAYY 4x150 SE | 60 | 61 | 0.023002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_763-3_0_3_line_63 | NAYY 4x150 SE | 61 | 62 | 0.039943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_763-3_0_3_line_64 | NAYY 4x150 SE | 61 | 63 | 0.017081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_763-3_0_3_line_65 | NAYY 4x150 SE | 62 | 64 | 0.055882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_763-3_0_3_line_66 | NAYY 4x150 SE | 63 | 65 | 0.074542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_763-3_0_3_line_67 | NAYY 4x150 SE | 64 | 66 | 0.0053648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_763-3_0_3_line_68 | NAYY 4x150 SE | 65 | 67 | 0.0018585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_763-3_0_3_line_69 | NAYY 4x150 SE | 66 | 69 | 0.0040287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_763-3_0_3_trafo_1 | 0.25 MVA 20/0.4 kV | 71 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2608745.7234 | 1167725.4264 | 2608744.7002 | 1167733.706
1 | 2608747.9528 | 1167707.3864 | 2608745.7234 | 1167725.4264
2 | 2608741.0681 | 1167734.3193 | 2608744.7002 | 1167733.706 | 2608744.7002 | 1167733.706
3 | 2608747.9528 | 1167707.3864 | 2608726.8983 | 1167701.2863
4 | 2608747.9528 | 1167707.3864 | 2608759.1976 | 1167711.716
5 | 2608732.4806 | 1167735.7696 | 2608741.0681 | 1167734.3193
6 | 2608726.8983 | 1167701.2863 | 2608729.3701 | 1167693.0802
7 | 2608726.8983 | 1167701.2863 | 2608707.8983 | 1167696.7778
8 | 2608767.6385 | 1167696.7651 | 2608762.5844 | 1167703.828 | 2608759.1976 | 1167711.716
9 | 2608759.1976 | 1167711.716 | 2608767.8754 | 1167715.5391
10 | 2608732.4806 | 1167735.7696 | 2608732.2392 | 1167735.8103
11 | 2608729.3701 | 1167693.0802 | 2608729.9977 | 1167690.9968 | 2608730.258 | 1167687.3559
12 | 2608707.8983 | 1167696.7778 | 2608699.8171 | 1167694.8602
13 | 2608767.6385 | 1167696.7651 | 2608776.2494 | 1167694.1151
14 | 2608767.6385 | 1167696.7651 | 2608769.0703 | 1167689.0499
15 | 2608773.0036 | 1167717.7985 | 2608767.8754 | 1167715.5391
16 | 2608724.8117 | 1167737.7079 | 2608726.9468 | 1167736.7041 | 2608732.2392 | 1167735.8103
17 | 2608716.2691 | 1167657.406 | 2608718.4971 | 1167662.2547 | 2608727.2493 | 1167675.4962 | 2608729.5015 | 1167679.5014 | 2608730.4976 | 1167684.0051 | 2608730.258 | 1167687.3559
18 | 2608699.8171 | 1167694.8602 | 2608689.5681 | 1167692.4282
19 | 2608793.9405 | 1167688.5702 | 2608792.8767 | 1167688.9979 | 2608776.2494 | 1167694.1151
20 | 2608773.0036 | 1167717.7985 | 2608775.6275 | 1167718.9545 | 2608800.9532 | 1167728.7123
21 | 2608713.2044 | 1167744.6994 | 2608716.9496 | 1167742.9483 | 2608722.7037 | 1167738.699 | 2608724.8117 | 1167737.7079
22 | 2608713.2044 | 1167744.6994 | 2608710.1991 | 1167748.1968 | 2608705.7795 | 1167755.4297
23 | 2608713.2044 | 1167744.6994 | 2608699.945 | 1167743.8289
24 | 2608705.7795 | 1167755.4297 | 2608703.691 | 1167758.8477
25 | 2608699.945 | 1167743.8289 | 2608688.9672 | 1167743.1082 | 2608689.4854 | 1167739.396 | 2608687.3018 | 1167735.6021 | 2608684.5027 | 1167734.0973 | 2608669.4926 | 1167733.0735
26 | 2608816.6648 | 1167678.5384 | 2608808.3618 | 1167682.7728 | 2608801.2094 | 1167685.6481
27 | 2608816.6648 | 1167678.5384 | 2608823.625 | 1167681.7723 | 2608862.6548 | 1167692.1429
28 | 2608793.9405 | 1167688.5702 | 2608801.2094 | 1167685.6481
29 | 2608668.8943 | 1167684.0443 | 2608689.5681 | 1167692.4282 | 2608689.5681 | 1167692.4282
30 | 2608667.1054 | 1167683.3188 | 2608668.8943 | 1167684.0443
31 | 2608667.1054 | 1167683.3188 | 2608662.5811 | 1167681.4841 | 2608654.0699 | 1167676.7864
32 | 2608654.0699 | 1167676.7864 | 2608640.0048 | 1167669.0233 | 2608626.5643 | 1167663.8905 | 2608620.5054 | 1167662.2544
33 | 2608590.3547 | 1167662.2039 | 2608605.1297 | 1167661.2031 | 2608616.9624 | 1167661.2978 | 2608620.5054 | 1167662.2544
34 | 2608802.9096 | 1167729.4661 | 2608800.9532 | 1167728.7123
35 | 2608807.3117 | 1167731.1621 | 2608802.9096 | 1167729.4661
36 | 2608807.3117 | 1167731.1621 | 2608804.8868 | 1167742.8575
37 | 2608807.3117 | 1167731.1621 | 2608810.3256 | 1167732.3227 | 2608844.8791 | 1167742.2003
38 | 2608806.066 | 1167756.1728 | 2608806.066 | 1167756.1728 | 2608802.9336 | 1167752.2774 | 2608804.8868 | 1167742.8575
39 | 2608850.4223 | 1167743.7848 | 2608844.8791 | 1167742.2003
40 | 2608806.066 | 1167756.1728 | 2608805.0995 | 1167762.8748 | 2608805.0783 | 1167763.0364
41 | 2608878.3709 | 1167752.0435 | 2608869.7781 | 1167749.318 | 2608850.4223 | 1167743.7848
42 | 2608878.3709 | 1167752.0435 | 2608900.8133 | 1167759.1619
43 | 2608912.0116 | 1167762.0283 | 2608902.0313 | 1167759.5482 | 2608900.8133 | 1167759.1619
44 | 2608917.2872 | 1167763.3392 | 2608912.0116 | 1167762.0283
45 | 2608917.2872 | 1167763.3392 | 2608916.1419 | 1167771.9085 | 2608917.6917 | 1167779.748 | 2608917.8915 | 1167784.7651
46 | 2608917.8915 | 1167784.7651 | 2608917.9795 | 1167786.9743 | 2608917.7358 | 1167789.7951
47 | 2608578.2568 | 1167710.1797 | 2608585.8329 | 1167716.1142 | 2608595.2682 | 1167722.7865 | 2608602.7761 | 1167728.4778 | 2608609.7366 | 1167731.6004 | 2608615.9864 | 1167733.966 | 2608620.6445 | 1167734.7806
48 | 2608569.8078 | 1167703.9521 | 2608576.8191 | 1167709.0535 | 2608578.2568 | 1167710.1797
49 | 2608623.69 | 1167736.5672 | 2608622.4599 | 1167735.098 | 2608620.6445 | 1167734.7806
50 | 2608569.8078 | 1167703.9521 | 2608581.3624 | 1167700.4112 | 2608592.2248 | 1167699.2482 | 2608604.3414 | 1167698.8541
51 | 2608623.69 | 1167736.5672 | 2608625.2182 | 1167738.3813 | 2608626.9662 | 1167741.6521 | 2608627.4661 | 1167745.3436 | 2608626.6072 | 1167751.9234
52 | 2608626.6072 | 1167751.9234 | 2608626.0191 | 1167756.3915 | 2608625.4107 | 1167763.9383
53 | 2608625.4107 | 1167763.9383 | 2608625.1776 | 1167766.8288 | 2608624.6808 | 1167774.118
54 | 2608699.1977 | 1167766.2011 | 2608699.1977 | 1167766.2011 | 2608703.691 | 1167758.8477
55 | 2608699.1977 | 1167766.2011 | 2608691.3323 | 1167769.4101
56 | 2608688.4528 | 1167770.5849 | 2608691.3323 | 1167769.4101
57 | 2608648.96 | 1167797.3669 | 2608653.4486 | 1167794.9499 | 2608657.7017 | 1167791.1985 | 2608661.4508 | 1167786.7017 | 2608667.949 | 1167781.1971 | 2608672.4541 | 1167777.9464 | 2608681.1996 | 1167774.446 | 2608686.9522 | 1167771.1971 | 2608688.4528 | 1167770.5849
58 | 2608612.2353 | 1167804.3736 | 2608616.9538 | 1167801.7012 | 2608628.2543 | 1167799.1049 | 2608637.5534 | 1167799.196 | 2608647.3527 | 1167797.398 | 2608648.96 | 1167797.3669
59 | 2608648.96 | 1167797.3669 | 2608652.5497 | 1167797.3053 | 2608663.7508 | 1167800.0005 | 2608670.8526 | 1167800.5998 | 2608679.6542 | 1167800.7014 | 2608684.4997 | 1167800.4032
60 | 2608612.2353 | 1167804.3736 | 2608623.4023 | 1167793.4285 | 2608624.021 | 1167788.9271 | 2608624.3412 | 1167779.1004 | 2608624.6808 | 1167774.118
61 | 2608701.4249 | 1167798.1981 | 2608691.6562 | 1167799.9627 | 2608684.4997 | 1167800.4032
62 | 2608765.7898 | 1167821.1135 | 2608762.3388 | 1167820.5415 | 2608742.8755 | 1167819.2778
63 | 2608765.7898 | 1167821.1135 | 2608779.1651 | 1167823.334 | 2608793.6348 | 1167825.7006 | 2608805.3037 | 1167827.6852
64 | 2608765.7898 | 1167821.1135 | 2608770.7001 | 1167812.8276 | 2608773.4969 | 1167810.6305 | 2608777.3864 | 1167810.4576
65 | 2608805.3037 | 1167827.6852 | 2608805.3969 | 1167800.4718 | 2608805.9988 | 1167786.5768 | 2608805.4022 | 1167781.0732 | 2608803.3039 | 1167776.579 | 2608803.858 | 1167772.3504
66 | 2608777.3864 | 1167810.4576 | 2608778.0971 | 1167810.426 | 2608794.3969 | 1167812.1283 | 2608798.6001 | 1167811.2228 | 2608801.597 | 1167808.2257 | 2608802.299 | 1167804.4248 | 2608802.5006 | 1167792.13 | 2608800.6005 | 1167788.2253 | 2608797.4972 | 1167785.4305 | 2608773.8197 | 1167780.3165
67 | 2608803.858 | 1167772.3504 | 2608804.555 | 1167767.031
68 | 2608772.003 | 1167779.9241 | 2608773.8197 | 1167780.3165
69 | 2608804.555 | 1167767.031 | 2608805.0783 | 1167763.0364

## bus_geodata
| x | y | coords
0 | 2608745.7234 | 1167725.4264
1 | 2608744.7002 | 1167733.706
2 | 2608747.9528 | 1167707.3864
3 | 2608741.0681 | 1167734.3193
4 | 2608726.8983 | 1167701.2863
5 | 2608759.1976 | 1167711.716
6 | 2608732.4806 | 1167735.7695
7 | 2608729.3701 | 1167693.0802
8 | 2608707.8983 | 1167696.7778
9 | 2608767.6385 | 1167696.7651
10 | 2608767.8754 | 1167715.5391
11 | 2608732.2392 | 1167735.8103
12 | 2608730.258 | 1167687.3559
13 | 2608699.8171 | 1167694.8602
14 | 2608776.2494 | 1167694.1151
15 | 2608769.0703 | 1167689.0499
16 | 2608773.0036 | 1167717.7985
17 | 2608724.8117 | 1167737.7079
18 | 2608713.2044 | 1167744.6994
19 | 2608705.7795 | 1167755.4297
20 | 2608699.945 | 1167743.8289
21 | 2608816.6648 | 1167678.5384
22 | 2608801.2094 | 1167685.6481
23 | 2608862.6548 | 1167692.1429
24 | 2608793.9405 | 1167688.5702
25 | 2608716.2691 | 1167657.406
26 | 2608689.5681 | 1167692.4282
27 | 2608668.8943 | 1167684.0443
28 | 2608667.1054 | 1167683.3188
29 | 2608654.0699 | 1167676.7864
30 | 2608620.5054 | 1167662.2545
31 | 2608800.9532 | 1167728.7123
32 | 2608802.9096 | 1167729.4661
33 | 2608807.3117 | 1167731.1621
34 | 2608804.8868 | 1167742.8575
35 | 2608844.8791 | 1167742.2003
36 | 2608806.066 | 1167756.1728
37 | 2608850.4223 | 1167743.7848
38 | 2608900.8133 | 1167759.1619
39 | 2608878.3709 | 1167752.0435
40 | 2608912.0116 | 1167762.0283
41 | 2608917.2872 | 1167763.3392
42 | 2608917.8915 | 1167784.7651
43 | 2608917.7358 | 1167789.7951
44 | 2608578.2568 | 1167710.1797
45 | 2608620.6445 | 1167734.7806
46 | 2608569.8078 | 1167703.9521
47 | 2608623.69 | 1167736.5672
48 | 2608604.3414 | 1167698.8541
49 | 2608626.6072 | 1167751.9234
50 | 2608625.4107 | 1167763.9383
51 | 2608699.1977 | 1167766.2011
52 | 2608703.691 | 1167758.8477
53 | 2608691.3323 | 1167769.4101
54 | 2608688.4528 | 1167770.5849
55 | 2608648.96 | 1167797.3669
56 | 2608612.2353 | 1167804.3736
57 | 2608684.4997 | 1167800.4032
58 | 2608669.4926 | 1167733.0735
59 | 2608624.6808 | 1167774.118
60 | 2608742.8755 | 1167819.2778
61 | 2608765.7898 | 1167821.1135
62 | 2608805.3037 | 1167827.6852
63 | 2608777.3864 | 1167810.4576
64 | 2608803.858 | 1167772.3504
65 | 2608773.8197 | 1167780.3165
66 | 2608804.555 | 1167767.031
67 | 2608772.003 | 1167779.9241
68 | 2608701.4249 | 1167798.1981
69 | 2608805.0783 | 1167763.0364
70 | 2608590.3547 | 1167662.2039
71 | 2608747.9528 | 1167707.3864

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1