## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_792-30_1_2_node_128 | 0.4 | n |  | TRUE
1 | bus_LV_792-30_1_2_node_51 | 0.4 | n |  | TRUE
2 | bus_LV_792-30_1_2_node_130 | 0.4 | n |  | TRUE
3 | bus_LV_792-30_1_2_node_129 | 0.4 | n |  | TRUE
4 | bus_LV_792-30_1_2_node_127 | 0.4 | n |  | TRUE
5 | bus_LV_792-30_1_2_node_124 | 0.4 | n |  | TRUE
6 | bus_LV_792-30_1_2_node_155 | 0.4 | n |  | TRUE
7 | bus_LV_792-30_1_2_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_792-30_1_2_node_156 | 0.4 | n |  | TRUE
9 | bus_LV_792-30_1_2_node_157 | 0.4 | n |  | TRUE
10 | bus_LV_792-30_1_2_node_76 | 0.4 | n |  | TRUE
11 | bus_LV_792-30_1_2_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_792-30_1_2_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_792-30_1_2_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_792-30_1_2_node_121 | 0.4 | n |  | TRUE
15 | bus_LV_792-30_1_2_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_792-30_1_2_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_792-30_1_2_node_49 | 0.4 | n |  | TRUE
18 | bus_LV_792-30_1_2_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_792-30_1_2_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_792-30_1_2_node_125 | 0.4 | n |  | TRUE
21 | bus_LV_792-30_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_792-30_1_2_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_792-30_1_2_node_54 | 0.4 | n |  | TRUE
24 | bus_LV_792-30_1_2_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_792-30_1_2_node_56 | 0.4 | n |  | TRUE
26 | bus_LV_792-30_1_2_node_57 | 0.4 | n |  | TRUE
27 | bus_LV_792-30_1_2_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_792-30_1_2_node_61 | 0.4 | n |  | TRUE
29 | bus_LV_792-30_1_2_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_792-30_1_2_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_792-30_1_2_node_63 | 0.4 | n |  | TRUE
32 | bus_LV_792-30_1_2_node_65 | 0.4 | n |  | TRUE
33 | bus_LV_792-30_1_2_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_792-30_1_2_node_66 | 0.4 | n |  | TRUE
35 | bus_LV_792-30_1_2_node_71 | 0.4 | n |  | TRUE
36 | bus_LV_792-30_1_2_node_67 | 0.4 | n |  | TRUE
37 | bus_LV_792-30_1_2_node_68 | 0.4 | n |  | TRUE
38 | bus_LV_792-30_1_2_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_792-30_1_2_node_69 | 0.4 | n |  | TRUE
40 | bus_LV_792-30_1_2_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_792-30_1_2_node_75 | 0.4 | n |  | TRUE
42 | bus_LV_792-30_1_2_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_792-30_1_2_node_73 | 0.4 | n |  | TRUE
44 | bus_LV_792-30_1_2_node_126 | 0.4 | n |  | TRUE
45 | bus_LV_792-30_1_2_node_78 | 0.4 | n |  | TRUE
46 | bus_LV_792-30_1_2_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_792-30_1_2_node_122 | 0.4 | n |  | TRUE
48 | bus_MV_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_792-30_1_2_load_128 | 0 | 0.00056532 | 0.00014168 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_792-30_1_2_load_130 | 2 | 0.00057754 | 0.00014475 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_792-30_1_2_load_129 | 3 | 0.00066656 | 0.00016705 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_792-30_1_2_load_127 | 4 | 0.00060293 | 0.00015111 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_792-30_1_2_load_124 | 5 | 0.00074108 | 0.00018573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_792-30_1_2_load_155 | 6 | 0.00040841 | 0.00010236 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_792-30_1_2_load_156 | 8 | 0.0005283 | 0.00013241 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_792-30_1_2_load_157 | 9 | 0.0010077 | 0.00025254 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_792-30_1_2_load_76 | 10 | 0.0035014 | 0.00087754 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_792-30_1_2_load_43 | 11 | 0.00061653 | 0.00015452 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_792-30_1_2_load_44 | 12 | 0.00033697 | 8.4454e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_792-30_1_2_load_45 | 13 | 0.00012841 | 3.2184e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_792-30_1_2_load_121 | 14 | 0.00053332 | 0.00013366 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_792-30_1_2_load_47 | 15 | 0.00019529 | 4.8943e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_792-30_1_2_load_48 | 16 | 0.00026742 | 6.7021e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_792-30_1_2_load_49 | 17 | 0.00040203 | 0.00010076 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_792-30_1_2_load_52 | 19 | 0.00028422 | 7.1231e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_792-30_1_2_load_125 | 20 | 0.00043145 | 0.00010813 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_792-30_1_2_load_53 | 22 | 0.00068436 | 0.00017152 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_792-30_1_2_load_56 | 25 | 0.0012168 | 0.00030496 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_792-30_1_2_load_58 | 27 | 0.0020269 | 0.00050799 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_792-30_1_2_load_61 | 28 | 0.00036538 | 9.1573e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_792-30_1_2_load_60 | 29 | 0.0011787 | 0.00029542 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_792-30_1_2_load_64 | 30 | 0.00067852 | 0.00017005 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_792-30_1_2_load_63 | 31 | 0.0005364 | 0.00013444 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_792-30_1_2_load_65 | 32 | 0.00048883 | 0.00012251 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_792-30_1_2_load_80 | 33 | 0.0039491 | 0.00098973 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_792-30_1_2_load_66 | 34 | 0.0011054 | 0.00027704 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_792-30_1_2_load_71 | 35 | 0.00091953 | 0.00023046 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_792-30_1_2_load_67 | 36 | 0.0006586 | 0.00016506 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_792-30_1_2_load_68 | 37 | 0.0017966 | 0.00045027 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_792-30_1_2_load_79 | 38 | 0.0015574 | 0.00039032 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_792-30_1_2_load_70 | 40 | 0.0011288 | 0.00028289 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_792-30_1_2_load_75 | 41 | 0.001888 | 0.00047318 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_792-30_1_2_load_72 | 42 | 0.0034993 | 0.00087702 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_792-30_1_2_load_73 | 43 | 0.00046187 | 0.00011576 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_792-30_1_2_load_126 | 44 | 0.00081549 | 0.00020438 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_792-30_1_2_load_78 | 45 | 0.002247 | 0.00056315 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_792-30_1_2_load_122 | 47 | 0.00087068 | 0.00021821 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_792-30_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.13776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_792-30_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0071687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_792-30_1_2_line_2 | NAYY 4x150 SE | 1 | 20 | 0.085317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_792-30_1_2_line_3 | NAYY 4x150 SE | 1 | 18 | 0.094636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_792-30_1_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.022566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_792-30_1_2_line_5 | NAYY 4x150 SE | 3 | 4 | 0.023983 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_792-30_1_2_line_6 | NAYY 4x150 SE | 4 | 44 | 0.049593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_792-30_1_2_line_7 | NAYY 4x150 SE | 5 | 47 | 0.024307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_792-30_1_2_line_8 | NAYY 4x150 SE | 6 | 7 | 0.010588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_792-30_1_2_line_9 | NAYY 4x150 SE | 6 | 8 | 0.019504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_792-30_1_2_line_10 | NAYY 4x150 SE | 7 | 27 | 0.0021581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_792-30_1_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.15229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_792-30_1_2_line_12 | NAYY 4x150 SE | 10 | 46 | 0.006003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_792-30_1_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.14044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_792-30_1_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.064192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_792-30_1_2_line_15 | NAYY 4x150 SE | 11 | 14 | 0.14577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_792-30_1_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.0036283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_792-30_1_2_line_17 | NAYY 4x150 SE | 14 | 47 | 0.017033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_792-30_1_2_line_18 | NAYY 4x150 SE | 15 | 16 | 0.012202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_792-30_1_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.013795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_792-30_1_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.058533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_792-30_1_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.12954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_792-30_1_2_line_22 | NAYY 4x150 SE | 20 | 39 | 0.086341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_792-30_1_2_line_23 | NAYY 4x150 SE | 21 | 29 | 0.0037294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_792-30_1_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.01264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_792-30_1_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.10912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_792-30_1_2_line_26 | NAYY 4x150 SE | 23 | 25 | 0.094753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_792-30_1_2_line_27 | NAYY 4x150 SE | 24 | 26 | 0.016201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_792-30_1_2_line_28 | NAYY 4x150 SE | 24 | 27 | 0.040766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_792-30_1_2_line_29 | NAYY 4x150 SE | 26 | 28 | 0.068493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_792-30_1_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.034792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_792-30_1_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.12712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_792-30_1_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.012981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_792-30_1_2_line_33 | NAYY 4x150 SE | 31 | 33 | 0.056291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_792-30_1_2_line_34 | NAYY 4x150 SE | 32 | 34 | 0.10365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_792-30_1_2_line_35 | NAYY 4x150 SE | 33 | 38 | 0.042241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_792-30_1_2_line_36 | NAYY 4x150 SE | 34 | 35 | 0.10087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_792-30_1_2_line_37 | NAYY 4x150 SE | 35 | 40 | 0.0015349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_792-30_1_2_line_38 | NAYY 4x150 SE | 36 | 37 | 0.026719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_792-30_1_2_line_39 | NAYY 4x150 SE | 37 | 38 | 0.066832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_792-30_1_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.028621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_792-30_1_2_line_41 | NAYY 4x150 SE | 39 | 41 | 0.11701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_792-30_1_2_line_42 | NAYY 4x150 SE | 41 | 45 | 0.038876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_792-30_1_2_line_43 | NAYY 4x150 SE | 41 | 46 | 0.08376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_792-30_1_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.0098577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_792-30_1_2_line_45 | NAYY 4x150 SE | 42 | 44 | 0.11615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_792-30_1_2_line_46 | NAYY 4x150 SE | 43 | 45 | 0.0042549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_792-30_1_2_trafo_71 | 0.25 MVA 20/0.4 kV | 48 | 35 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2600815.6045 | 1146299.6319 | 2600782.878 | 1146341.8151 | 2600776.6087 | 1146355.421 | 2600771.4442 | 1146379.6767 | 2600762.2172 | 1146398.4292 | 2600748.205 | 1146417.5369
1 | 2600742.2475 | 1146421.5242 | 2600748.205 | 1146417.5369 | 2600748.205 | 1146417.5369
2 | 2600815.6045 | 1146299.6319 | 2600820.2003 | 1146279.1558 | 2600831.9951 | 1146244.8517 | 2600836.3285 | 1146235.6477 | 2600845.7857 | 1146222.5425 | 2600846.9844 | 1146221.3063
3 | 2600815.6045 | 1146299.6319 | 2600816.2474 | 1146318.3188 | 2600823.571 | 1146351.2358 | 2600832.9837 | 1146384.82 | 2600838.1677 | 1146390.0121
4 | 2600742.2475 | 1146421.5242 | 2600723.4936 | 1146434.0756
5 | 2600744.5398 | 1146291.1681 | 2600738.67 | 1146305.1255 | 2600734.4326 | 1146312.8856
6 | 2600744.5398 | 1146291.1681 | 2600750.5021 | 1146276.9909 | 2600762.0881 | 1146251.7466 | 2600766.2106 | 1146246.8029
7 | 2600701.3616 | 1146444.1248 | 2600723.4936 | 1146434.0756 | 2600723.4936 | 1146434.0756
8 | 2601316.3192 | 1146115.169 | 2601326.7567 | 1146113.3898
9 | 2601345.9831 | 1146110.1123 | 2601326.7567 | 1146113.3898
10 | 2601316.3192 | 1146115.169 | 2601314.19 | 1146115.5213
11 | 2600807.6891 | 1146016.3595 | 2600902.2182 | 1145896.9581
12 | 2600807.6891 | 1146016.3595 | 2600806.5439 | 1146022.2511
13 | 2600708.0664 | 1146595.0877 | 2600699.458 | 1146600.8544 | 2600676.2995 | 1146612.2353 | 2600664.2086 | 1146627.6527 | 2600652.8017 | 1146638.8015 | 2600592.3465 | 1146671.5049
14 | 2600708.0664 | 1146595.0877 | 2600721.2267 | 1146586.2718 | 2600768.0049 | 1146574.0359
15 | 2600685.7925 | 1146451.0297 | 2600708.0664 | 1146595.0877
16 | 2600771.515 | 1146573.1177 | 2600768.0049 | 1146574.0359
17 | 2600701.3616 | 1146444.1248 | 2600690.3028 | 1146449.1461 | 2600685.7925 | 1146451.0297
18 | 2600771.515 | 1146573.1177 | 2600783.3199 | 1146570.0299
19 | 2600838.1677 | 1146390.0121 | 2600839.7417 | 1146403.7172
20 | 2600838.1677 | 1146390.0121 | 2600843.3526 | 1146387.7783 | 2600858.8489 | 1146359.4665 | 2600871.1735 | 1146342.9443
21 | 2600970.2377 | 1146264.6359 | 2600944.7892 | 1146271.2576 | 2600937.4143 | 1146277.8709 | 2600917.1252 | 1146301.3906 | 2600879.1381 | 1146332.2671 | 2600871.1735 | 1146342.9443
22 | 2600846.9844 | 1146221.3063 | 2600865.8833 | 1146137.0591
23 | 2600970.2377 | 1146264.6359 | 2600972.7421 | 1146261.8725
24 | 2601198.5318 | 1146207.3352 | 2601206.4923 | 1146197.5174
25 | 2601273.9706 | 1146122.175 | 2601247.2228 | 1146129.7734 | 2601233.9476 | 1146139.331 | 2601222.8829 | 1146158.4382 | 2601212.5456 | 1146190.0517 | 2601206.4923 | 1146197.5174
26 | 2601198.5318 | 1146207.3352 | 2601198.8369 | 1146218.8631 | 2601182.0019 | 1146248.6523 | 2601149.4705 | 1146285.3002
27 | 2601273.9706 | 1146122.175 | 2601281.2305 | 1146117.1851 | 2601288.2363 | 1146114.7186
28 | 2601273.9706 | 1146122.175 | 2601314.19 | 1146115.5213
29 | 2601288.2363 | 1146114.7186 | 2601288.4217 | 1146109.7162 | 2601283.1003 | 1146100.7775 | 2601253.5464 | 1146080.6952 | 2601239.5376 | 1146070.4541 | 2601239.5376 | 1146070.4541
30 | 2601239.5376 | 1146070.4541 | 2601207.9049 | 1146074.5723 | 2601205.1248 | 1146075.3689
31 | 2601089.8415 | 1146078.2419 | 2601089.8415 | 1146078.2419 | 2601123.531 | 1146083.8837 | 2601134.0005 | 1146085.2974 | 2601154.3078 | 1146097.4958 | 2601180.7014 | 1146094.9994 | 2601188.6839 | 1146086.141 | 2601197.2042 | 1146077.6384 | 2601205.1248 | 1146075.3689
32 | 2601089.8415 | 1146078.2419 | 2601076.8765 | 1146077.5934
33 | 2601089.8415 | 1146078.2419 | 2601123.309 | 1146123.503
34 | 2601076.8765 | 1146077.5934 | 2601047.4714 | 1146076.1227 | 2601007.4755 | 1146069.1352 | 2600984.0861 | 1146066.8749 | 2600973.9777 | 1146067.1308
35 | 2601123.309 | 1146123.503 | 2601121.7096 | 1146133.2964 | 2601117.9289 | 1146142.1334 | 2601112.2132 | 1146146.5234 | 2601098.107 | 1146152.9448
36 | 2600973.9777 | 1146067.1308 | 2600887.2782 | 1146118.6863
37 | 2600887.2782 | 1146118.6863 | 2600885.8212 | 1146119.169
38 | 2601037.9982 | 1146105.6695 | 2601034.5858 | 1146132.1698
39 | 2601034.5858 | 1146132.1698 | 2601098.107 | 1146152.9448
40 | 2600865.8833 | 1146137.0591 | 2600869.9403 | 1146127.4994 | 2600876.2089 | 1146122.3533 | 2600885.8212 | 1146119.169
41 | 2600865.8833 | 1146137.0591 | 2600760.2105 | 1146086.8092
42 | 2600760.2105 | 1146086.8092 | 2600757.0064 | 1146088.6443 | 2600751.2062 | 1146095.1357 | 2600742.0707 | 1146119.9883
43 | 2600806.5439 | 1146022.2511 | 2600801.764 | 1146039.2477 | 2600794.6568 | 1146054.9545 | 2600785.9594 | 1146072.0618 | 2600760.2105 | 1146086.8092
44 | 2600740.6027 | 1146123.9819 | 2600739.4802 | 1146133.7755
45 | 2600766.2106 | 1146246.8029 | 2600739.4802 | 1146133.7755
46 | 2600742.0707 | 1146119.9883 | 2600740.6027 | 1146123.9819 | 2600740.6027 | 1146123.9819

## bus_geodata
| x | y | coords
0 | 2600748.205 | 1146417.5369
1 | 2600815.6045 | 1146299.6319
2 | 2600742.2475 | 1146421.5242
3 | 2600734.4326 | 1146312.8856
4 | 2600744.5398 | 1146291.1681
5 | 2600723.4936 | 1146434.0756
6 | 2601326.7567 | 1146113.3898
7 | 2601316.3192 | 1146115.169
8 | 2601345.9831 | 1146110.1123
9 | 2600902.2182 | 1145896.9581
10 | 2600807.6891 | 1146016.3595
11 | 2600708.0664 | 1146595.0877
12 | 2600592.3465 | 1146671.5049
13 | 2600768.0049 | 1146574.0359
14 | 2600685.7925 | 1146451.0297
15 | 2600771.515 | 1146573.1177
16 | 2600783.3199 | 1146570.0299
17 | 2600839.7417 | 1146403.7172
18 | 2600838.1677 | 1146390.0121
19 | 2600871.1735 | 1146342.9443
20 | 2600846.9844 | 1146221.3063
21 | 2600970.2377 | 1146264.6359
22 | 2601206.4923 | 1146197.5174
23 | 2601198.5318 | 1146207.3352
24 | 2601273.9706 | 1146122.175
25 | 2601149.4705 | 1146285.3002
26 | 2601288.2363 | 1146114.7186
27 | 2601314.19 | 1146115.5213
28 | 2601239.5376 | 1146070.4541
29 | 2600972.7421 | 1146261.8725
30 | 2601205.1248 | 1146075.3689
31 | 2601089.8415 | 1146078.2419
32 | 2601076.8765 | 1146077.5934
33 | 2601123.309 | 1146123.503
34 | 2600973.9777 | 1146067.1308
35 | 2600887.2782 | 1146118.6863
36 | 2601037.9982 | 1146105.6695
37 | 2601034.5858 | 1146132.1698
38 | 2601098.107 | 1146152.9448
39 | 2600865.8833 | 1146137.0591
40 | 2600885.8212 | 1146119.169
41 | 2600760.2105 | 1146086.8092
42 | 2600739.4802 | 1146133.7755
43 | 2600740.6027 | 1146123.9819
44 | 2600766.2106 | 1146246.8029
45 | 2600742.0707 | 1146119.9883
46 | 2600806.5439 | 1146022.2511
47 | 2600701.3616 | 1146444.1248
48 | 2600887.2782 | 1146118.6863

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1