## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_852-5_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_852-5_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_852-5_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_852-5_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_852-5_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_852-5_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_852-5_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_852-5_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_852-5_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_852-5_0_2_node_174 | 0.4 | n |  | TRUE
10 | bus_LV_852-5_0_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_852-5_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_852-5_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_852-5_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_852-5_0_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_852-5_0_2_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_852-5_0_2_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_852-5_0_2_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_852-5_0_2_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_852-5_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_852-5_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_852-5_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_852-5_0_2_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_852-5_0_2_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_852-5_0_2_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_852-5_0_2_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_852-5_0_2_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_852-5_0_2_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_852-5_0_2_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_852-5_0_2_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_852-5_0_2_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_852-5_0_2_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_852-5_0_2_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_852-5_0_2_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_852-5_0_2_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_852-5_0_2_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_852-5_0_2_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_852-5_0_2_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_852-5_0_2_node_50 | 0.4 | n |  | TRUE
39 | bus_LV_852-5_0_2_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_852-5_0_2_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_852-5_0_2_node_53 | 0.4 | n |  | TRUE
42 | bus_LV_852-5_0_2_node_172 | 0.4 | n |  | TRUE
43 | bus_LV_852-5_0_2_node_173 | 0.4 | n |  | TRUE
44 | bus_LV_852-5_0_2_node_175 | 0.4 | n |  | TRUE
45 | bus_LV_852-5_0_2_node_54 | 0.4 | n |  | TRUE
46 | bus_MV_0_node_16 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_852-5_0_2_load_0 | 0 | 0.00051355 | 0.00012871 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_852-5_0_2_load_1 | 1 | 0.00074259 | 0.00018611 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_852-5_0_2_load_2 | 2 | 0.00010426 | 2.6129e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_852-5_0_2_load_5 | 5 | 0.00053659 | 0.00013448 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_852-5_0_2_load_6 | 6 | 0.00031275 | 7.8383e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_852-5_0_2_load_8 | 8 | 0.007208 | 0.0018065 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_852-5_0_2_load_9 | 11 | 0.00054657 | 0.00013698 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_852-5_0_2_load_12 | 14 | 0.001302 | 0.00032631 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_852-5_0_2_load_13 | 15 | 0.0019271 | 0.00048297 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_852-5_0_2_load_16 | 17 | 0.0021715 | 0.00054424 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_852-5_0_2_load_15 | 18 | 0.00017716 | 4.4399e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_852-5_0_2_load_17 | 19 | 0.0012759 | 0.00031978 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_852-5_0_2_load_18 | 20 | 0.0013045 | 0.00032693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_852-5_0_2_load_19 | 21 | 0.00060665 | 0.00015204 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_852-5_0_2_load_47 | 23 | 0.00025277 | 6.335e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_852-5_0_2_load_38 | 24 | 0.0013104 | 0.00032841 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_852-5_0_2_load_45 | 25 | 0.00089112 | 0.00022334 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_852-5_0_2_load_33 | 26 | 0.0027016 | 0.00067708 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_852-5_0_2_load_42 | 27 | 0.0009282 | 0.00023263 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_852-5_0_2_load_26 | 28 | 0.00021266 | 5.3298e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_852-5_0_2_load_34 | 29 | 0.00026793 | 6.7149e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_852-5_0_2_load_36 | 31 | 0.00045953 | 0.00011517 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_852-5_0_2_load_39 | 32 | 0.0027403 | 0.00068677 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_852-5_0_2_load_40 | 33 | 0.00045398 | 0.00011378 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_852-5_0_2_load_41 | 34 | 0.0010144 | 0.00025424 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_852-5_0_2_load_43 | 35 | 0.00020026 | 5.019e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_852-5_0_2_load_44 | 36 | 0.0016219 | 0.00040648 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_852-5_0_2_load_50 | 38 | 0.00018664 | 4.6777e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_852-5_0_2_load_53 | 41 | 0.00067867 | 0.00017009 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_852-5_0_2_load_172 | 42 | 0.00044941 | 0.00011263 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_852-5_0_2_load_173 | 43 | 0.00217 | 0.00054385 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_852-5_0_2_load_175 | 44 | 0.0004091 | 0.00010253 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_852-5_0_2_load_54 | 45 | 0.001822 | 0.00045664 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_852-5_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.00298 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_852-5_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.035928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_852-5_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.058397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_852-5_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.20788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_852-5_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_852-5_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.091799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_852-5_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.08568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_852-5_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.014698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_852-5_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.17607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_852-5_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.3687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_852-5_0_2_line_10 | NAYY 4x150 SE | 9 | 42 | 0.12287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_852-5_0_2_line_11 | NAYY 4x150 SE | 10 | 24 | 0.28831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_852-5_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.0084479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_852-5_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.2069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_852-5_0_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.1783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_852-5_0_2_line_15 | NAYY 4x150 SE | 12 | 15 | 0.21226 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_852-5_0_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.058874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_852-5_0_2_line_17 | NAYY 4x150 SE | 13 | 17 | 0.24633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_852-5_0_2_line_18 | NAYY 4x150 SE | 15 | 18 | 0.018452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_852-5_0_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.070085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_852-5_0_2_line_20 | NAYY 4x150 SE | 16 | 20 | 0.023992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_852-5_0_2_line_21 | NAYY 4x150 SE | 16 | 21 | 0.034657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_852-5_0_2_line_22 | NAYY 4x150 SE | 17 | 24 | 0.10007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_852-5_0_2_line_23 | NAYY 4x150 SE | 18 | 22 | 0.16615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_852-5_0_2_line_24 | NAYY 4x150 SE | 18 | 23 | 0.15466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_852-5_0_2_line_25 | NAYY 4x150 SE | 19 | 25 | 0.0258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_852-5_0_2_line_26 | NAYY 4x150 SE | 20 | 26 | 0.0083786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_852-5_0_2_line_27 | NAYY 4x150 SE | 21 | 27 | 0.0041545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_852-5_0_2_line_28 | NAYY 4x150 SE | 22 | 28 | 0.03501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_852-5_0_2_line_29 | NAYY 4x150 SE | 23 | 39 | 0.25618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_852-5_0_2_line_30 | NAYY 4x150 SE | 26 | 29 | 0.007337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_852-5_0_2_line_31 | NAYY 4x150 SE | 29 | 30 | 0.014711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_852-5_0_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.0067286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_852-5_0_2_line_33 | NAYY 4x150 SE | 31 | 32 | 0.014333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_852-5_0_2_line_34 | NAYY 4x150 SE | 32 | 33 | 0.015085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_852-5_0_2_line_35 | NAYY 4x150 SE | 33 | 34 | 0.020142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_852-5_0_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.026345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_852-5_0_2_line_37 | NAYY 4x150 SE | 36 | 37 | 0.12114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_852-5_0_2_line_38 | NAYY 4x150 SE | 37 | 38 | 0.11991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_852-5_0_2_line_39 | NAYY 4x150 SE | 38 | 40 | 0.014312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_852-5_0_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.13871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_852-5_0_2_line_41 | NAYY 4x150 SE | 40 | 41 | 0.027728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_852-5_0_2_line_42 | NAYY 4x150 SE | 41 | 45 | 0.0067752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_852-5_0_2_line_43 | NAYY 4x150 SE | 42 | 43 | 0.035497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_852-5_0_2_line_44 | NAYY 4x150 SE | 43 | 44 | 0.0063009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_852-5_0_2_trafo_16 | 0.25 MVA 20/0.4 kV | 46 | 17 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25
0 | 2591728.0121 | 1181656.7537 | 2591728.9931 | 1181653.9398
1 | 2591728.9931 | 1181653.9398 | 2591732.2637 | 1181644.5577 | 2591735.7165 | 1181634.4922 | 2591737.4776 | 1181619.2426
2 | 2591744.2969 | 1181561.3094 | 2591741.6709 | 1181578.4218 | 2591739.089 | 1181594.1779 | 2591737.6028 | 1181618.1589 | 2591737.4776 | 1181619.2426
3 | 2591590.4224 | 1181567.5285 | 2591596.2773 | 1181549.9334 | 2591613.4198 | 1181522.4617 | 2591625.6341 | 1181509.0821 | 2591636.9605 | 1181505.0307 | 2591651.5071 | 1181504.8213 | 2591668.216 | 1181510.8898 | 2591681.8718 | 1181517.9076 | 2591691.0636 | 1181527.2773 | 2591699.7878 | 1181540.8721 | 2591707.5643 | 1181548.365 | 2591723.5698 | 1181553.9678 | 2591738.8695 | 1181557.2371 | 2591744.2969 | 1181561.3094
4 | 2591744.2969 | 1181561.3094 | 2591747.6457 | 1181547.8756 | 2591748.7404 | 1181546.1538
5 | 2591590.4224 | 1181567.5285 | 2591586.4669 | 1181599.8951 | 2591585.794 | 1181620.7734 | 2591591.4653 | 1181640.6978 | 2591589.8388 | 1181651.4946 | 2591587.865 | 1181657.864
6 | 2591809.291 | 1181486.0252 | 2591804.7366 | 1181489.2776 | 2591799.8333 | 1181494.1647 | 2591778.1282 | 1181514.0493 | 2591754.168 | 1181537.6169 | 2591748.7404 | 1181546.1538
7 | 2591583.5146 | 1181671.9029 | 2591587.865 | 1181657.864
8 | 2591809.291 | 1181486.0252 | 2591810.9257 | 1181480.9204 | 2591809.7201 | 1181470.5056 | 2591818.489 | 1181450.1831 | 2591820.6953 | 1181438.6408 | 2591823.3653 | 1181431.1777 | 2591820.5792 | 1181415.3623 | 2591824.6426 | 1181388.2984 | 2591824.0021 | 1181355.7271 | 2591827.2399 | 1181333.5224 | 2591831.3774 | 1181321.3771 | 2591831.0698 | 1181314.2628
9 | 2591583.5146 | 1181671.9029 | 2591243.1048 | 1181813.5343
10 | 2591831.0698 | 1181314.2628 | 2591826.6137 | 1181311.3118 | 2591817.6788 | 1181316.7158 | 2591805.0289 | 1181324.9041 | 2591798.0832 | 1181332.9178 | 2591787.5848 | 1181345.1942 | 2591779.9337 | 1181356.5772 | 2591767.6618 | 1181383.9749 | 2591758.953 | 1181403.5415 | 2591758.9257 | 1181403.6428
11 | 2591244.1044 | 1181590.3517 | 2591235.1311 | 1181600.1255 | 2591225.5443 | 1181602.93 | 2591209.1603 | 1181604.9441 | 2591196.5773 | 1181610.9436 | 2591195.1923 | 1181619.3166 | 2591201.0019 | 1181628.6684 | 2591195.6224 | 1181641.6274 | 2591175.3973 | 1181663.9689 | 2591176.3492 | 1181672.5274 | 2591198.5291 | 1181691.3264 | 2591200.5415 | 1181694.1248 | 2591201.867 | 1181697.1689 | 2591203.4035 | 1181703.4698 | 2591205.2349 | 1181707.736 | 2591226.2431 | 1181739.9325 | 2591230.3155 | 1181746.7967 | 2591236.16 | 1181759.2056 | 2591238.507 | 1181766.239 | 2591240.8631 | 1181774.2841 | 2591242.7016 | 1181783.4861 | 2591243.9362 | 1181792.1666 | 2591244.5865 | 1181798.2243 | 2591244.6172 | 1181803.4825 | 2591243.1048 | 1181813.5343
12 | 2591187.4203 | 1181234.3864 | 2591180.8607 | 1181239.7099
13 | 2591004.8146 | 1181339.9585 | 2591042.4155 | 1181309.0415 | 2591074.1183 | 1181291.2735 | 2591094.3337 | 1181272.0111 | 2591118.6537 | 1181255.2105 | 2591132.0473 | 1181249.4654 | 2591149.5541 | 1181246.9824 | 2591180.8607 | 1181239.7099
14 | 2591187.4203 | 1181234.3864 | 2591244.0618 | 1181281.8381 | 2591252.558 | 1181284.8382 | 2591266.5048 | 1181286.6297 | 2591340.0881 | 1181295.7933 | 2591346.9656 | 1181299.0072
15 | 2591187.4203 | 1181234.3864 | 2591191.0972 | 1181226.6103 | 2591189.6984 | 1181194.8739 | 2591186.1177 | 1181128.5563 | 2591189.8111 | 1181023.147
16 | 2591004.8146 | 1181339.9585 | 2590965.7464 | 1181364.8639 | 2590962.145 | 1181366.8037 | 2590960.1454 | 1181367.5405 | 2590957.5575 | 1181368.1002 | 2590953.7769 | 1181367.7391
17 | 2591004.8146 | 1181339.9585 | 2591172.9611 | 1181519.9764
18 | 2591190.4573 | 1181004.7063 | 2591189.8111 | 1181023.147
19 | 2590953.7769 | 1181367.7391 | 2590955.6215 | 1181360.4882 | 2590956.8276 | 1181355.1614 | 2590957.5307 | 1181350.5246 | 2590957.958 | 1181345.2768 | 2590958.0632 | 1181339.1068 | 2590957.8201 | 1181334.9495 | 2590957.3169 | 1181330.4702 | 2590956.6152 | 1181325.9801 | 2590955.3847 | 1181320.2902 | 2590952.9322 | 1181309.4772 | 2590949.9629 | 1181298.9997
20 | 2590953.7769 | 1181367.7391 | 2590951.9683 | 1181373.5226 | 2590950.0136 | 1181378.7061 | 2590947.4036 | 1181384.7687 | 2590944.9265 | 1181390.0047
21 | 2590953.7769 | 1181367.7391 | 2590947.1053 | 1181364.4143 | 2590943.2451 | 1181361.8855 | 2590939.9492 | 1181358.8668 | 2590927.8309 | 1181345.397
22 | 2591244.1044 | 1181590.3517 | 2591172.9611 | 1181519.9764
23 | 2591172.7396 | 1180846.8652 | 2591164.4596 | 1180871.5569 | 2591162.7533 | 1180895.0826 | 2591168.3938 | 1180913.3947 | 2591184.29 | 1180936.5051 | 2591190.3096 | 1180953.0824 | 2591191.5027 | 1180974.8696 | 2591190.4573 | 1181004.7063
24 | 2591190.4573 | 1181004.7063 | 2591041.2308 | 1180964.0776
25 | 2590942.433 | 1181274.3257 | 2590943.4219 | 1181277.5087 | 2590947.7267 | 1181291.1091 | 2590949.9629 | 1181298.9997
26 | 2590941.4968 | 1181397.6467 | 2590942.867 | 1181394.3583 | 2590944.9265 | 1181390.0047
27 | 2590927.8309 | 1181345.397 | 2590925.0522 | 1181342.3085
28 | 2591172.7396 | 1180846.8652 | 2591162.6437 | 1180841.8999 | 2591158.5375 | 1180833.335 | 2591153.1175 | 1180820.144
29 | 2590826.8277 | 1180847.1559 | 2590838.4326 | 1180844.9035 | 2590844.8619 | 1180844.2266 | 2590850.5739 | 1180843.8954 | 2590857.0432 | 1180844.319 | 2590863.269 | 1180845.3767 | 2590868.6094 | 1180846.7803 | 2590874.387 | 1180849.3283 | 2590880.4402 | 1180852.3983 | 2590886.1971 | 1180856.436 | 2590891.5199 | 1180861.2748 | 2590901.1964 | 1180871.4874 | 2590915.1574 | 1180886.8517 | 2590930.4744 | 1180905.0043 | 2590940.0896 | 1180915.2059 | 2590948.4707 | 1180922.4302 | 2590956.9348 | 1180928.954 | 2590965.764 | 1180934.5879 | 2590975.2102 | 1180939.1425 | 2590984.204 | 1180942.5528 | 2590998.5526 | 1180946.8333 | 2591014.1455 | 1180950.7561 | 2591025.6523 | 1180954.4518 | 2591031.9873 | 1180957.088 | 2591037.0176 | 1180960.5711 | 2591041.2308 | 1180964.0776
30 | 2590941.4968 | 1181397.6467 | 2590939.8312 | 1181401.6444 | 2590938.9357 | 1181404.5141
31 | 2590936.0928 | 1181418.9257 | 2590936.7725 | 1181413.9221 | 2590937.4998 | 1181410.1301 | 2590938.3873 | 1181406.2712 | 2590938.9357 | 1181404.5141
32 | 2590936.0928 | 1181418.9257 | 2590932.6883 | 1181419.7424 | 2590929.8882 | 1181421.3475
33 | 2590921.8581 | 1181433.1354 | 2590925.6808 | 1181426.4788 | 2590927.5171 | 1181423.819 | 2590929.8882 | 1181421.3475 | 2590929.8882 | 1181421.3475
34 | 2590914.3458 | 1181446.2168 | 2590921.8581 | 1181433.1354
35 | 2590914.3458 | 1181446.2168 | 2590906.4352 | 1181459.992 | 2590904.8771 | 1181463.9537
36 | 2590826.884 | 1181000.2589 | 2590829.4526 | 1180999.0741 | 2590836.6584 | 1180996.8619 | 2590843.4301 | 1180995.3951 | 2590850.4322 | 1180994.873 | 2590852.4593 | 1180994.8001
37 | 2590716.0313 | 1181043.7953 | 2590737.4722 | 1181041.7608 | 2590747.6413 | 1181039.7551 | 2590758.3435 | 1181036.7591 | 2590766.7396 | 1181033.9668 | 2590777.1275 | 1181030.2377 | 2590786.2925 | 1181025.8657 | 2590794.6325 | 1181021.2726 | 2590802.9857 | 1181015.4234 | 2590813.9173 | 1181007.6914 | 2590822.1494 | 1181002.4427 | 2590826.884 | 1181000.2589
38 | 2590716.0313 | 1181043.7953 | 2590713.6254 | 1181024.0445 | 2590710.8956 | 1180997.424 | 2590707.3125 | 1180976.9858 | 2590702.884 | 1180962.8966 | 2590698.1776 | 1180951.8428 | 2590695.8077 | 1180945.3987 | 2590695.802 | 1180941.7636 | 2590696.4468 | 1180938.9945 | 2590699.1777 | 1180936.9892 | 2590705.7422 | 1180934.8889 | 2590707.5304 | 1180933.7937
39 | 2590716.3846 | 1180922.9217 | 2590713.9855 | 1180927.0721 | 2590712.0357 | 1180930.4213 | 2590709.3815 | 1180932.6599 | 2590707.5304 | 1180933.7937
40 | 2590826.8277 | 1180847.1559 | 2590825.4256 | 1180854.0838 | 2590823.8334 | 1180856.6654 | 2590821.2851 | 1180858.2368 | 2590814.9877 | 1180860.2587 | 2590809.7134 | 1180862.1567 | 2590803.4269 | 1180866.313 | 2590799.0642 | 1180869.9772 | 2590789.7785 | 1180880.4191 | 2590780.0493 | 1180890.4282 | 2590773.0181 | 1180896.9314 | 2590765.8943 | 1180902.8677 | 2590760.5154 | 1180906.1889 | 2590754.5105 | 1180909.5999 | 2590748.7333 | 1180912.1547 | 2590716.3846 | 1180922.9217
41 | 2590716.3846 | 1180922.9217 | 2590702.5028 | 1180909.6366 | 2590699.3759 | 1180907.5071 | 2590696.4342 | 1180906.5334 | 2590694.8065 | 1180906.6518
42 | 2590688.2346 | 1180908.1471 | 2590692.6848 | 1180906.8061 | 2590694.8065 | 1180906.6518
43 | 2591758.9257 | 1181403.6428 | 2591754.6986 | 1181419.3666 | 2591749.0081 | 1181429.3241 | 2591743.3008 | 1181434.5606
44 | 2591743.3008 | 1181434.5606 | 2591740.2833 | 1181437.3292 | 2591738.2544 | 1181438.1945

## bus_geodata
| x | y | coords
0 | 2591728.0121 | 1181656.7537
1 | 2591728.9931 | 1181653.9398
2 | 2591737.4776 | 1181619.2426
3 | 2591744.2969 | 1181561.3094
4 | 2591590.4224 | 1181567.5285
5 | 2591748.7404 | 1181546.1538
6 | 2591587.865 | 1181657.864
7 | 2591809.291 | 1181486.0252
8 | 2591583.5146 | 1181671.9029
9 | 2591831.0698 | 1181314.2628
10 | 2591243.1048 | 1181813.5343
11 | 2591180.8607 | 1181239.7099
12 | 2591187.4203 | 1181234.3864
13 | 2591004.8146 | 1181339.9585
14 | 2591346.9656 | 1181299.0072
15 | 2591189.8111 | 1181023.147
16 | 2590953.7769 | 1181367.7391
17 | 2591172.9611 | 1181519.9764
18 | 2591190.4573 | 1181004.7063
19 | 2590949.9629 | 1181298.9997
20 | 2590944.9265 | 1181390.0047
21 | 2590927.8309 | 1181345.397
22 | 2591172.7396 | 1180846.8652
23 | 2591041.2308 | 1180964.0776
24 | 2591244.1044 | 1181590.3517
25 | 2590942.433 | 1181274.3257
26 | 2590941.4968 | 1181397.6467
27 | 2590925.0522 | 1181342.3085
28 | 2591153.1175 | 1180820.144
29 | 2590938.9357 | 1181404.5141
30 | 2590936.0928 | 1181418.9257
31 | 2590929.8882 | 1181421.3475
32 | 2590921.8581 | 1181433.1354
33 | 2590914.3458 | 1181446.2168
34 | 2590904.8771 | 1181463.9537
35 | 2590852.4593 | 1180994.8001
36 | 2590826.884 | 1181000.2589
37 | 2590716.0313 | 1181043.7953
38 | 2590707.5304 | 1180933.7937
39 | 2590826.8277 | 1180847.1559
40 | 2590716.3846 | 1180922.9217
41 | 2590694.8065 | 1180906.6518
42 | 2591758.9257 | 1181403.6428
43 | 2591743.3008 | 1181434.5606
44 | 2591738.2544 | 1181438.1945
45 | 2590688.2346 | 1180908.1471
46 | 2591172.9611 | 1181519.9764

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1