## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_879-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_879-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_879-2_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_879-2_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_879-2_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_879-2_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_879-2_0_3_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_879-2_0_3_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_879-2_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_879-2_0_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_879-2_0_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_879-2_0_3_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_879-2_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_879-2_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_879-2_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_879-2_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_879-2_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_879-2_0_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_879-2_0_3_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_879-2_0_3_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_879-2_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_879-2_0_3_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_879-2_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_879-2_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_879-2_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_879-2_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_879-2_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_879-2_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_879-2_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_879-2_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_879-2_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_MV_122_1_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_879-2_0_3_load_0 | 0 | 0.00063616 | 0.00015944 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_879-2_0_3_load_1 | 1 | 0.00039451 | 9.8873e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_879-2_0_3_load_3 | 3 | 0.0003665 | 9.1853e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_879-2_0_3_load_4 | 4 | 0.0036077 | 0.00090418 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_879-2_0_3_load_5 | 5 | 0.0015848 | 0.00039718 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_879-2_0_3_load_21 | 7 | 0.00074899 | 0.00018771 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_879-2_0_3_load_17 | 8 | 0.00057118 | 0.00014315 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_879-2_0_3_load_20 | 10 | 0.00043989 | 0.00011025 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_879-2_0_3_load_6 | 11 | 0.017075 | 0.0042794 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_879-2_0_3_load_7 | 12 | 0.028591 | 0.0071656 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_879-2_0_3_load_8 | 13 | 0.03172 | 0.0079498 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_879-2_0_3_load_10 | 15 | 0.014031 | 0.0035165 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_879-2_0_3_load_22 | 17 | 0.034282 | 0.0085919 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_879-2_0_3_load_30 | 18 | 0.0038 | 0.00095237 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_879-2_0_3_load_23 | 19 | 0.0059124 | 0.0014818 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_879-2_0_3_load_29 | 20 | 0.0013189 | 0.00033055 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_879-2_0_3_load_12 | 21 | 0.003847 | 0.00096416 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_879-2_0_3_load_13 | 22 | 0.0028033 | 0.00070258 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_879-2_0_3_load_14 | 23 | 0.022455 | 0.0056276 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_879-2_0_3_load_16 | 25 | 0.0028881 | 0.00072383 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_879-2_0_3_load_25 | 26 | 0.0039639 | 0.00099345 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_879-2_0_3_load_24 | 27 | 0.052637 | 0.013192 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_879-2_0_3_load_27 | 29 | 0.00022292 | 5.5869e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_879-2_0_3_load_28 | 30 | 0.0019476 | 0.00048812 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_879-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_879-2_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_879-2_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.017433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_879-2_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.050979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_879-2_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0032793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_879-2_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.017603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_879-2_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.06896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_879-2_0_3_line_7 | NAYY 4x150 SE | 6 | 8 | 0.010637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_879-2_0_3_line_8 | NAYY 4x150 SE | 7 | 28 | 0.018067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_879-2_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.013102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_879-2_0_3_line_10 | NAYY 4x150 SE | 9 | 10 | 0.009836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_879-2_0_3_line_11 | NAYY 4x150 SE | 10 | 24 | 0.037931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_879-2_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.012535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_879-2_0_3_line_13 | NAYY 4x150 SE | 11 | 13 | 0.0082558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_879-2_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.051396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_879-2_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.011461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_879-2_0_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.11098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_879-2_0_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.0088604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_879-2_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.10517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_879-2_0_3_line_19 | NAYY 4x150 SE | 17 | 19 | 0.019988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_879-2_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.025858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_879-2_0_3_line_21 | NAYY 4x150 SE | 19 | 27 | 0.0077094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_879-2_0_3_line_22 | NAYY 4x150 SE | 20 | 30 | 0.0037018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_879-2_0_3_line_23 | NAYY 4x150 SE | 21 | 22 | 0.053811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_879-2_0_3_line_24 | NAYY 4x150 SE | 21 | 23 | 0.010634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_879-2_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.035216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_879-2_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.00036755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_879-2_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.00423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_879-2_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.018389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_879-2_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.017008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_879-2_0_3_trafo_23 | 0.25 MVA 20/0.4 kV | 31 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2603011.6451 | 1183975.1067 | 2603011.5311 | 1183966.1309 | 2603013.9592 | 1183964.4312 | 2603013.9592 | 1183964.4312
1 | 2603011.825 | 1183989.2652 | 2603011.6451 | 1183975.1067
2 | 2603013.9592 | 1183964.4312 | 2603031.3924 | 1183964.4675
3 | 2603011.825 | 1183989.2652 | 2602998.7571 | 1183989.5701 | 2602992.3698 | 1183986.4765 | 2602978.48 | 1183981.6561 | 2602962.3753 | 1183981.9642
4 | 2603011.825 | 1183989.2652 | 2603015.1031 | 1183989.1758
5 | 2603048.9949 | 1183964.5042 | 2603031.3924 | 1183964.4675
6 | 2603048.9949 | 1183964.5042 | 2603046.4985 | 1183903.9162 | 2603045.7778 | 1183895.6265
7 | 2603048.9949 | 1183964.5042 | 2603049.2016 | 1183975.1395
8 | 2603043.4735 | 1183877.7123 | 2603045.36 | 1183890.82 | 2603045.7778 | 1183895.6265
9 | 2603049.4563 | 1183988.2388 | 2603049.2016 | 1183975.1395
10 | 2603049.4563 | 1183988.2388 | 2603049.6437 | 1183998.073
11 | 2603047.7076 | 1184035.8736 | 2603049.2856 | 1184024.4796 | 2603049.9324 | 1184013.2297 | 2603049.6437 | 1183998.073
12 | 2602962.7164 | 1184191.4573 | 2602955.7415 | 1184201.8727
13 | 2602962.7164 | 1184191.4573 | 2602967.3102 | 1184184.5976
14 | 2602935.0889 | 1184247.3275 | 2602934.6251 | 1184243.6587 | 2602934.6575 | 1184239.8012 | 2602935.2088 | 1184236.1885 | 2602936.2869 | 1184232.1647 | 2602940.0683 | 1184225.3964 | 2602954.9323 | 1184203.0809 | 2602955.7415 | 1184201.8727
15 | 2602973.6874 | 1184175.075 | 2602967.3102 | 1184184.5976
16 | 2602825.4219 | 1184231.9015 | 2602835.6489 | 1184233.696 | 2602851.2031 | 1184236.4824 | 2602864.7194 | 1184238.9789 | 2602890.4165 | 1184243.7712 | 2602903.6432 | 1184245.3449 | 2602914.4962 | 1184246.8397 | 2602925.0823 | 1184247.6896 | 2602935.0889 | 1184247.3275
17 | 2602973.6874 | 1184175.075 | 2602978.6176 | 1184167.7129
18 | 2602825.4219 | 1184231.9015 | 2602829.7063 | 1184209.9255 | 2602830.9903 | 1184189.6934 | 2602830.9551 | 1184166.6593 | 2602831.1767 | 1184127.1821
19 | 2602989.7396 | 1184151.1049 | 2602978.6176 | 1184167.7129
20 | 2602831.1767 | 1184127.1821 | 2602831.3219 | 1184101.3241
21 | 2602994.0152 | 1184144.6897 | 2602992.0546 | 1184147.6482 | 2602989.7396 | 1184151.1049
22 | 2602831.3426 | 1184097.6224 | 2602831.3219 | 1184101.3241
23 | 2603038.9608 | 1184069.8899 | 2603036.0393 | 1184076.9556 | 2603032.0815 | 1184084.9911 | 2603027.7574 | 1184092.7708 | 2603023.1205 | 1184100.4502 | 2603018.3921 | 1184107.9073 | 2603012.588 | 1184116.665
24 | 2603006.7135 | 1184125.5292 | 2603012.588 | 1184116.665
25 | 2603047.7076 | 1184035.8736 | 2603046.3982 | 1184044.1772 | 2603044.6614 | 1184052.4361 | 2603042.2683 | 1184060.5947 | 2603039.463 | 1184068.6753 | 2603038.9608 | 1184069.8899
26 | 2603006.7135 | 1184125.5292 | 2603006.5104 | 1184125.8356
27 | 2603006.5104 | 1184125.8356 | 2603004.1737 | 1184129.3615
28 | 2602994.0152 | 1184144.6897 | 2603004.1737 | 1184129.3615
29 | 2603043.4735 | 1183877.7123 | 2603048.2623 | 1183872.0006 | 2603049.2952 | 1183867.1765 | 2603049.5488 | 1183862.5623

## bus_geodata
| x | y | coords
0 | 2603011.6451 | 1183975.1067
1 | 2603013.9592 | 1183964.4312
2 | 2603011.825 | 1183989.2652
3 | 2603031.3924 | 1183964.4675
4 | 2602962.3753 | 1183981.9642
5 | 2603015.1031 | 1183989.1758
6 | 2603048.9949 | 1183964.5042
7 | 2603045.7778 | 1183895.6265
8 | 2603049.2016 | 1183975.1395
9 | 2603049.4563 | 1183988.2388
10 | 2603049.6437 | 1183998.073
11 | 2602962.7164 | 1184191.4573
12 | 2602955.7415 | 1184201.8727
13 | 2602967.3102 | 1184184.5976
14 | 2602935.0889 | 1184247.3275
15 | 2602973.6874 | 1184175.075
16 | 2602825.4219 | 1184231.9015
17 | 2602978.6176 | 1184167.7129
18 | 2602831.1767 | 1184127.1821
19 | 2602989.7396 | 1184151.1049
20 | 2602831.3219 | 1184101.3241
21 | 2603012.588 | 1184116.665
22 | 2603038.9608 | 1184069.8899
23 | 2603006.7135 | 1184125.5292
24 | 2603047.7076 | 1184035.8736
25 | 2603006.5104 | 1184125.8356
26 | 2603004.1737 | 1184129.3615
27 | 2602994.0152 | 1184144.6897
28 | 2603043.4735 | 1183877.7123
29 | 2603049.5488 | 1183862.5623
30 | 2602831.3426 | 1184097.6224
31 | 2602935.0889 | 1184247.3275

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99468 | -0.037348 | 0.00063616 | 0.00015944
1 | 0.99478 | -0.036645 | 0.00039451 | 9.8873e-05
2 | 0.99458 | -0.03809 | 0 | 0
3 | 0.99494 | -0.035549 | 0.0003665 | 9.1853e-05
4 | 0.99431 | -0.039948 | 0.0036077 | 0.00090418
5 | 0.99457 | -0.038143 | 0.0015848 | 0.00039718
6 | 0.9951 | -0.034378 | 0 | 0
7 | 0.99501 | -0.035058 | 0.00074899 | 0.00018771
8 | 0.99522 | -0.033565 | 0.00057118 | 0.00014315
9 | 0.99537 | -0.032489 | 0 | 0
10 | 0.99549 | -0.031681 | 0.00043989 | 0.00011025
11 | 0.99484 | -0.036155 | 0.017075 | 0.0042794
12 | 0.9942 | -0.040669 | 0.028591 | 0.0071656
13 | 0.99546 | -0.031765 | 0.03172 | 0.0079498
14 | 0.99368 | -0.044352 | 0 | 0
15 | 0.99685 | -0.022027 | 0.014031 | 0.0035165
16 | 0.99255 | -0.052308 | 0 | 0
17 | 0.9981 | -0.013271 | 0.034282 | 0.0085919
18 | 0.99148 | -0.059854 | 0.0038 | 0.00095237
19 | 1 | 0 | -0.23148 | -0.057902
20 | 0.99136 | -0.060712 | 0.0013189 | 0.00033055
21 | 0.99726 | -0.019184 | 0.003847 | 0.00096416
22 | 0.99639 | -0.02535 | 0.0028033 | 0.00070258
23 | 0.99749 | -0.017555 | 0.022455 | 0.0056276
24 | 0.99595 | -0.028397 | 0 | 0
25 | 0.99751 | -0.017416 | 0.0028881 | 0.00072383
26 | 0.99776 | -0.015694 | 0.0039639 | 0.00099345
27 | 0.99893 | -0.0074874 | 0.052637 | 0.013192
28 | 0.995 | -0.035099 | 0 | 0
29 | 0.995 | -0.035138 | 0.00022292 | 5.5869e-05
30 | 0.99135 | -0.060786 | 0.0019476 | 0.00048812
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0058301 | -0.0014605 | 0.0058307 | 0.0014605 | 5.6673e-07 | 6.2971e-08 | 0.0087215 | 0.0087214 | 0.0087215 | 0.99468 | -0.037348 | 0.99478 | -0.036645 | 3.2302
1 | 0.005194 | 0.001301 | -0.0051934 | -0.001301 | 5.3341e-07 | 2.1382e-08 | 0.0077698 | 0.0077699 | 0.0077699 | 0.99468 | -0.037348 | 0.99458 | -0.03809 | 2.8777
2 | -0.0062252 | -0.0015594 | 0.0062261 | 0.0015595 | 9.4319e-07 | 1.364e-07 | 0.0093115 | 0.0093114 | 0.0093115 | 0.99478 | -0.036645 | 0.99494 | -0.035549 | 3.4487
3 | 0.0036087 | 0.00090388 | -0.0036077 | -0.00090418 | 9.2724e-07 | -3.0477e-07 | 0.0053988 | 0.0053991 | 0.0053991 | 0.99458 | -0.03809 | 0.99431 | -0.039948 | 1.9997
4 | 0.0015848 | 0.00039714 | -0.0015848 | -0.00039718 | 1.1504e-08 | -3.8132e-08 | 0.002371 | 0.002371 | 0.002371 | 0.99458 | -0.03809 | 0.99457 | -0.038143 | 0.87816
5 | -0.0065926 | -0.0016514 | 0.0065937 | 0.0016516 | 1.0678e-06 | 1.8204e-07 | 0.0098596 | 0.0098595 | 0.0098596 | 0.99494 | -0.035549 | 0.9951 | -0.034378 | 3.6517
6 | 0.000972 | 0.00024227 | -0.00097191 | -0.00024313 | 9.0867e-08 | -8.6084e-07 | 0.001453 | 0.0014533 | 0.0014533 | 0.9951 | -0.034378 | 0.99501 | -0.035058 | 0.53826
7 | -0.0075657 | -0.0018939 | 0.0075666 | 0.001894 | 8.4944e-07 | 1.885e-07 | 0.011312 | 0.011312 | 0.011312 | 0.9951 | -0.034378 | 0.99522 | -0.033565 | 4.1898
8 | 0.00022292 | 5.5415e-05 | -0.00022292 | -5.5649e-05 | 1.2521e-09 | -2.3419e-07 | 0.00033322 | 0.0003333 | 0.0003333 | 0.99501 | -0.035058 | 0.995 | -0.035099 | 0.12344
9 | -0.0081377 | -0.0020372 | 0.008139 | 0.0020375 | 1.2102e-06 | 2.9517e-07 | 0.012166 | 0.012166 | 0.012166 | 0.99522 | -0.033565 | 0.99537 | -0.032489 | 4.5061
10 | -0.008139 | -0.0020375 | 0.0081399 | 0.0020377 | 9.085e-07 | 2.2156e-07 | 0.012166 | 0.012166 | 0.012166 | 0.99537 | -0.032489 | 0.99549 | -0.031681 | 4.5061
11 | -0.0085798 | -0.002148 | 0.0085836 | 0.002149 | 3.8923e-06 | 1.0037e-06 | 0.012824 | 0.012824 | 0.012824 | 0.99549 | -0.031681 | 0.99595 | -0.028397 | 4.7496
12 | 0.035699 | 0.0089486 | -0.035677 | -0.0089402 | 2.2302e-05 | 8.4152e-06 | 0.053397 | 0.053397 | 0.053397 | 0.99484 | -0.036155 | 0.9942 | -0.040669 | 19.7767
13 | -0.052774 | -0.013228 | 0.052806 | 0.01324 | 3.21e-05 | 1.2239e-05 | 0.078937 | 0.078937 | 0.078937 | 0.99484 | -0.036155 | 0.99546 | -0.031765 | 29.2358
14 | 0.0070857 | 0.0017746 | -0.0070821 | -0.0017739 | 3.6068e-06 | 7.2111e-07 | 0.010605 | 0.010605 | 0.010605 | 0.9942 | -0.040669 | 0.99368 | -0.044352 | 3.9278
15 | -0.084526 | -0.02119 | 0.08464 | 0.021234 | 0.00011417 | 4.3763e-05 | 0.12635 | 0.12635 | 0.12635 | 0.99546 | -0.031765 | 0.99685 | -0.022027 | 46.7969
16 | 0.0070821 | 0.0017739 | -0.0070743 | -0.0017723 | 7.7887e-06 | 1.5597e-06 | 0.010605 | 0.010606 | 0.010606 | 0.99368 | -0.044352 | 0.99255 | -0.052308 | 3.928
17 | -0.098671 | -0.02475 | 0.098791 | 0.024796 | 0.00011996 | 4.6021e-05 | 0.1473 | 0.1473 | 0.1473 | 0.99685 | -0.022027 | 0.9981 | -0.013271 | 54.5541
18 | 0.0070743 | 0.0017723 | -0.007067 | -0.0017708 | 7.3821e-06 | 1.4814e-06 | 0.010606 | 0.010606 | 0.010606 | 0.99255 | -0.052308 | 0.99148 | -0.059854 | 3.9281
19 | -0.13307 | -0.033388 | 0.13332 | 0.033482 | 0.00024549 | 9.3895e-05 | 0.19841 | 0.1984 | 0.19841 | 0.9981 | -0.013271 | 1 | 0 | 36.7417
20 | 0.0032669 | 0.00081844 | -0.0032666 | -0.00081863 | 3.8789e-07 | -1.8426e-07 | 0.0049029 | 0.004903 | 0.004903 | 0.99148 | -0.059854 | 0.99136 | -0.060712 | 1.8159
21 | 0.097356 | 0.02442 | -0.097255 | -0.024381 | 0.00010097 | 3.8734e-05 | 0.14487 | 0.14487 | 0.14487 | 1 | 0 | 0.99893 | -0.0074874 | 53.6574
22 | 0.0019476 | 0.00048808 | -0.0019476 | -0.00048812 | 1.9741e-08 | -4.0136e-08 | 0.0029234 | 0.0029234 | 0.0029234 | 0.99136 | -0.060712 | 0.99135 | -0.060786 | 1.0827
23 | 0.0114 | 0.0028555 | -0.011391 | -0.0028525 | 9.7154e-06 | 3.0352e-06 | 0.01701 | 0.01701 | 0.01701 | 0.99726 | -0.019184 | 0.99639 | -0.02535 | 6.3
24 | -0.015247 | -0.0038197 | 0.015251 | 0.0038209 | 3.4344e-06 | 1.1821e-06 | 0.02275 | 0.02275 | 0.02275 | 0.99726 | -0.019184 | 0.99749 | -0.017555 | 8.4259
25 | 0.0085873 | 0.0021499 | -0.0085836 | -0.002149 | 3.6137e-06 | 9.3139e-07 | 0.012824 | 0.012824 | 0.012824 | 0.99639 | -0.02535 | 0.99595 | -0.028397 | 4.7495
26 | -0.037705 | -0.0094485 | 0.037706 | 0.0094488 | 7.2559e-07 | 2.7428e-07 | 0.056247 | 0.056247 | 0.056247 | 0.99749 | -0.017555 | 0.99751 | -0.017416 | 20.8321
27 | -0.040594 | -0.010173 | 0.040604 | 0.010176 | 9.6788e-06 | 3.6674e-06 | 0.060555 | 0.060555 | 0.060555 | 0.99751 | -0.017416 | 0.99776 | -0.015694 | 22.4278
28 | -0.044568 | -0.01117 | 0.044618 | 0.011189 | 5.0693e-05 | 1.9257e-05 | 0.066467 | 0.066466 | 0.066467 | 0.99776 | -0.015694 | 0.99893 | -0.0074874 | 24.6172
29 | 0.00022292 | 5.5649e-05 | -0.00022292 | -5.5869e-05 | 1.1793e-09 | -2.2046e-07 | 0.0003333 | 0.00033338 | 0.00033338 | 0.995 | -0.035099 | 0.995 | -0.035138 | 0.12347

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23739 | 0.059384

## res_load
| p_mw | q_mvar
0 | 0.00063616 | 0.00015944
1 | 0.00039451 | 9.8873e-05
2 | 0.0003665 | 9.1853e-05
3 | 0.0036077 | 0.00090418
4 | 0.0015848 | 0.00039718
5 | 0.00074899 | 0.00018771
6 | 0.00057118 | 0.00014315
7 | 0.00043989 | 0.00011025
8 | 0.017075 | 0.0042794
9 | 0.028591 | 0.0071656
10 | 0.03172 | 0.0079498
11 | 0.014031 | 0.0035165
12 | 0.034282 | 0.0085919
13 | 0.0038 | 0.00095237
14 | 0.0059124 | 0.0014818
15 | 0.0013189 | 0.00033055
16 | 0.003847 | 0.00096416
17 | 0.0028033 | 0.00070258
18 | 0.022455 | 0.0056276
19 | 0.0028881 | 0.00072383
20 | 0.0039639 | 0.00099345
21 | 0.052637 | 0.013192
22 | 0.00022292 | 5.5869e-05
23 | 0.0019476 | 0.00048812

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1