## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_879-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_879-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_879-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_879-3_0_5_node_60 | 0.4 | n |  | TRUE
4 | bus_LV_879-3_0_5_node_39 | 0.4 | n |  | TRUE
5 | bus_LV_879-3_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_879-3_0_5_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_879-3_0_5_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_879-3_0_5_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_879-3_0_5_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_879-3_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_879-3_0_5_node_68 | 0.4 | n |  | TRUE
12 | bus_LV_879-3_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_879-3_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_879-3_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_879-3_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_879-3_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_879-3_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_879-3_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_879-3_0_5_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_879-3_0_5_node_41 | 0.4 | n |  | TRUE
21 | bus_LV_879-3_0_5_node_57 | 0.4 | n |  | TRUE
22 | bus_LV_879-3_0_5_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_879-3_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_879-3_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_879-3_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_879-3_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_879-3_0_5_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_879-3_0_5_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_879-3_0_5_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_879-3_0_5_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_879-3_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_879-3_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_879-3_0_5_node_66 | 0.4 | n |  | TRUE
34 | bus_LV_879-3_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_879-3_0_5_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_879-3_0_5_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_879-3_0_5_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_879-3_0_5_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_879-3_0_5_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_879-3_0_5_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_879-3_0_5_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_879-3_0_5_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_879-3_0_5_node_76 | 0.4 | n |  | TRUE
44 | bus_LV_879-3_0_5_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_879-3_0_5_node_71 | 0.4 | n |  | TRUE
46 | bus_LV_879-3_0_5_node_70 | 0.4 | n |  | TRUE
47 | bus_LV_879-3_0_5_node_77 | 0.4 | n |  | TRUE
48 | bus_LV_879-3_0_5_node_75 | 0.4 | n |  | TRUE
49 | bus_LV_879-3_0_5_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_879-3_0_5_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_879-3_0_5_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_879-3_0_5_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_879-3_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_879-3_0_5_node_73 | 0.4 | n |  | TRUE
55 | bus_LV_879-3_0_5_node_72 | 0.4 | n |  | TRUE
56 | bus_LV_879-3_0_5_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_879-3_0_5_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_879-3_0_5_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_879-3_0_5_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_879-3_0_5_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_879-3_0_5_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_879-3_0_5_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_879-3_0_5_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_879-3_0_5_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_879-3_0_5_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_879-3_0_5_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_879-3_0_5_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_879-3_0_5_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_879-3_0_5_node_78 | 0.4 | n |  | TRUE
70 | bus_LV_879-3_0_5_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_879-3_0_5_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_879-3_0_5_node_82 | 0.4 | n |  | TRUE
73 | bus_LV_879-3_0_5_node_80 | 0.4 | n |  | TRUE
74 | bus_LV_879-3_0_5_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_879-3_0_5_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_879-3_0_5_node_81 | 0.4 | n |  | TRUE
77 | bus_MV_122_1_node_226 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_879-3_0_5_load_0 | 0 | 0.0021486 | 0.00053848 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_879-3_0_5_load_60 | 3 | 0.00066632 | 0.000167 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_879-3_0_5_load_39 | 4 | 0.0019826 | 0.00049688 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_879-3_0_5_load_3 | 5 | 0.00057799 | 0.00014486 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_879-3_0_5_load_43 | 6 | 0.0006395 | 0.00016027 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_879-3_0_5_load_44 | 7 | 0.00022069 | 5.5309e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_879-3_0_5_load_46 | 8 | 0.0013739 | 0.00034433 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_879-3_0_5_load_4 | 9 | 0.0014749 | 0.00036964 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_879-3_0_5_load_68 | 11 | 0.00016855 | 4.2242e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_879-3_0_5_load_9 | 13 | 0.00012694 | 3.1814e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_879-3_0_5_load_10 | 14 | 0.0021384 | 0.00053594 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_879-3_0_5_load_12 | 15 | 0.00013728 | 3.4406e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_879-3_0_5_load_14 | 19 | 0.00054366 | 0.00013625 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_879-3_0_5_load_57 | 21 | 0.0048053 | 0.0012043 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_879-3_0_5_load_16 | 23 | 0.00058925 | 0.00014768 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_879-3_0_5_load_19 | 26 | 0.00060849 | 0.0001525 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_879-3_0_5_load_21 | 28 | 0.00056018 | 0.0001404 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_879-3_0_5_load_37 | 30 | 0.00036641 | 9.183e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_879-3_0_5_load_25 | 31 | 0.0042369 | 0.0010619 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_879-3_0_5_load_23 | 32 | 0.00029967 | 7.5105e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_879-3_0_5_load_66 | 33 | 0.0064798 | 0.001624 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_879-3_0_5_load_24 | 34 | 0.000373 | 9.3483e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_879-3_0_5_load_26 | 36 | 0.0022874 | 0.00057327 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_879-3_0_5_load_67 | 40 | 0.011487 | 0.0028789 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_879-3_0_5_load_69 | 41 | 0.00058097 | 0.0001456 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_879-3_0_5_load_83 | 42 | 0.05431 | 0.013611 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_879-3_0_5_load_74 | 44 | 0.036684 | 0.0091939 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_879-3_0_5_load_71 | 45 | 0.0062904 | 0.0015765 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_879-3_0_5_load_77 | 47 | 0.0093605 | 0.002346 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_879-3_0_5_load_75 | 48 | 0.0092857 | 0.0023272 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_879-3_0_5_load_31 | 49 | 0.0011595 | 0.00029059 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_879-3_0_5_load_35 | 51 | 0.0010945 | 0.00027432 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_879-3_0_5_load_36 | 52 | 0.0011751 | 0.00029452 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_879-3_0_5_load_73 | 54 | 0.0019311 | 0.00048398 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_879-3_0_5_load_72 | 55 | 0.0019315 | 0.00048408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_879-3_0_5_load_62 | 57 | 0.0008261 | 0.00020704 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_879-3_0_5_load_61 | 58 | 0.00079227 | 0.00019856 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_879-3_0_5_load_58 | 59 | 0.00083459 | 0.00020917 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_879-3_0_5_load_59 | 60 | 0.00097024 | 0.00024316 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_879-3_0_5_load_47 | 61 | 0.000863 | 0.00021629 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_879-3_0_5_load_48 | 62 | 0.00048051 | 0.00012043 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_879-3_0_5_load_50 | 64 | 0.00072353 | 0.00018133 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_879-3_0_5_load_56 | 67 | 0.00054607 | 0.00013686 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_879-3_0_5_load_63 | 68 | 0.00054519 | 0.00013664 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_879-3_0_5_load_78 | 69 | 0.0011056 | 0.00027708 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_879-3_0_5_load_55 | 71 | 0.00074664 | 0.00018713 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_879-3_0_5_load_82 | 72 | 0.00044799 | 0.00011228 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_879-3_0_5_load_54 | 74 | 0.00051176 | 0.00012826 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_879-3_0_5_load_64 | 75 | 0.0018532 | 0.00046446 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_879-3_0_5_load_81 | 76 | 0.0011545 | 0.00028935 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_879-3_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.1197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_879-3_0_5_line_1 | NAYY 4x150 SE | 1 | 2 | 0.2284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_879-3_0_5_line_2 | NAYY 4x150 SE | 2 | 5 | 0.074157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_879-3_0_5_line_3 | NAYY 4x150 SE | 2 | 6 | 0.29575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_879-3_0_5_line_4 | NAYY 4x150 SE | 3 | 4 | 0.0027962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_879-3_0_5_line_5 | NAYY 4x150 SE | 4 | 22 | 0.087037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_879-3_0_5_line_6 | NAYY 4x150 SE | 6 | 7 | 0.12386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_879-3_0_5_line_7 | NAYY 4x150 SE | 7 | 8 | 0.01698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_879-3_0_5_line_8 | NAYY 4x150 SE | 8 | 18 | 0.3661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_879-3_0_5_line_9 | NAYY 4x150 SE | 9 | 10 | 0.02101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_879-3_0_5_line_10 | NAYY 4x150 SE | 9 | 11 | 0.42507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_879-3_0_5_line_11 | NAYY 4x150 SE | 10 | 12 | 0.44251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_879-3_0_5_line_12 | NAYY 4x150 SE | 11 | 16 | 0.26335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_879-3_0_5_line_13 | NAYY 4x150 SE | 12 | 20 | 0.029143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_879-3_0_5_line_14 | NAYY 4x150 SE | 13 | 14 | 0.003694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_879-3_0_5_line_15 | NAYY 4x150 SE | 14 | 15 | 0.014422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_879-3_0_5_line_16 | NAYY 4x150 SE | 15 | 18 | 0.023816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_879-3_0_5_line_17 | NAYY 4x150 SE | 16 | 17 | 0.026293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_879-3_0_5_line_18 | NAYY 4x150 SE | 17 | 19 | 0.031417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_879-3_0_5_line_19 | NAYY 4x150 SE | 18 | 19 | 0.027922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_879-3_0_5_line_20 | NAYY 4x150 SE | 20 | 21 | 0.11245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_879-3_0_5_line_21 | NAYY 4x150 SE | 20 | 22 | 0.056467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_879-3_0_5_line_22 | NAYY 4x150 SE | 21 | 59 | 0.021576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_879-3_0_5_line_23 | NAYY 4x150 SE | 22 | 56 | 0.018581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_879-3_0_5_line_24 | NAYY 4x150 SE | 22 | 30 | 0.26536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_879-3_0_5_line_25 | NAYY 4x150 SE | 23 | 24 | 0.004646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_879-3_0_5_line_26 | NAYY 4x150 SE | 23 | 25 | 0.0050286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_879-3_0_5_line_27 | NAYY 4x150 SE | 24 | 26 | 0.01731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_879-3_0_5_line_28 | NAYY 4x150 SE | 24 | 27 | 0.027203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_879-3_0_5_line_29 | NAYY 4x150 SE | 25 | 28 | 0.01864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_879-3_0_5_line_30 | NAYY 4x150 SE | 25 | 29 | 0.011814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_879-3_0_5_line_31 | NAYY 4x150 SE | 27 | 30 | 0.0271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_879-3_0_5_line_32 | NAYY 4x150 SE | 29 | 31 | 0.11056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_879-3_0_5_line_33 | NAYY 4x150 SE | 29 | 32 | 0.020126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_879-3_0_5_line_34 | NAYY 4x150 SE | 31 | 33 | 0.0093947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_879-3_0_5_line_35 | NAYY 4x150 SE | 32 | 34 | 0.0045122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_879-3_0_5_line_36 | NAYY 4x150 SE | 33 | 35 | 0.027532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
37 | LV_879-3_0_5_line_37 | NAYY 4x150 SE | 35 | 40 | 0.031342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_879-3_0_5_line_38 | NAYY 4x150 SE | 35 | 37 | 0.02228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_879-3_0_5_line_39 | NAYY 4x150 SE | 36 | 37 | 0.03576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_879-3_0_5_line_40 | NAYY 4x150 SE | 37 | 38 | 0.008184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_879-3_0_5_line_41 | NAYY 4x150 SE | 37 | 39 | 0.038502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_879-3_0_5_line_42 | NAYY 4x150 SE | 38 | 41 | 0.0021781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_879-3_0_5_line_43 | NAYY 4x150 SE | 39 | 42 | 0.012246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_879-3_0_5_line_44 | NAYY 4x150 SE | 39 | 43 | 0.002651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_879-3_0_5_line_45 | NAYY 4x150 SE | 40 | 44 | 0.0064293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_879-3_0_5_line_46 | NAYY 4x150 SE | 41 | 46 | 0.028571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_879-3_0_5_line_47 | NAYY 4x150 SE | 43 | 47 | 0.006382 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_879-3_0_5_line_48 | NAYY 4x150 SE | 43 | 48 | 0.013825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_879-3_0_5_line_49 | NAYY 4x150 SE | 45 | 46 | 0.021603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_879-3_0_5_line_50 | NAYY 4x150 SE | 46 | 52 | 0.016031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_879-3_0_5_line_51 | NAYY 4x150 SE | 49 | 50 | 0.0029504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_879-3_0_5_line_52 | NAYY 4x150 SE | 50 | 51 | 0.041888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_879-3_0_5_line_53 | NAYY 4x150 SE | 50 | 52 | 0.016587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_879-3_0_5_line_54 | NAYY 4x150 SE | 51 | 54 | 0.019551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_879-3_0_5_line_55 | NAYY 4x150 SE | 53 | 54 | 0.09584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_879-3_0_5_line_56 | NAYY 4x150 SE | 53 | 55 | 0.067019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_879-3_0_5_line_57 | NAYY 4x150 SE | 56 | 57 | 0.14639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_879-3_0_5_line_58 | NAYY 4x150 SE | 57 | 58 | 0.044837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_879-3_0_5_line_59 | NAYY 4x150 SE | 58 | 65 | 0.0082124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_879-3_0_5_line_60 | NAYY 4x150 SE | 59 | 60 | 0.021818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_879-3_0_5_line_61 | NAYY 4x150 SE | 61 | 62 | 0.0032038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_879-3_0_5_line_62 | NAYY 4x150 SE | 61 | 63 | 0.015686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_879-3_0_5_line_63 | NAYY 4x150 SE | 62 | 64 | 0.01684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_879-3_0_5_line_64 | NAYY 4x150 SE | 63 | 65 | 0.27281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_879-3_0_5_line_65 | NAYY 4x150 SE | 63 | 66 | 0.11656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_879-3_0_5_line_66 | NAYY 4x150 SE | 64 | 67 | 0.0050006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_879-3_0_5_line_67 | NAYY 4x150 SE | 65 | 68 | 0.031649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_879-3_0_5_line_68 | NAYY 4x150 SE | 66 | 69 | 0.049922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_879-3_0_5_line_69 | NAYY 4x150 SE | 66 | 70 | 0.15968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_879-3_0_5_line_70 | NAYY 4x150 SE | 67 | 71 | 0.013632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_879-3_0_5_line_71 | NAYY 4x150 SE | 70 | 72 | 0.0687 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_879-3_0_5_line_72 | NAYY 4x150 SE | 70 | 73 | 0.27567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_879-3_0_5_line_73 | NAYY 4x150 SE | 71 | 74 | 0.0057379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_879-3_0_5_line_74 | NAYY 4x150 SE | 73 | 76 | 0.0542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_879-3_0_5_line_75 | NAYY 4x150 SE | 73 | 75 | 0.19271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_879-3_0_5_trafo_22 | 0.25 MVA 20/0.4 kV | 77 | 29 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55
0 | 2602074.4962 | 1183560.3467 | 2602069.5692 | 1183547.6941 | 2602044.0898 | 1183444.6804
1 | 2602074.4962 | 1183560.3467 | 2602088.0722 | 1183504.8338 | 2602123.1291 | 1183361.5054 | 2602132.0759 | 1183339.5639
2 | 2602132.0759 | 1183339.5639 | 2602125.151 | 1183320.3405 | 2602109.1011 | 1183307.9731 | 2602077.0038 | 1183298.513
3 | 2602132.0759 | 1183339.5639 | 2602423.3077 | 1183288.0862
4 | 2602774.2638 | 1183563.7678 | 2602771.8981 | 1183562.2771
5 | 2602860.538 | 1183564.4966 | 2602839.3913 | 1183568.1776 | 2602832.7192 | 1183569.0527 | 2602824.635 | 1183569.4937 | 2602816.4291 | 1183569.2565 | 2602804.3304 | 1183568.2171 | 2602792.064 | 1183566.4884 | 2602774.2638 | 1183563.7678
6 | 2602423.3077 | 1183288.0862 | 2602423.504 | 1183285.5991 | 2602433.1444 | 1183249.9957 | 2602444.215 | 1183188.8798 | 2602449.1544 | 1183169.2161 | 2602449.9327 | 1183167.2758
7 | 2602452.6463 | 1183151.1676 | 2602453.854 | 1183157.5008 | 2602449.9327 | 1183167.2758
8 | 2602597.8169 | 1182815.084 | 2602452.6463 | 1183151.1676
9 | 2602940.9177 | 1183122.1184 | 2602954.3562 | 1183105.9684
10 | 2602954.3562 | 1183105.9684 | 2602869.4696 | 1182689.4571
11 | 2602817.6911 | 1183497.3756 | 2602814.0611 | 1183489.3587 | 2602810.8282 | 1183481.2531 | 2602808.0915 | 1183472.8586 | 2602805.7595 | 1183464.3866 | 2602804.023 | 1183455.5479 | 2602802.8286 | 1183446.665 | 2602802.1608 | 1183437.8602 | 2602802.0732 | 1183429.089 | 2602802.4818 | 1183420.2513 | 2602803.4859 | 1183411.5139 | 2602804.9326 | 1183402.799 | 2602806.8526 | 1183394.151 | 2602809.07 | 1183386.259 | 2602811.7301 | 1183378.5452 | 2602814.4891 | 1183371.6207 | 2602817.8664 | 1183364.8521 | 2602820.6478 | 1183358.8614 | 2602824.1698 | 1183352.871 | 2602828.7228 | 1183345.8584 | 2602833.894 | 1183339.1129 | 2602839.5461 | 1183332.5232 | 2602845.4271 | 1183326.1449 | 2602851.5753 | 1183319.889 | 2602858.0745 | 1183313.8889 | 2602864.627 | 1183308.278 | 2602871.3397 | 1183302.7671 | 2602878.2891 | 1183297.4343 | 2602885.4979 | 1183292.2684 | 2602911.5611 | 1183274.0269 | 2602916.3721 | 1183270.5607 | 2602921.0992 | 1183267.0278 | 2602925.7424 | 1183263.3615 | 2602930.2788 | 1183259.595 | 2602934.6244 | 1183255.5061 | 2602938.7794 | 1183251.2504 | 2602942.7206 | 1183246.7499 | 2602946.3185 | 1183242.0493 | 2602949.5959 | 1183237.0371 | 2602952.5604 | 1183231.8248 | 2602955.0288 | 1183226.3565 | 2602957.0392 | 1183220.7323 | 2602958.5383 | 1183214.9079 | 2602959.5259 | 1183209.0053 | 2602959.903 | 1183202.9135 | 2602959.9211 | 1183196.8548 | 2602959.5347 | 1183190.896 | 2602958.8047 | 1183184.9259 | 2602957.838 | 1183179.1114 | 2602956.5811 | 1183173.3411 | 2602955.0647 | 1183167.6375 | 2602953.4261 | 1183161.9671 | 2602947.9072 | 1183144.9112 | 2602944.1873 | 1183133.5258 | 2602942.5028 | 1183127.8332 | 2602940.9177 | 1183122.1184
12 | 2602611.5135 | 1182742.5081 | 2602869.4696 | 1182689.4571
13 | 2602817.6911 | 1183497.3756 | 2602824.5937 | 1183510.0965 | 2602832.588 | 1183522.4176
14 | 2602630.0788 | 1182807.845 | 2602626.4568 | 1182808.5706
15 | 2602615.9329 | 1182818.4043 | 2602617.8796 | 1182816.9602 | 2602626.4568 | 1182808.5706 | 2602626.4568 | 1182808.5706
16 | 2602597.8169 | 1182815.084 | 2602598.5631 | 1182819.8979 | 2602610.5558 | 1182822.3932 | 2602615.9329 | 1182818.4043
17 | 2602590.2758 | 1182756.3174 | 2602601.9159 | 1182744.6941 | 2602611.5135 | 1182742.5081
18 | 2602590.2758 | 1182756.3174 | 2602593.7493 | 1182775.173 | 2602594.4437 | 1182787.397
19 | 2602597.8169 | 1182815.084 | 2602594.9845 | 1182796.918 | 2602594.4437 | 1182787.397
20 | 2602832.588 | 1183522.4176 | 2602834.0126 | 1183512.2241 | 2602835.2048 | 1183492.6813 | 2602837.7759 | 1183462.7226 | 2602839.1086 | 1183453.2406 | 2602840.6463 | 1183446.0376 | 2602842.3897 | 1183439.7685 | 2602844.1316 | 1183436.601 | 2602847.408 | 1183433.4454 | 2602856.4707 | 1183430.2257 | 2602861.3343 | 1183428.2936 | 2602866.2521 | 1183424.7719
21 | 2602832.588 | 1183522.4176 | 2602838.1265 | 1183529.9907 | 2602844.1078 | 1183537.4417 | 2602852.5918 | 1183547.2952 | 2602865.2112 | 1183561.375 | 2602860.538 | 1183564.4966
22 | 2602866.2521 | 1183424.7719 | 2602866.2521 | 1183424.7719 | 2602872.194 | 1183418.6048 | 2602874.6532 | 1183416.1047 | 2602877.0586 | 1183414.4272 | 2602880.4864 | 1183413.9174 | 2602883.4557 | 1183414.4302 | 2602883.5336 | 1183414.483
23 | 2602860.538 | 1183564.4966 | 2602865.2112 | 1183561.375 | 2602874.0311 | 1183570.8728
24 | 2602860.538 | 1183564.4966 | 2602858.0306 | 1183572.1994 | 2602853.7137 | 1183580.7018 | 2602848.3741 | 1183588.7701 | 2602828.1089 | 1183618.0425 | 2602818.3998 | 1183633.168 | 2602809.4693 | 1183648.2494 | 2602793.8077 | 1183677.0126 | 2602779.1459 | 1183706.2099 | 2602772.0628 | 1183721.6257 | 2602765.4223 | 1183737.4642 | 2602753.4696 | 1183769.0529 | 2602744.5747 | 1183790.8935 | 2602741.0022 | 1183800.2616
25 | 2602752.262 | 1183840.6669 | 2602756.6418 | 1183842.2171
26 | 2602761.3822 | 1183843.8949 | 2602756.6418 | 1183842.2171
27 | 2602752.262 | 1183840.6669 | 2602749.9567 | 1183857.8192
28 | 2602731.3461 | 1183825.5832 | 2602733.4962 | 1183831.1537 | 2602740.7606 | 1183836.6042 | 2602752.262 | 1183840.6669
29 | 2602761.3822 | 1183843.8949 | 2602759.6848 | 1183850.3753 | 2602758.1452 | 1183862.214
30 | 2602772.5478 | 1183847.8464 | 2602761.3822 | 1183843.8949
31 | 2602731.3461 | 1183825.5832 | 2602741.0022 | 1183800.2616
32 | 2602772.5478 | 1183847.8464 | 2602785.6431 | 1183871.9314 | 2602806.0925 | 1183921.7441 | 2602810.2563 | 1183950.7419
33 | 2602772.5478 | 1183847.8464 | 2602780.0261 | 1183829.1613
34 | 2602810.2563 | 1183950.7419 | 2602811.5916 | 1183960.0412
35 | 2602781.7028 | 1183824.9721 | 2602780.0261 | 1183829.1613
36 | 2602815.5046 | 1183987.2932 | 2602811.5916 | 1183960.0412
37 | 2602815.5046 | 1183987.2932 | 2602810.032 | 1183986.6682 | 2602784.4063 | 1183983.3986
38 | 2602826.9303 | 1184005.9081 | 2602821.0406 | 1183999.5688 | 2602815.984 | 1183990.6396 | 2602815.5046 | 1183987.2932
39 | 2602826.9303 | 1184005.9081 | 2602808.0466 | 1184005.2546 | 2602791.2691 | 1184003.535
40 | 2602826.9303 | 1184005.9081 | 2602828.2251 | 1184012.1341 | 2602828.27 | 1184013.9573
41 | 2602826.9303 | 1184005.9081 | 2602834.7208 | 1183995.5397 | 2602837.7507 | 1183979.8107 | 2602845.4903 | 1183980.5814 | 2602847.2611 | 1183980.7045
42 | 2602828.27 | 1184013.9573 | 2602828.3285 | 1184016.1346
43 | 2602849.0223 | 1183968.588 | 2602847.2611 | 1183980.7045
44 | 2602847.2611 | 1183980.7045 | 2602846.8858 | 1183983.3279
45 | 2602778.0286 | 1183982.5849 | 2602784.4063 | 1183983.3986
46 | 2602829.0955 | 1184044.6957 | 2602828.3285 | 1184016.1346
47 | 2602845.9669 | 1183989.6418 | 2602846.8858 | 1183983.3279
48 | 2602846.8858 | 1183983.3279 | 2602856.1214 | 1183984.2104 | 2602856.5755 | 1183979.6857
49 | 2602829.0955 | 1184044.6957 | 2602830.21 | 1184044.5962 | 2602838.4768 | 1184043.8218 | 2602841.3483 | 1184040.5548 | 2602841.9556 | 1184032.7467
50 | 2602829.0955 | 1184044.6957 | 2602829.5233 | 1184060.7211
51 | 2602829.9659 | 1184077.3018 | 2602830.4145 | 1184080.2178
52 | 2602829.9659 | 1184077.3018 | 2602788.1006 | 1184075.9088
53 | 2602829.9659 | 1184077.3018 | 2602829.5233 | 1184060.7211
54 | 2602769.4742 | 1184079.3086 | 2602776.7806 | 1184075.5321 | 2602788.1006 | 1184075.9088
55 | 2602713.8669 | 1184134.7679 | 2602746.6884 | 1184134.1154 | 2602766.7569 | 1184113.2915 | 2602769.4742 | 1184079.3086
56 | 2602713.8669 | 1184134.7679 | 2602714.5033 | 1184067.7516
57 | 2602874.0311 | 1183570.8728 | 2602921.6019 | 1183622.3106 | 2602933.6716 | 1183635.701 | 2602939.5003 | 1183642.5407 | 2602945.1534 | 1183649.4692 | 2602950.5774 | 1183656.6199 | 2602955.6577 | 1183663.8372 | 2602960.4632 | 1183671.3322 | 2602965.0243 | 1183678.8939 | 2602967.3563 | 1183683.1334
58 | 2602986.1375 | 1183723.8203 | 2602980.6726 | 1183710.8512 | 2602977.0965 | 1183702.7453 | 2602973.3218 | 1183694.6616 | 2602969.3487 | 1183686.7556 | 2602967.3563 | 1183683.1334
59 | 2602989.3264 | 1183731.3882 | 2602986.1375 | 1183723.8203
60 | 2602883.5336 | 1183414.483 | 2602886.9967 | 1183416.8331 | 2602900.3616 | 1183428.3348
61 | 2603047.1273 | 1183749.8925 | 2603045.985 | 1183746.8993
62 | 2603052.7202 | 1183764.5476 | 2603047.1273 | 1183749.8925
63 | 2603041.2957 | 1183730.784 | 2603041.751 | 1183733.9486 | 2603043.4654 | 1183740.2972 | 2603045.985 | 1183746.8993
64 | 2602989.3264 | 1183731.3882 | 2603025.1912 | 1183817.539 | 2603031.8695 | 1183834.5177 | 2603034.705 | 1183842.8122 | 2603037.2809 | 1183851.1511 | 2603039.5666 | 1183859.69 | 2603041.6081 | 1183868.2399 | 2603043.4735 | 1183877.7123 | 2603048.2623 | 1183872.0006 | 2603049.2952 | 1183867.1765 | 2603051.1978 | 1183832.5596 | 2603050.7035 | 1183813.5829 | 2603047.5885 | 1183784.0884 | 2603047.791 | 1183775.9844 | 2603049.1298 | 1183769.9486 | 2603052.7202 | 1183764.5476
65 | 2603052.7202 | 1183764.5476 | 2603059.7233 | 1183757.7698 | 2603065.2148 | 1183751.3804 | 2603069.5695 | 1183744.0899 | 2603072.7407 | 1183737.3103 | 2603075.4622 | 1183729.352 | 2603080.5048 | 1183704.9975 | 2603081.1715 | 1183684.7097 | 2603080.2852 | 1183655.8944
66 | 2603041.2957 | 1183730.784 | 2603040.8153 | 1183727.4448 | 2603040.7487 | 1183725.8191
67 | 2602959.9435 | 1183720.1682 | 2602971.8182 | 1183725.888 | 2602980.2817 | 1183729.783 | 2602982.7392 | 1183730.6068 | 2602985.0214 | 1183730.997 | 2602989.3264 | 1183731.3882
68 | 2603080.2852 | 1183655.8944 | 2603069.0016 | 1183643.3712 | 2603060.5062 | 1183642.133 | 2603046.0696 | 1183645.6054 | 2603036.3518 | 1183646.3231
69 | 2603124.9726 | 1183503.8166 | 2603082.6396 | 1183618.9988 | 2603080.2852 | 1183655.8944
70 | 2603040.1908 | 1183712.1989 | 2603040.7487 | 1183725.8191
71 | 2603124.9726 | 1183503.8166 | 2603139.615 | 1183501.8675 | 2603161.3161 | 1183504.3244 | 2603192.434 | 1183512.9116
72 | 2603124.9726 | 1183503.8166 | 2603146.1837 | 1183464.7296 | 2603173.6448 | 1183430.037 | 2603211.3329 | 1183400.2636 | 2603243.8451 | 1183371.4993 | 2603263.1021 | 1183348.6422 | 2603292.5344 | 1183298.9658 | 2603288.1408 | 1183292.4156
73 | 2603039.9559 | 1183706.4659 | 2603040.1908 | 1183712.1989
74 | 2603234.7393 | 1183282.2931 | 2603288.1408 | 1183292.4156
75 | 2603288.1408 | 1183292.4156 | 2603309.7554 | 1183100.9237

## bus_geodata
| x | y | coords
0 | 2602044.0898 | 1183444.6804
1 | 2602074.4962 | 1183560.3467
2 | 2602132.0759 | 1183339.5639
3 | 2602771.8981 | 1183562.2771
4 | 2602774.2638 | 1183563.7678
5 | 2602077.0038 | 1183298.513
6 | 2602423.3077 | 1183288.0862
7 | 2602449.9327 | 1183167.2758
8 | 2602452.6463 | 1183151.1676
9 | 2602954.3562 | 1183105.9684
10 | 2602940.9177 | 1183122.1184
11 | 2602869.4696 | 1182689.4571
12 | 2602817.6911 | 1183497.3756
13 | 2602630.0788 | 1182807.845
14 | 2602626.4568 | 1182808.5706
15 | 2602615.9329 | 1182818.4043
16 | 2602611.5135 | 1182742.5081
17 | 2602590.2758 | 1182756.3174
18 | 2602597.8169 | 1182815.084
19 | 2602594.4437 | 1182787.397
20 | 2602832.588 | 1183522.4176
21 | 2602866.2521 | 1183424.7719
22 | 2602860.538 | 1183564.4966
23 | 2602756.6418 | 1183842.2171
24 | 2602752.262 | 1183840.6669
25 | 2602761.3822 | 1183843.8949
26 | 2602749.9567 | 1183857.8192
27 | 2602731.3461 | 1183825.5832
28 | 2602758.1452 | 1183862.214
29 | 2602772.5478 | 1183847.8464
30 | 2602741.0022 | 1183800.2616
31 | 2602810.2563 | 1183950.7419
32 | 2602780.0261 | 1183829.1613
33 | 2602811.5916 | 1183960.0412
34 | 2602781.7028 | 1183824.9721
35 | 2602815.5046 | 1183987.2932
36 | 2602791.2691 | 1184003.535
37 | 2602826.9303 | 1184005.9081
38 | 2602828.27 | 1184013.9573
39 | 2602847.2611 | 1183980.7045
40 | 2602784.4063 | 1183983.3986
41 | 2602828.3285 | 1184016.1346
42 | 2602849.0223 | 1183968.588
43 | 2602846.8858 | 1183983.3279
44 | 2602778.0286 | 1183982.5849
45 | 2602841.9556 | 1184032.7467
46 | 2602829.0955 | 1184044.6957
47 | 2602845.9669 | 1183989.6418
48 | 2602856.5755 | 1183979.6857
49 | 2602830.4145 | 1184080.2178
50 | 2602829.9659 | 1184077.3018
51 | 2602788.1006 | 1184075.9088
52 | 2602829.5233 | 1184060.7211
53 | 2602713.8669 | 1184134.7679
54 | 2602769.4742 | 1184079.3086
55 | 2602714.5033 | 1184067.7516
56 | 2602874.0311 | 1183570.8728
57 | 2602967.3563 | 1183683.1334
58 | 2602986.1375 | 1183723.8203
59 | 2602883.5336 | 1183414.483
60 | 2602900.3616 | 1183428.3348
61 | 2603047.1273 | 1183749.8925
62 | 2603045.985 | 1183746.8993
63 | 2603052.7202 | 1183764.5476
64 | 2603041.2957 | 1183730.784
65 | 2602989.3264 | 1183731.3882
66 | 2603080.2852 | 1183655.8944
67 | 2603040.7487 | 1183725.8191
68 | 2602959.9435 | 1183720.1682
69 | 2603036.3518 | 1183646.3231
70 | 2603124.9726 | 1183503.8166
71 | 2603040.1908 | 1183712.1989
72 | 2603192.434 | 1183512.9116
73 | 2603288.1408 | 1183292.4156
74 | 2603039.9559 | 1183706.4659
75 | 2603309.7554 | 1183100.9237
76 | 2603234.7393 | 1183282.2931
77 | 2602761.3822 | 1183843.8949

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97049 | -0.21189 | 0.0021486 | 0.00053848
1 | 0.97086 | -0.20916 | 0 | 0
2 | 0.97158 | -0.20391 | 0 | 0
3 | 0.99236 | -0.053844 | 0.00066632 | 0.000167
4 | 0.99237 | -0.053825 | 0.0019826 | 0.00049688
5 | 0.97152 | -0.20437 | 0.00057799 | 0.00014486
6 | 0.97277 | -0.19523 | 0.0006395 | 0.00016027
7 | 0.97338 | -0.19075 | 0.00022069 | 5.5309e-05
8 | 0.97347 | -0.19009 | 0.0013739 | 0.00034433
9 | 0.98517 | -0.10531 | 0.0014749 | 0.00036964
10 | 0.98546 | -0.1032 | 0 | 0
11 | 0.98014 | -0.14153 | 0.00016855 | 4.2242e-05
12 | 0.99163 | -0.059076 | 0 | 0
13 | 0.976 | -0.17159 | 0.00012694 | 3.1814e-05
14 | 0.976 | -0.17159 | 0.0021384 | 0.00053594
15 | 0.97605 | -0.17125 | 0.00013728 | 3.4406e-05
16 | 0.9771 | -0.16361 | 0 | 0
17 | 0.97679 | -0.16582 | 0 | 0
18 | 0.97613 | -0.17065 | 0 | 0
19 | 0.97643 | -0.16846 | 0.00054366 | 0.00013625
20 | 0.99204 | -0.056183 | 0 | 0
21 | 0.99097 | -0.06374 | 0.0048053 | 0.0012043
22 | 0.9927 | -0.051485 | 0 | 0
23 | 0.99962 | -0.0026775 | 0.00058925 | 0.00014768
24 | 0.99952 | -0.0033936 | 0 | 0
25 | 0.99973 | -0.0018878 | 0 | 0
26 | 0.9995 | -0.003499 | 0.00060849 | 0.0001525
27 | 0.99893 | -0.0075058 | 0 | 0
28 | 0.99972 | -0.0019923 | 0.00056018 | 0.0001404
29 | 1 | 0 | -0.18477 | -0.046498
30 | 0.99835 | -0.011607 | 0.00036641 | 9.183e-05
31 | 0.98807 | -0.082837 | 0.0042369 | 0.0010619
32 | 0.99998 | -0.00013541 | 0.00029967 | 7.5105e-05
33 | 0.98708 | -0.089764 | 0.0064798 | 0.001624
34 | 0.99998 | -0.00015221 | 0.000373 | 9.3483e-05
35 | 0.98433 | -0.10922 | 0 | 0
36 | 0.9813 | -0.13066 | 0.0022874 | 0.00057327
37 | 0.98142 | -0.12981 | 0 | 0
38 | 0.98125 | -0.13102 | 0 | 0
39 | 0.97732 | -0.15904 | 0 | 0
40 | 0.98213 | -0.12481 | 0.011487 | 0.0028789
41 | 0.98121 | -0.13134 | 0.00058097 | 0.0001456
42 | 0.97635 | -0.166 | 0.05431 | 0.013611
43 | 0.97725 | -0.15956 | 0 | 0
44 | 0.98179 | -0.12725 | 0.036684 | 0.0091939
45 | 0.98045 | -0.13678 | 0.0062904 | 0.0015765
46 | 0.98064 | -0.13537 | 0 | 0
47 | 0.97716 | -0.16018 | 0.0093605 | 0.002346
48 | 0.97706 | -0.1609 | 0.0092857 | 0.0023272
49 | 0.98032 | -0.13768 | 0.0011595 | 0.00029059
50 | 0.98033 | -0.13765 | 0 | 0
51 | 0.98002 | -0.13981 | 0.0010945 | 0.00027432
52 | 0.98047 | -0.13659 | 0.0011751 | 0.00029452
53 | 0.97964 | -0.14253 | 0 | 0
54 | 0.97991 | -0.1406 | 0.0019311 | 0.00048398
55 | 0.97946 | -0.14388 | 0.0019315 | 0.00048408
56 | 0.99241 | -0.053506 | 0 | 0
57 | 0.99017 | -0.069461 | 0.0008261 | 0.00020704
58 | 0.98954 | -0.07398 | 0.00079227 | 0.00019856
59 | 0.99091 | -0.064136 | 0.00083459 | 0.00020917
60 | 0.99088 | -0.064352 | 0.00097024 | 0.00024316
61 | 0.98602 | -0.099193 | 0.000863 | 0.00021629
62 | 0.986 | -0.099292 | 0.00048051 | 0.00012043
63 | 0.9861 | -0.098569 | 0 | 0
64 | 0.98594 | -0.09973 | 0.00072353 | 0.00018133
65 | 0.98943 | -0.074741 | 0 | 0
66 | 0.98533 | -0.10413 | 0 | 0
67 | 0.98593 | -0.099823 | 0.00054607 | 0.00013686
68 | 0.98941 | -0.074918 | 0.00054519 | 0.00013664
69 | 0.98525 | -0.1047 | 0.0011056 | 0.00027708
70 | 0.98453 | -0.10991 | 0 | 0
71 | 0.9859 | -0.099999 | 0.00074664 | 0.00018713
72 | 0.98449 | -0.11023 | 0.00044799 | 0.00011228
73 | 0.98333 | -0.11856 | 0 | 0
74 | 0.9859 | -0.10003 | 0.00051176 | 0.00012826
75 | 0.98282 | -0.12227 | 0.0018532 | 0.00046446
76 | 0.98324 | -0.11921 | 0.0011545 | 0.00028935
77 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021486 | -0.00053848 | 0.0021494 | 0.00053731 | 8.1045e-07 | -1.1679e-06 | 0.0032943 | 0.0032938 | 0.0032943 | 0.97049 | -0.21189 | 0.97086 | -0.20916 | 1.2201
1 | -0.0021494 | -0.00053731 | 0.0021509 | 0.00053508 | 1.5457e-06 | -2.2319e-06 | 0.0032938 | 0.0032928 | 0.0032938 | 0.97086 | -0.20916 | 0.97158 | -0.20391 | 1.2199
2 | 0.00057802 | 0.00014395 | -0.00057799 | -0.00014486 | 3.6251e-08 | -9.0438e-07 | 0.00088493 | 0.00088526 | 0.00088526 | 0.97158 | -0.20391 | 0.97152 | -0.20437 | 0.32788
3 | -0.0027289 | -0.00067903 | 0.0027322 | 0.00067661 | 3.2199e-06 | -2.4286e-06 | 0.0041777 | 0.0041764 | 0.0041777 | 0.97158 | -0.20391 | 0.97277 | -0.19523 | 1.5473
4 | -0.00066632 | -0.000167 | 0.00066632 | 0.00016696 | 1.7418e-09 | -3.5457e-08 | 0.00099912 | 0.00099911 | 0.00099912 | 0.99236 | -0.053844 | 0.99237 | -0.053825 | 0.37005
5 | -0.0026489 | -0.00066384 | 0.0026497 | 0.00066304 | 8.5672e-07 | -7.9537e-07 | 0.0039719 | 0.0039715 | 0.0039719 | 0.99237 | -0.053825 | 0.9927 | -0.051485 | 1.4711
6 | -0.0033717 | -0.00083688 | 0.0033737 | 0.00083613 | 2.0533e-06 | -7.4885e-07 | 0.0051546 | 0.0051541 | 0.0051546 | 0.97277 | -0.19523 | 0.97338 | -0.19075 | 1.9091
7 | -0.0035944 | -0.00089144 | 0.0035947 | 0.00089135 | 3.195e-07 | -8.819e-08 | 0.0054914 | 0.0054914 | 0.0054914 | 0.97338 | -0.19075 | 0.97347 | -0.19009 | 2.0339
8 | -0.0049686 | -0.0012357 | 0.0049818 | 0.0012362 | 1.3162e-05 | 4.9857e-07 | 0.0075914 | 0.0075898 | 0.0075914 | 0.97347 | -0.19009 | 0.97613 | -0.17065 | 2.8116
9 | -0.0096436 | -0.0024039 | 0.0096464 | 0.0024047 | 2.7797e-06 | 8.0154e-07 | 0.014561 | 0.014561 | 0.014561 | 0.98517 | -0.10531 | 0.98546 | -0.1032 | 5.3931
10 | 0.0081687 | 0.0020343 | -0.0081284 | -0.0020241 | 4.0355e-05 | 1.0136e-05 | 0.012334 | 0.012336 | 0.012336 | 0.98517 | -0.10531 | 0.98014 | -0.14153 | 4.5687
11 | -0.0096464 | -0.0024047 | 0.0097049 | 0.0024216 | 5.8538e-05 | 1.6842e-05 | 0.014561 | 0.014559 | 0.014561 | 0.98546 | -0.1032 | 0.99163 | -0.059076 | 5.393
12 | 0.0079598 | 0.0019819 | -0.0079359 | -0.001976 | 2.3982e-05 | 5.9148e-06 | 0.01208 | 0.012081 | 0.012081 | 0.98014 | -0.14153 | 0.9771 | -0.16361 | 4.4744
13 | -0.0097049 | -0.0024216 | 0.0097088 | 0.0024227 | 3.8547e-06 | 1.1065e-06 | 0.014559 | 0.014559 | 0.014559 | 0.99163 | -0.059076 | 0.99204 | -0.056183 | 5.3923
14 | -0.00012694 | -3.1814e-05 | 0.00012694 | 3.1768e-05 | 8.6332e-11 | -4.6131e-08 | 0.00019354 | 0.00019352 | 0.00019354 | 0.976 | -0.17159 | 0.976 | -0.17159 | 0.07168
15 | -0.0022654 | -0.00056771 | 0.0022655 | 0.00056757 | 1.0735e-07 | -1.3895e-07 | 0.0034538 | 0.0034537 | 0.0034538 | 0.976 | -0.17159 | 0.97605 | -0.17125 | 1.2792
16 | -0.0024028 | -0.00060198 | 0.002403 | 0.00060176 | 1.994e-07 | -2.2099e-07 | 0.003663 | 0.0036629 | 0.003663 | 0.97605 | -0.17125 | 0.97613 | -0.17065 | 1.3567
17 | 0.0079359 | 0.001976 | -0.0079335 | -0.0019754 | 2.3946e-06 | 5.9176e-07 | 0.012081 | 0.012081 | 0.012081 | 0.9771 | -0.16361 | 0.97679 | -0.16582 | 4.4744
18 | 0.0079335 | 0.0019754 | -0.0079306 | -0.0019747 | 2.8612e-06 | 7.0736e-07 | 0.012081 | 0.012081 | 0.012081 | 0.97679 | -0.16582 | 0.97643 | -0.16846 | 4.4745
19 | -0.0073847 | -0.0018379 | 0.0073869 | 0.0018384 | 2.2062e-06 | 4.9938e-07 | 0.011253 | 0.011253 | 0.011253 | 0.97613 | -0.17065 | 0.97643 | -0.16846 | 4.1677
20 | 0.0066171 | 0.0016573 | -0.0066102 | -0.0016561 | 6.9126e-06 | 1.2084e-06 | 0.0099251 | 0.0099256 | 0.0099256 | 0.99204 | -0.056183 | 0.99097 | -0.06374 | 3.6761
21 | -0.016326 | -0.00408 | 0.016336 | 0.0040826 | 1.0561e-05 | 2.6029e-06 | 0.024484 | 0.024484 | 0.024484 | 0.99204 | -0.056183 | 0.9927 | -0.051485 | 4.5341
22 | 0.001805 | 0.00045182 | -0.0018049 | -0.00045206 | 9.8888e-08 | -2.3992e-07 | 0.0027101 | 0.0027102 | 0.0027102 | 0.99097 | -0.06374 | 0.99091 | -0.064136 | 1.0038
23 | 0.010669 | 0.0026644 | -0.010666 | -0.0026635 | 2.9642e-06 | 8.999e-07 | 0.015989 | 0.015989 | 0.015989 | 0.9927 | -0.051485 | 0.99241 | -0.053506 | 5.9218
24 | -0.029655 | -0.0074101 | 0.029819 | 0.0074661 | 0.00016353 | 5.5995e-05 | 0.044444 | 0.044442 | 0.044444 | 0.9927 | -0.051485 | 0.99835 | -0.011607 | 8.2304
25 | 0.030831 | 0.007723 | -0.030828 | -0.007722 | 3.053e-06 | 1.0524e-06 | 0.045893 | 0.045893 | 0.045893 | 0.99962 | -0.0026775 | 0.99952 | -0.0033936 | 8.4987
26 | -0.03142 | -0.0078707 | 0.031424 | 0.0078719 | 3.4319e-06 | 1.1881e-06 | 0.04677 | 0.04677 | 0.04677 | 0.99962 | -0.0026775 | 0.99973 | -0.0018878 | 8.6611
27 | 0.0006085 | 0.00015228 | -0.00060849 | -0.0001525 | 8.8633e-09 | -2.2346e-07 | 0.00090581 | 0.00090589 | 0.00090589 | 0.99952 | -0.0033936 | 0.9995 | -0.003499 | 0.33552
28 | 0.030219 | 0.0075697 | -0.030202 | -0.0075638 | 1.7177e-05 | 5.8939e-06 | 0.044987 | 0.044987 | 0.044987 | 0.99952 | -0.0033936 | 0.99893 | -0.0075058 | 8.331
29 | 0.00056019 | 0.00014015 | -0.00056018 | -0.0001404 | 8.0855e-09 | -2.413e-07 | 0.00083371 | 0.0008338 | 0.0008338 | 0.99973 | -0.0018878 | 0.99972 | -0.0019923 | 0.30881
30 | -0.031984 | -0.008012 | 0.031992 | 0.0080149 | 8.3528e-06 | 2.9027e-06 | 0.047604 | 0.047604 | 0.047604 | 0.99973 | -0.0018878 | 1 | 0 | 8.8155
31 | 0.030202 | 0.0075638 | -0.030185 | -0.0075579 | 1.7112e-05 | 5.8726e-06 | 0.044987 | 0.044988 | 0.044988 | 0.99893 | -0.0075058 | 0.99835 | -0.011607 | 8.331
32 | 0.15131 | 0.038314 | -0.14956 | -0.037644 | 0.0017507 | 0.00067047 | 0.22528 | 0.22529 | 0.22529 | 1 | 0 | 0.98807 | -0.082837 | 41.7195
33 | 0.00067269 | 0.00016827 | -0.00067267 | -0.00016853 | 1.2581e-08 | -2.592e-07 | 0.0010009 | 0.0010009 | 0.0010009 | 1 | 0 | 0.99998 | -0.00013541 | 0.37072
34 | 0.14532 | 0.036582 | -0.14518 | -0.036528 | 0.00014046 | 5.3782e-05 | 0.2189 | 0.2189 | 0.2189 | 0.98807 | -0.082837 | 0.98708 | -0.089764 | 40.5379
35 | 0.000373 | 9.3424e-05 | -0.000373 | -9.3483e-05 | 8.6738e-10 | -5.8861e-08 | 0.00055502 | 0.00055504 | 0.00055504 | 0.99998 | -0.00013541 | 0.99998 | -0.00015221 | 0.20557
36 | 0.1387 | 0.034904 | -0.13832 | -0.03476 | 0.0003757 | 0.0001438 | 0.20914 | 0.20914 | 0.20914 | 0.98708 | -0.089764 | 0.98433 | -0.10922 | 38.729
37 | 0.048288 | 0.012117 | -0.048184 | -0.012078 | 0.00010423 | 3.969e-05 | 0.073003 | 0.073003 | 0.073003 | 0.98433 | -0.10922 | 0.98213 | -0.12481 | 27.0381
38 | 0.090035 | 0.022643 | -0.089777 | -0.022544 | 0.00025765 | 9.8815e-05 | 0.13613 | 0.13613 | 0.13613 | 0.98433 | -0.10922 | 0.98142 | -0.12981 | 50.4201
39 | -0.0022874 | -0.00057327 | 0.0022876 | 0.00057292 | 2.6844e-07 | -3.4858e-07 | 0.0034685 | 0.0034683 | 0.0034685 | 0.9813 | -0.13066 | 0.98142 | -0.12981 | 1.2846
40 | 0.01418 | 0.003552 | -0.014177 | -0.0035512 | 2.3603e-06 | 8.0442e-07 | 0.021499 | 0.021499 | 0.021499 | 0.98142 | -0.12981 | 0.98125 | -0.13102 | 7.9625
41 | 0.073309 | 0.018419 | -0.073013 | -0.018306 | 0.00029691 | 0.00011371 | 0.11117 | 0.11117 | 0.11117 | 0.98142 | -0.12981 | 0.97732 | -0.15904 | 41.1732
42 | 0.014177 | 0.0035512 | -0.014177 | -0.003551 | 6.2819e-07 | 2.141e-07 | 0.021499 | 0.021499 | 0.021499 | 0.98125 | -0.13102 | 0.98121 | -0.13134 | 7.9625
43 | 0.054363 | 0.013631 | -0.05431 | -0.013611 | 5.2353e-05 | 1.9983e-05 | 0.082772 | 0.082772 | 0.082772 | 0.97732 | -0.15904 | 0.97635 | -0.166 | 30.6563
44 | 0.01865 | 0.0046744 | -0.018649 | -0.0046739 | 1.3338e-06 | 4.7979e-07 | 0.028396 | 0.028396 | 0.028396 | 0.97732 | -0.15904 | 0.97725 | -0.15956 | 10.5169
45 | 0.036696 | 0.0091986 | -0.036684 | -0.0091939 | 1.2402e-05 | 4.6886e-06 | 0.055599 | 0.055599 | 0.055599 | 0.98213 | -0.12481 | 0.98179 | -0.12725 | 20.5922
46 | 0.013596 | 0.0034054 | -0.013588 | -0.0034028 | 7.5787e-06 | 2.5542e-06 | 0.020618 | 0.020618 | 0.020618 | 0.98121 | -0.13134 | 0.98064 | -0.13537 | 7.6362
47 | 0.0093613 | 0.0023462 | -0.0093605 | -0.002346 | 8.0913e-07 | 2.3125e-07 | 0.014254 | 0.014254 | 0.014254 | 0.97725 | -0.15956 | 0.97716 | -0.16018 | 5.2793
48 | 0.0092874 | 0.0023277 | -0.0092857 | -0.0023272 | 1.7252e-06 | 4.9037e-07 | 0.014142 | 0.014142 | 0.014142 | 0.97725 | -0.15956 | 0.97706 | -0.1609 | 5.2376
49 | -0.0062904 | -0.0015765 | 0.0062916 | 0.0015767 | 1.2286e-06 | 2.0005e-07 | 0.0095469 | 0.0095468 | 0.0095469 | 0.98045 | -0.13678 | 0.98064 | -0.13537 | 3.5359
50 | 0.0072967 | 0.0018261 | -0.0072954 | -0.0018258 | 1.2261e-06 | 2.6935e-07 | 0.011071 | 0.011071 | 0.011071 | 0.98064 | -0.13537 | 0.98047 | -0.13659 | 4.1004
51 | -0.0011595 | -0.00029059 | 0.0011595 | 0.00029055 | 5.7023e-09 | -3.5005e-08 | 0.0017599 | 0.0017599 | 0.0017599 | 0.98032 | -0.13768 | 0.98033 | -0.13765 | 0.65183
52 | 0.0049599 | 0.0012406 | -0.0049585 | -0.0012406 | 1.4812e-06 | 4.1725e-08 | 0.0075277 | 0.0075279 | 0.0075279 | 0.98033 | -0.13765 | 0.98002 | -0.13981 | 2.7881
53 | -0.0061194 | -0.0015312 | 0.0061203 | 0.0015313 | 8.9279e-07 | 1.3422e-07 | 0.0092876 | 0.0092876 | 0.0092876 | 0.98033 | -0.13765 | 0.98047 | -0.13659 | 3.4399
54 | 0.0038639 | 0.00096627 | -0.0038635 | -0.00096635 | 4.198e-07 | -8.4858e-08 | 0.005866 | 0.0058661 | 0.0058661 | 0.98002 | -0.13981 | 0.97991 | -0.1406 | 2.1726
55 | -0.0019319 | -0.00048338 | 0.0019324 | 0.00048237 | 5.1478e-07 | -1.009e-06 | 0.0029341 | 0.0029337 | 0.0029341 | 0.97964 | -0.14253 | 0.97991 | -0.1406 | 1.0867
56 | 0.0019319 | 0.00048338 | -0.0019315 | -0.00048408 | 3.6007e-07 | -7.0517e-07 | 0.0029341 | 0.0029344 | 0.0029344 | 0.97964 | -0.14253 | 0.97946 | -0.14388 | 1.0868
57 | 0.010666 | 0.0026635 | -0.010643 | -0.0026564 | 2.3354e-05 | 7.095e-06 | 0.015989 | 0.01599 | 0.01599 | 0.99241 | -0.053506 | 0.99017 | -0.069461 | 5.9221
58 | 0.0098164 | 0.0024494 | -0.0098103 | -0.0024476 | 6.0856e-06 | 1.7642e-06 | 0.014748 | 0.014748 | 0.014748 | 0.99017 | -0.069461 | 0.98954 | -0.07398 | 5.4623
59 | 0.0090181 | 0.0022491 | -0.0090171 | -0.0022488 | 9.4184e-07 | 2.5676e-07 | 0.013557 | 0.013557 | 0.013557 | 0.98954 | -0.07398 | 0.98943 | -0.074741 | 5.0211
60 | 0.00097027 | 0.00024289 | -0.00097024 | -0.00024316 | 2.89e-08 | -2.6993e-07 | 0.0014569 | 0.001457 | 0.001457 | 0.99091 | -0.064136 | 0.99088 | -0.064352 | 0.53964
61 | 0.0030088 | 0.00075353 | -0.0030087 | -0.00075356 | 4.1213e-08 | -2.5012e-08 | 0.0045404 | 0.0045404 | 0.0045404 | 0.98602 | -0.099193 | 0.986 | -0.099292 | 1.6816
62 | -0.0038718 | -0.00096982 | 0.0038721 | 0.00096975 | 3.3414e-07 | -7.1577e-08 | 0.0058427 | 0.0058427 | 0.0058427 | 0.98602 | -0.099193 | 0.9861 | -0.098569 | 2.164
63 | 0.0025282 | 0.00063313 | -0.002528 | -0.00063329 | 1.5296e-07 | -1.5594e-07 | 0.0038152 | 0.0038153 | 0.0038153 | 0.986 | -0.099292 | 0.98594 | -0.09973 | 1.4131
64 | -0.0084443 | -0.0021055 | 0.0084719 | 0.0021126 | 2.7621e-05 | 7.1314e-06 | 0.012738 | 0.012737 | 0.012738 | 0.9861 | -0.098569 | 0.98943 | -0.074741 | 4.7179
65 | 0.0045722 | 0.0011357 | -0.0045687 | -0.0011359 | 3.4588e-06 | -1.5548e-07 | 0.0068958 | 0.0068963 | 0.0068963 | 0.9861 | -0.098569 | 0.98533 | -0.10413 | 2.5542
66 | 0.0018045 | 0.00045195 | -0.0018045 | -0.00045201 | 2.3143e-08 | -5.4871e-08 | 0.0027233 | 0.0027234 | 0.0027234 | 0.98594 | -0.09973 | 0.98593 | -0.099823 | 1.0087
67 | 0.0005452 | 0.00013624 | -0.00054519 | -0.00013664 | 1.3275e-08 | -4.0137e-07 | 0.00081979 | 0.00081994 | 0.00081994 | 0.98943 | -0.074741 | 0.98941 | -0.074918 | 0.30368
68 | 0.0011057 | 0.00027648 | -0.0011056 | -0.00027708 | 8.6839e-08 | -6.0242e-07 | 0.0016695 | 0.0016697 | 0.0016697 | 0.98533 | -0.10413 | 0.98525 | -0.1047 | 0.61842
69 | 0.0034631 | 0.00085938 | -0.0034604 | -0.00086036 | 2.7224e-06 | -9.8512e-07 | 0.0052268 | 0.0052275 | 0.0052275 | 0.98533 | -0.10413 | 0.98453 | -0.10991 | 1.9361
70 | 0.0012584 | 0.00031515 | -0.0012584 | -0.00031531 | 3.0682e-08 | -1.6203e-07 | 0.0018992 | 0.0018993 | 0.0018993 | 0.98593 | -0.099823 | 0.9859 | -0.099999 | 0.70343
71 | 0.00044801 | 0.00011141 | -0.00044799 | -0.00011228 | 1.9646e-08 | -8.6604e-07 | 0.0006768 | 0.00067711 | 0.00067711 | 0.98453 | -0.10991 | 0.98449 | -0.11023 | 0.25078
72 | 0.0030123 | 0.00074895 | -0.0030088 | -0.00075108 | 3.5633e-06 | -2.1309e-06 | 0.0045507 | 0.0045519 | 0.0045519 | 0.98453 | -0.10991 | 0.98333 | -0.11856 | 1.6859
73 | 0.00051176 | 0.00012819 | -0.00051176 | -0.00012826 | 2.136e-09 | -7.2348e-08 | 0.00077237 | 0.00077239 | 0.00077239 | 0.9859 | -0.099999 | 0.9859 | -0.10003 | 0.28607
74 | 0.0011546 | 0.0002887 | -0.0011545 | -0.00028935 | 1.0323e-07 | -6.4779e-07 | 0.001747 | 0.0017472 | 0.0017472 | 0.98333 | -0.11856 | 0.98324 | -0.11921 | 0.64712
75 | 0.0018542 | 0.00046238 | -0.0018532 | -0.00046446 | 9.4639e-07 | -2.0793e-06 | 0.002805 | 0.0028058 | 0.0028058 | 0.98333 | -0.11856 | 0.98282 | -0.12227 | 1.0392

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18477 | 0.046498

## res_load
| p_mw | q_mvar
0 | 0.0021486 | 0.00053848
1 | 0.00066632 | 0.000167
2 | 0.0019826 | 0.00049688
3 | 0.00057799 | 0.00014486
4 | 0.0006395 | 0.00016027
5 | 0.00022069 | 5.5309e-05
6 | 0.0013739 | 0.00034433
7 | 0.0014749 | 0.00036964
8 | 0.00016855 | 4.2242e-05
9 | 0.00012694 | 3.1814e-05
10 | 0.0021384 | 0.00053594
11 | 0.00013728 | 3.4406e-05
12 | 0.00054366 | 0.00013625
13 | 0.0048053 | 0.0012043
14 | 0.00058925 | 0.00014768
15 | 0.00060849 | 0.0001525
16 | 0.00056018 | 0.0001404
17 | 0.00036641 | 9.183e-05
18 | 0.0042369 | 0.0010619
19 | 0.00029967 | 7.5105e-05
20 | 0.0064798 | 0.001624
21 | 0.000373 | 9.3483e-05
22 | 0.0022874 | 0.00057327
23 | 0.011487 | 0.0028789
24 | 0.00058097 | 0.0001456
25 | 0.05431 | 0.013611
26 | 0.036684 | 0.0091939
27 | 0.0062904 | 0.0015765
28 | 0.0093605 | 0.002346
29 | 0.0092857 | 0.0023272
30 | 0.0011595 | 0.00029059
31 | 0.0010945 | 0.00027432
32 | 0.0011751 | 0.00029452
33 | 0.0019311 | 0.00048398
34 | 0.0019315 | 0.00048408
35 | 0.0008261 | 0.00020704
36 | 0.00079227 | 0.00019856
37 | 0.00083459 | 0.00020917
38 | 0.00097024 | 0.00024316
39 | 0.000863 | 0.00021629
40 | 0.00048051 | 0.00012043
41 | 0.00072353 | 0.00018133
42 | 0.00054607 | 0.00013686
43 | 0.00054519 | 0.00013664
44 | 0.0011056 | 0.00027708
45 | 0.00074664 | 0.00018713
46 | 0.00044799 | 0.00011228
47 | 0.00051176 | 0.00012826
48 | 0.0018532 | 0.00046446
49 | 0.0011545 | 0.00028935

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1