## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_901-2_1_1_node_219 | 0.4 | n |  | TRUE
1 | bus_LV_901-2_1_1_node_194 | 0.4 | n |  | TRUE
2 | bus_LV_901-2_1_1_node_191 | 0.4 | n |  | TRUE
3 | bus_LV_901-2_1_1_node_192 | 0.4 | n |  | TRUE
4 | bus_LV_901-2_1_1_node_86 | 0.4 | n |  | TRUE
5 | bus_LV_901-2_1_1_node_87 | 0.4 | n |  | TRUE
6 | bus_LV_901-2_1_1_node_88 | 0.4 | n |  | TRUE
7 | bus_LV_901-2_1_1_node_89 | 0.4 | n |  | TRUE
8 | bus_LV_901-2_1_1_node_90 | 0.4 | n |  | TRUE
9 | bus_LV_901-2_1_1_node_230 | 0.4 | n |  | TRUE
10 | bus_LV_901-2_1_1_node_101 | 0.4 | n |  | TRUE
11 | bus_LV_901-2_1_1_node_150 | 0.4 | n |  | TRUE
12 | bus_LV_901-2_1_1_node_91 | 0.4 | n |  | TRUE
13 | bus_LV_901-2_1_1_node_182 | 0.4 | n |  | TRUE
14 | bus_LV_901-2_1_1_node_233 | 0.4 | n |  | TRUE
15 | bus_LV_901-2_1_1_node_92 | 0.4 | n |  | TRUE
16 | bus_LV_901-2_1_1_node_181 | 0.4 | n |  | TRUE
17 | bus_LV_901-2_1_1_node_180 | 0.4 | n |  | TRUE
18 | bus_LV_901-2_1_1_node_93 | 0.4 | n |  | TRUE
19 | bus_LV_901-2_1_1_node_94 | 0.4 | n |  | TRUE
20 | bus_LV_901-2_1_1_node_95 | 0.4 | n |  | TRUE
21 | bus_LV_901-2_1_1_node_97 | 0.4 | n |  | TRUE
22 | bus_LV_901-2_1_1_node_96 | 0.4 | n |  | TRUE
23 | bus_LV_901-2_1_1_node_179 | 0.4 | n |  | TRUE
24 | bus_LV_901-2_1_1_node_199 | 0.4 | n |  | TRUE
25 | bus_LV_901-2_1_1_node_99 | 0.4 | n |  | TRUE
26 | bus_LV_901-2_1_1_node_151 | 0.4 | n |  | TRUE
27 | bus_LV_901-2_1_1_node_189 | 0.4 | n |  | TRUE
28 | bus_LV_901-2_1_1_node_177 | 0.4 | n |  | TRUE
29 | bus_LV_901-2_1_1_node_200 | 0.4 | n |  | TRUE
30 | bus_LV_901-2_1_1_node_98 | 0.4 | n |  | TRUE
31 | bus_LV_901-2_1_1_node_100 | 0.4 | n |  | TRUE
32 | bus_LV_901-2_1_1_node_102 | 0.4 | n |  | TRUE
33 | bus_LV_901-2_1_1_node_103 | 0.4 | n |  | TRUE
34 | bus_LV_901-2_1_1_node_104 | 0.4 | n |  | TRUE
35 | bus_LV_901-2_1_1_node_105 | 0.4 | n |  | TRUE
36 | bus_LV_901-2_1_1_node_106 | 0.4 | n |  | TRUE
37 | bus_LV_901-2_1_1_node_121 | 0.4 | n |  | TRUE
38 | bus_LV_901-2_1_1_node_122 | 0.4 | n |  | TRUE
39 | bus_LV_901-2_1_1_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_901-2_1_1_node_108 | 0.4 | n |  | TRUE
41 | bus_LV_901-2_1_1_node_148 | 0.4 | n |  | TRUE
42 | bus_LV_901-2_1_1_node_109 | 0.4 | n |  | TRUE
43 | bus_LV_901-2_1_1_node_110 | 0.4 | n |  | TRUE
44 | bus_LV_901-2_1_1_node_149 | 0.4 | n |  | TRUE
45 | bus_LV_901-2_1_1_node_147 | 0.4 | n |  | TRUE
46 | bus_LV_901-2_1_1_node_116 | 0.4 | n |  | TRUE
47 | bus_LV_901-2_1_1_node_113 | 0.4 | n |  | TRUE
48 | bus_LV_901-2_1_1_node_129 | 0.4 | n |  | TRUE
49 | bus_LV_901-2_1_1_node_127 | 0.4 | n |  | TRUE
50 | bus_LV_901-2_1_1_node_125 | 0.4 | n |  | TRUE
51 | bus_LV_901-2_1_1_node_114 | 0.4 | n |  | TRUE
52 | bus_LV_901-2_1_1_node_128 | 0.4 | n |  | TRUE
53 | bus_LV_901-2_1_1_node_134 | 0.4 | n |  | TRUE
54 | bus_LV_901-2_1_1_node_210 | 0.4 | n |  | TRUE
55 | bus_LV_901-2_1_1_node_133 | 0.4 | n |  | TRUE
56 | bus_LV_901-2_1_1_node_131 | 0.4 | n |  | TRUE
57 | bus_LV_901-2_1_1_node_115 | 0.4 | n |  | TRUE
58 | bus_LV_901-2_1_1_node_126 | 0.4 | n |  | TRUE
59 | bus_LV_901-2_1_1_node_142 | 0.4 | n |  | TRUE
60 | bus_LV_901-2_1_1_node_144 | 0.4 | n |  | TRUE
61 | bus_LV_901-2_1_1_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_901-2_1_1_node_117 | 0.4 | n |  | TRUE
63 | bus_LV_901-2_1_1_node_118 | 0.4 | n |  | TRUE
64 | bus_LV_901-2_1_1_node_119 | 0.4 | n |  | TRUE
65 | bus_LV_901-2_1_1_node_120 | 0.4 | n |  | TRUE
66 | bus_LV_901-2_1_1_node_208 | 0.4 | n |  | TRUE
67 | bus_LV_901-2_1_1_node_213 | 0.4 | n |  | TRUE
68 | bus_LV_901-2_1_1_node_166 | 0.4 | n |  | TRUE
69 | bus_LV_901-2_1_1_node_164 | 0.4 | n |  | TRUE
70 | bus_LV_901-2_1_1_node_228 | 0.4 | n |  | TRUE
71 | bus_LV_901-2_1_1_node_207 | 0.4 | n |  | TRUE
72 | bus_LV_901-2_1_1_node_214 | 0.4 | n |  | TRUE
73 | bus_LV_901-2_1_1_node_123 | 0.4 | n |  | TRUE
74 | bus_LV_901-2_1_1_node_204 | 0.4 | n |  | TRUE
75 | bus_LV_901-2_1_1_node_202 | 0.4 | n |  | TRUE
76 | bus_LV_901-2_1_1_node_135 | 0.4 | n |  | TRUE
77 | bus_LV_901-2_1_1_node_137 | 0.4 | n |  | TRUE
78 | bus_LV_901-2_1_1_node_138 | 0.4 | n |  | TRUE
79 | bus_LV_901-2_1_1_node_141 | 0.4 | n |  | TRUE
80 | bus_LV_901-2_1_1_node_139 | 0.4 | n |  | TRUE
81 | bus_LV_901-2_1_1_node_140 | 0.4 | n |  | TRUE
82 | bus_LV_901-2_1_1_node_143 | 0.4 | n |  | TRUE
83 | bus_LV_901-2_1_1_node_145 | 0.4 | n |  | TRUE
84 | bus_LV_901-2_1_1_node_146 | 0.4 | n |  | TRUE
85 | bus_LV_901-2_1_1_node_169 | 0.4 | n |  | TRUE
86 | bus_LV_901-2_1_1_node_152 | 0.4 | n |  | TRUE
87 | bus_LV_901-2_1_1_node_170 | 0.4 | n |  | TRUE
88 | bus_LV_901-2_1_1_node_167 | 0.4 | n |  | TRUE
89 | bus_LV_901-2_1_1_node_188 | 0.4 | n |  | TRUE
90 | bus_LV_901-2_1_1_node_171 | 0.4 | n |  | TRUE
91 | bus_LV_901-2_1_1_node_172 | 0.4 | n |  | TRUE
92 | bus_LV_901-2_1_1_node_173 | 0.4 | n |  | TRUE
93 | bus_LV_901-2_1_1_node_174 | 0.4 | n |  | TRUE
94 | bus_LV_901-2_1_1_node_175 | 0.4 | n |  | TRUE
95 | bus_LV_901-2_1_1_node_176 | 0.4 | n |  | TRUE
96 | bus_LV_901-2_1_1_node_183 | 0.4 | n |  | TRUE
97 | bus_LV_901-2_1_1_node_184 | 0.4 | n |  | TRUE
98 | bus_LV_901-2_1_1_node_185 | 0.4 | n |  | TRUE
99 | bus_LV_901-2_1_1_node_187 | 0.4 | n |  | TRUE
100 | bus_LV_901-2_1_1_node_231 | 0.4 | n |  | TRUE
101 | bus_LV_901-2_1_1_node_130 | 0.4 | n |  | TRUE
102 | bus_LV_901-2_1_1_node_132 | 0.4 | n |  | TRUE
103 | bus_LV_901-2_1_1_node_211 | 0.4 | n |  | TRUE
104 | bus_LV_901-2_1_1_node_212 | 0.4 | n |  | TRUE
105 | bus_LV_901-2_1_1_node_153 | 0.4 | n |  | TRUE
106 | bus_LV_901-2_1_1_node_160 | 0.4 | n |  | TRUE
107 | bus_LV_901-2_1_1_node_163 | 0.4 | n |  | TRUE
108 | bus_LV_901-2_1_1_node_158 | 0.4 | n |  | TRUE
109 | bus_LV_901-2_1_1_node_162 | 0.4 | n |  | TRUE
110 | bus_LV_901-2_1_1_node_154 | 0.4 | n |  | TRUE
111 | bus_LV_901-2_1_1_node_155 | 0.4 | n |  | TRUE
112 | bus_LV_901-2_1_1_node_209 | 0.4 | n |  | TRUE
113 | bus_LV_901-2_1_1_node_156 | 0.4 | n |  | TRUE
114 | bus_LV_901-2_1_1_node_229 | 0.4 | n |  | TRUE
115 | bus_LV_901-2_1_1_node_168 | 0.4 | n |  | TRUE
116 | bus_LV_901-2_1_1_node_193 | 0.4 | n |  | TRUE
117 | bus_LV_901-2_1_1_node_157 | 0.4 | n |  | TRUE
118 | bus_LV_901-2_1_1_node_159 | 0.4 | n |  | TRUE
119 | bus_LV_901-2_1_1_node_161 | 0.4 | n |  | TRUE
120 | bus_LV_901-2_1_1_node_165 | 0.4 | n |  | TRUE
121 | bus_LV_901-2_1_1_node_206 | 0.4 | n |  | TRUE
122 | bus_LV_901-2_1_1_node_203 | 0.4 | n |  | TRUE
123 | bus_LV_901-2_1_1_node_178 | 0.4 | n |  | TRUE
124 | bus_LV_901-2_1_1_node_190 | 0.4 | n |  | TRUE
125 | bus_LV_901-2_1_1_node_225 | 0.4 | n |  | TRUE
126 | bus_LV_901-2_1_1_node_216 | 0.4 | n |  | TRUE
127 | bus_LV_901-2_1_1_node_215 | 0.4 | n |  | TRUE
128 | bus_LV_901-2_1_1_node_201 | 0.4 | n |  | TRUE
129 | bus_LV_901-2_1_1_node_205 | 0.4 | n |  | TRUE
130 | bus_MV_0_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_901-2_1_1_load_219 | 0 | 0.00092379 | 0.00023152 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_901-2_1_1_load_191 | 2 | 0.00067867 | 0.00017009 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_901-2_1_1_load_86 | 4 | 8.2437e-05 | 2.0661e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_901-2_1_1_load_87 | 5 | 0.00017201 | 4.3111e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_901-2_1_1_load_89 | 7 | 0.00014572 | 3.6522e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_901-2_1_1_load_90 | 8 | 0.00014907 | 3.7361e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_901-2_1_1_load_230 | 9 | 0.00023639 | 5.9245e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_901-2_1_1_load_150 | 11 | 0.00026407 | 6.6183e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_901-2_1_1_load_91 | 12 | 6.1386e-05 | 1.5385e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_901-2_1_1_load_233 | 14 | 7.5537e-05 | 1.8931e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_901-2_1_1_load_92 | 15 | 0.00030277 | 7.5881e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_901-2_1_1_load_180 | 17 | 0.00016472 | 4.1282e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_901-2_1_1_load_96 | 22 | 8.628e-05 | 2.1624e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_901-2_1_1_load_199 | 24 | 0.00010752 | 2.6946e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_901-2_1_1_load_99 | 25 | 7.0222e-05 | 1.7599e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_901-2_1_1_load_189 | 27 | 0.00013449 | 3.3706e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_901-2_1_1_load_200 | 29 | 0.00037448 | 9.3853e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_901-2_1_1_load_98 | 30 | 8.5849e-05 | 2.1516e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_901-2_1_1_load_100 | 31 | 0.00023096 | 5.7885e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_901-2_1_1_load_102 | 32 | 0.00077488 | 0.0001942 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_901-2_1_1_load_103 | 33 | 0.0002126 | 5.3283e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_901-2_1_1_load_105 | 35 | 0.00044326 | 0.00011109 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_901-2_1_1_load_106 | 36 | 0.00034488 | 8.6435e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_901-2_1_1_load_121 | 37 | 0.00038528 | 9.6561e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_901-2_1_1_load_122 | 38 | 0.0002858 | 7.1628e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_901-2_1_1_load_107 | 39 | 0.00012054 | 3.0211e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_901-2_1_1_load_149 | 44 | 0.00045597 | 0.00011428 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_901-2_1_1_load_113 | 47 | 0.00027593 | 6.9155e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_901-2_1_1_load_129 | 48 | 0.00046602 | 0.0001168 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_901-2_1_1_load_127 | 49 | 0.00023459 | 5.8793e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_901-2_1_1_load_125 | 50 | 0.00053633 | 0.00013442 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_901-2_1_1_load_114 | 51 | 0.00031858 | 7.9844e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_901-2_1_1_load_128 | 52 | 0.00012248 | 3.0697e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_901-2_1_1_load_134 | 53 | 0.00016644 | 4.1714e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_901-2_1_1_load_133 | 55 | 0.00031374 | 7.8632e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_901-2_1_1_load_115 | 57 | 0.00066905 | 0.00016768 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_901-2_1_1_load_126 | 58 | 0.00047056 | 0.00011793 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_901-2_1_1_load_142 | 59 | 0.00020639 | 5.1726e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_901-2_1_1_load_144 | 60 | 0.00024046 | 6.0265e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_901-2_1_1_load_117 | 62 | 0.0002203 | 5.5212e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_901-2_1_1_load_213 | 67 | 0.00061688 | 0.00015461 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_901-2_1_1_load_166 | 68 | 0.00015313 | 3.8377e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_901-2_1_1_load_164 | 69 | 7.8641e-05 | 1.9709e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_901-2_1_1_load_228 | 70 | 0.00012559 | 3.1475e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_901-2_1_1_load_214 | 72 | 0.0001067 | 2.6741e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_901-2_1_1_load_123 | 73 | 0.00078786 | 0.00019746 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_901-2_1_1_load_204 | 74 | 8.2526e-05 | 2.0683e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_901-2_1_1_load_202 | 75 | 0.0003139 | 7.8671e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_901-2_1_1_load_135 | 76 | 0.00021601 | 5.4136e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_901-2_1_1_load_141 | 79 | 0.00026447 | 6.6283e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_901-2_1_1_load_139 | 80 | 0.00037685 | 9.4446e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_901-2_1_1_load_143 | 82 | 0.00055413 | 0.00013888 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_901-2_1_1_load_145 | 83 | 0.00019243 | 4.8228e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_901-2_1_1_load_170 | 87 | 9.7329e-05 | 2.4393e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_901-2_1_1_load_167 | 88 | 0.00077791 | 0.00019496 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_901-2_1_1_load_171 | 90 | 0.00017714 | 4.4396e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_901-2_1_1_load_172 | 91 | 0.00046675 | 0.00011698 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_901-2_1_1_load_173 | 92 | 0.00023954 | 6.0033e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_901-2_1_1_load_175 | 94 | 0.00011275 | 2.8257e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_901-2_1_1_load_183 | 96 | 0.00026682 | 6.6871e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_901-2_1_1_load_184 | 97 | 5.3597e-05 | 1.3433e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_901-2_1_1_load_187 | 99 | 5.3888e-05 | 1.3505e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_901-2_1_1_load_231 | 100 | 0.00042837 | 0.00010736 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_901-2_1_1_load_130 | 101 | 0.001364 | 0.00034186 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_901-2_1_1_load_211 | 103 | 0.00013838 | 3.4683e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_901-2_1_1_load_212 | 104 | 0.00015311 | 3.8373e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_901-2_1_1_load_160 | 106 | 0.00012727 | 3.1897e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_901-2_1_1_load_163 | 107 | 0.00012848 | 3.2201e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_901-2_1_1_load_158 | 108 | 0.00023854 | 5.9783e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_901-2_1_1_load_162 | 109 | 6.6528e-05 | 1.6673e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_901-2_1_1_load_154 | 110 | 8.1115e-05 | 2.0329e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_901-2_1_1_load_156 | 113 | 8.7672e-05 | 2.1973e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_901-2_1_1_load_229 | 114 | 0.00037947 | 9.5104e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_901-2_1_1_load_168 | 115 | 0.00016675 | 4.1791e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_901-2_1_1_load_157 | 117 | 0.00012458 | 3.1222e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_901-2_1_1_load_159 | 118 | 0.00014682 | 3.6798e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_901-2_1_1_load_165 | 120 | 0.00010855 | 2.7206e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_901-2_1_1_load_206 | 121 | 7.4366e-05 | 1.8638e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_901-2_1_1_load_178 | 123 | 0.00089575 | 0.0002245 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_901-2_1_1_load_190 | 124 | 5.1931e-05 | 1.3015e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_901-2_1_1_load_225 | 125 | 0.00020448 | 5.1248e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_901-2_1_1_load_215 | 127 | 0.00013862 | 3.4741e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_901-2_1_1_load_201 | 128 | 9.0706e-05 | 2.2733e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_901-2_1_1_load_205 | 129 | 5.8933e-05 | 1.477e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_901-2_1_1_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_901-2_1_1_line_1 | NAYY 4x150 SE | 1 | 126 | 0.3026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_901-2_1_1_line_2 | NAYY 4x150 SE | 1 | 3 | 0.14728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_901-2_1_1_line_3 | NAYY 4x150 SE | 2 | 3 | 0.024412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_901-2_1_1_line_4 | NAYY 4x150 SE | 3 | 116 | 0.15193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_901-2_1_1_line_5 | NAYY 4x150 SE | 4 | 5 | 0.041295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_901-2_1_1_line_6 | NAYY 4x150 SE | 4 | 6 | 0.08202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_901-2_1_1_line_7 | NAYY 4x150 SE | 5 | 7 | 0.0025982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_901-2_1_1_line_8 | NAYY 4x150 SE | 6 | 8 | 0.05243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_901-2_1_1_line_9 | NAYY 4x150 SE | 7 | 12 | 0.015027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_901-2_1_1_line_10 | NAYY 4x150 SE | 8 | 13 | 0.2248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_901-2_1_1_line_11 | NAYY 4x150 SE | 8 | 14 | 0.081873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_901-2_1_1_line_12 | NAYY 4x150 SE | 9 | 10 | 0.19251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_901-2_1_1_line_13 | NAYY 4x150 SE | 9 | 11 | 0.21341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_901-2_1_1_line_14 | NAYY 4x150 SE | 10 | 25 | 0.0111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_901-2_1_1_line_15 | NAYY 4x150 SE | 11 | 26 | 0.042502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_901-2_1_1_line_16 | NAYY 4x150 SE | 11 | 20 | 0.21468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_901-2_1_1_line_17 | NAYY 4x150 SE | 12 | 15 | 0.0035894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_901-2_1_1_line_18 | NAYY 4x150 SE | 13 | 16 | 0.017231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_901-2_1_1_line_19 | NAYY 4x150 SE | 15 | 18 | 0.02453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_901-2_1_1_line_20 | NAYY 4x150 SE | 16 | 17 | 0.1742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_901-2_1_1_line_21 | NAYY 4x150 SE | 17 | 125 | 0.13369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_901-2_1_1_line_22 | NAYY 4x150 SE | 18 | 19 | 0.064377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_901-2_1_1_line_23 | NAYY 4x150 SE | 18 | 20 | 0.009318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_901-2_1_1_line_24 | NAYY 4x150 SE | 19 | 21 | 0.088162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_901-2_1_1_line_25 | NAYY 4x150 SE | 19 | 22 | 0.046346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_901-2_1_1_line_26 | NAYY 4x150 SE | 21 | 23 | 0.034184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_901-2_1_1_line_27 | NAYY 4x150 SE | 21 | 24 | 0.058364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_901-2_1_1_line_28 | NAYY 4x150 SE | 23 | 27 | 0.14095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_901-2_1_1_line_29 | NAYY 4x150 SE | 23 | 28 | 0.13795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_901-2_1_1_line_30 | NAYY 4x150 SE | 24 | 29 | 0.029183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_901-2_1_1_line_31 | NAYY 4x150 SE | 25 | 30 | 0.11699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_901-2_1_1_line_32 | NAYY 4x150 SE | 26 | 105 | 0.095002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_901-2_1_1_line_33 | NAYY 4x150 SE | 26 | 86 | 0.34379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_901-2_1_1_line_34 | NAYY 4x150 SE | 27 | 124 | 0.00015027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_901-2_1_1_line_35 | NAYY 4x150 SE | 28 | 123 | 0.033717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_901-2_1_1_line_36 | NAYY 4x150 SE | 28 | 93 | 0.056546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_901-2_1_1_line_37 | NAYY 4x150 SE | 30 | 31 | 0.0063261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_901-2_1_1_line_38 | NAYY 4x150 SE | 32 | 33 | 0.026698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_901-2_1_1_line_39 | NAYY 4x150 SE | 32 | 34 | 0.018601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_901-2_1_1_line_40 | NAYY 4x150 SE | 33 | 35 | 0.023527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_901-2_1_1_line_41 | NAYY 4x150 SE | 34 | 36 | 0.03313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_901-2_1_1_line_42 | NAYY 4x150 SE | 36 | 37 | 0.024081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_901-2_1_1_line_43 | NAYY 4x150 SE | 37 | 38 | 0.027891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_901-2_1_1_line_44 | NAYY 4x150 SE | 38 | 73 | 0.028923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_901-2_1_1_line_45 | NAYY 4x150 SE | 39 | 40 | 0.19902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_901-2_1_1_line_46 | NAYY 4x150 SE | 39 | 41 | 0.16722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_901-2_1_1_line_47 | NAYY 4x150 SE | 40 | 42 | 0.050978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_901-2_1_1_line_48 | NAYY 4x150 SE | 40 | 43 | 0.25685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_901-2_1_1_line_49 | NAYY 4x150 SE | 41 | 44 | 0.048925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_901-2_1_1_line_50 | NAYY 4x150 SE | 41 | 45 | 0.3416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_901-2_1_1_line_51 | NAYY 4x150 SE | 42 | 46 | 0.17272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_901-2_1_1_line_52 | NAYY 4x150 SE | 42 | 47 | 0.054612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_901-2_1_1_line_53 | NAYY 4x150 SE | 43 | 48 | 0.066733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_901-2_1_1_line_54 | NAYY 4x150 SE | 43 | 49 | 0.1652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_901-2_1_1_line_55 | NAYY 4x150 SE | 45 | 58 | 0.13813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_901-2_1_1_line_56 | NAYY 4x150 SE | 45 | 82 | 0.044332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_901-2_1_1_line_57 | NAYY 4x150 SE | 45 | 84 | 0.064482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_901-2_1_1_line_58 | NAYY 4x150 SE | 46 | 50 | 0.05353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_901-2_1_1_line_59 | NAYY 4x150 SE | 47 | 51 | 0.027792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_901-2_1_1_line_60 | NAYY 4x150 SE | 49 | 52 | 0.10834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_901-2_1_1_line_61 | NAYY 4x150 SE | 50 | 61 | 0.040172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_901-2_1_1_line_62 | NAYY 4x150 SE | 51 | 57 | 0.0074605 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_901-2_1_1_line_63 | NAYY 4x150 SE | 53 | 54 | 0.019395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_901-2_1_1_line_64 | NAYY 4x150 SE | 54 | 104 | 0.019935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_901-2_1_1_line_65 | NAYY 4x150 SE | 54 | 103 | 0.0047136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_901-2_1_1_line_66 | NAYY 4x150 SE | 55 | 56 | 0.036906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_901-2_1_1_line_67 | NAYY 4x150 SE | 56 | 102 | 0.13059 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_901-2_1_1_line_68 | NAYY 4x150 SE | 56 | 101 | 0.0027349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_901-2_1_1_line_69 | NAYY 4x150 SE | 58 | 59 | 0.24173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_901-2_1_1_line_70 | NAYY 4x150 SE | 58 | 60 | 0.21054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_901-2_1_1_line_71 | NAYY 4x150 SE | 59 | 81 | 0.029353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_901-2_1_1_line_72 | NAYY 4x150 SE | 60 | 83 | 0.10939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_901-2_1_1_line_73 | NAYY 4x150 SE | 61 | 73 | 0.014849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_901-2_1_1_line_74 | NAYY 4x150 SE | 61 | 65 | 0.18817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_901-2_1_1_line_75 | NAYY 4x150 SE | 62 | 63 | 0.060566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_901-2_1_1_line_76 | NAYY 4x150 SE | 63 | 64 | 0.16989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_901-2_1_1_line_77 | NAYY 4x150 SE | 63 | 65 | 0.002755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_901-2_1_1_line_78 | NAYY 4x150 SE | 64 | 66 | 0.040872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_901-2_1_1_line_79 | NAYY 4x150 SE | 64 | 67 | 0.31672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_901-2_1_1_line_80 | NAYY 4x150 SE | 66 | 70 | 0.10883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_901-2_1_1_line_81 | NAYY 4x150 SE | 66 | 71 | 0.14743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_901-2_1_1_line_82 | NAYY 4x150 SE | 67 | 72 | 0.0054935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_901-2_1_1_line_83 | NAYY 4x150 SE | 68 | 69 | 0.056928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_901-2_1_1_line_84 | NAYY 4x150 SE | 69 | 120 | 0.015457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_901-2_1_1_line_85 | NAYY 4x150 SE | 71 | 129 | 0.06177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_901-2_1_1_line_86 | NAYY 4x150 SE | 72 | 104 | 0.010778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_901-2_1_1_line_87 | NAYY 4x150 SE | 74 | 75 | 0.028574 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_901-2_1_1_line_88 | NAYY 4x150 SE | 75 | 128 | 0.0030927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_901-2_1_1_line_89 | NAYY 4x150 SE | 76 | 77 | 0.0049179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_901-2_1_1_line_90 | NAYY 4x150 SE | 77 | 78 | 0.016322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_901-2_1_1_line_91 | NAYY 4x150 SE | 78 | 79 | 0.014415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_901-2_1_1_line_92 | NAYY 4x150 SE | 78 | 80 | 0.015495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_901-2_1_1_line_93 | NAYY 4x150 SE | 80 | 81 | 0.070168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_901-2_1_1_line_94 | NAYY 4x150 SE | 84 | 85 | 0.067632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_901-2_1_1_line_95 | NAYY 4x150 SE | 85 | 89 | 0.2781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_901-2_1_1_line_96 | NAYY 4x150 SE | 85 | 88 | 0.017985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_901-2_1_1_line_97 | NAYY 4x150 SE | 86 | 87 | 0.0090969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_901-2_1_1_line_98 | NAYY 4x150 SE | 87 | 90 | 0.015163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_901-2_1_1_line_99 | NAYY 4x150 SE | 89 | 100 | 0.042477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_901-2_1_1_line_100 | NAYY 4x150 SE | 91 | 92 | 0.017695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_901-2_1_1_line_101 | NAYY 4x150 SE | 91 | 93 | 0.034794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_901-2_1_1_line_102 | NAYY 4x150 SE | 92 | 94 | 0.13685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_901-2_1_1_line_103 | NAYY 4x150 SE | 93 | 95 | 0.17566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_901-2_1_1_line_104 | NAYY 4x150 SE | 95 | 96 | 0.22335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_901-2_1_1_line_105 | NAYY 4x150 SE | 96 | 97 | 0.011966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_901-2_1_1_line_106 | NAYY 4x150 SE | 97 | 98 | 0.35317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_901-2_1_1_line_107 | NAYY 4x150 SE | 98 | 99 | 0.023813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_901-2_1_1_line_108 | NAYY 4x150 SE | 102 | 103 | 0.31492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_901-2_1_1_line_109 | NAYY 4x150 SE | 105 | 106 | 0.014384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_901-2_1_1_line_110 | NAYY 4x150 SE | 105 | 107 | 0.010004 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_901-2_1_1_line_111 | NAYY 4x150 SE | 106 | 108 | 0.0086409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_901-2_1_1_line_112 | NAYY 4x150 SE | 107 | 109 | 0.0084327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_901-2_1_1_line_113 | NAYY 4x150 SE | 108 | 117 | 0.0091696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_901-2_1_1_line_114 | NAYY 4x150 SE | 109 | 113 | 0.0031208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_901-2_1_1_line_115 | NAYY 4x150 SE | 110 | 111 | 0.11837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_901-2_1_1_line_116 | NAYY 4x150 SE | 110 | 112 | 0.15199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_901-2_1_1_line_117 | NAYY 4x150 SE | 111 | 113 | 0.079375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_901-2_1_1_line_118 | NAYY 4x150 SE | 112 | 114 | 0.061446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_901-2_1_1_line_119 | NAYY 4x150 SE | 112 | 115 | 0.19589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_901-2_1_1_line_120 | NAYY 4x150 SE | 112 | 116 | 0.27349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_901-2_1_1_line_121 | NAYY 4x150 SE | 117 | 118 | 0.0062491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_901-2_1_1_line_122 | NAYY 4x150 SE | 118 | 119 | 0.22116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_901-2_1_1_line_123 | NAYY 4x150 SE | 119 | 120 | 0.016347 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_901-2_1_1_line_124 | NAYY 4x150 SE | 119 | 121 | 0.2856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_901-2_1_1_line_125 | NAYY 4x150 SE | 121 | 122 | 0.024526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_901-2_1_1_line_126 | NAYY 4x150 SE | 122 | 129 | 0.0097338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_901-2_1_1_line_127 | NAYY 4x150 SE | 122 | 128 | 0.026812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_901-2_1_1_line_128 | NAYY 4x150 SE | 126 | 127 | 0.18075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_901-2_1_1_trafo_166 | 0.25 MVA 20/0.4 kV | 130 | 68 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29
0 | 2628393.5499 | 1190908.489 | 2628376.274 | 1190928.9345
1 | 2628393.5499 | 1190908.489 | 2628440.846 | 1190863.0555 | 2628456.9567 | 1190848.5353 | 2628468.7821 | 1190838.9419 | 2628477.508 | 1190833.3692 | 2628499.1348 | 1190819.7536 | 2628566.9324 | 1190776.4086 | 2628586.1271 | 1190746.851 | 2628591.2341 | 1190739.1712 | 2628601.1227 | 1190720.0971 | 2628607.9868 | 1190703.71
2 | 2628393.5499 | 1190908.489 | 2628382.948 | 1190898.0666 | 2628371.0968 | 1190887.427 | 2628365.8614 | 1190883.6669 | 2628363.1369 | 1190882.5868 | 2628359.8911 | 1190882.1267 | 2628352.9492 | 1190882.9165 | 2628330.37 | 1190888.4683 | 2628319.9418 | 1190892.877 | 2628308.1037 | 1190898.7909 | 2628302.2891 | 1190903.0435 | 2628295.1912 | 1190909.4357 | 2628288.2981 | 1190916.0289 | 2628283.4706 | 1190921.1422 | 2628280.1746 | 1190923.25 | 2628276.5704 | 1190924.4225 | 2628272.5204 | 1190924.7258 | 2628268.6976 | 1190923.7406
3 | 2628268.6976 | 1190923.7406 | 2628259.6843 | 1190946.4282
4 | 2628238.1973 | 1190788.4468 | 2628242.6956 | 1190799.8185 | 2628246.7814 | 1190808.0977 | 2628252.3082 | 1190816.3949 | 2628266.2504 | 1190834.8037 | 2628270.1988 | 1190841.4926 | 2628271.6039 | 1190847.4802 | 2628271.9618 | 1190854.0409 | 2628271.5369 | 1190860.0644 | 2628270.0582 | 1190868.0728 | 2628258.414 | 1190899.1567 | 2628257.2289 | 1190904.6986 | 2628257.1637 | 1190908.8338 | 2628258.1815 | 1190912.8741 | 2628259.4102 | 1190915.8704 | 2628262.2445 | 1190919.519 | 2628265.2061 | 1190922.0454 | 2628268.6976 | 1190923.7406
5 | 2627785.7597 | 1190345.2481 | 2627785.8657 | 1190345.9644 | 2627786.6959 | 1190349.459 | 2627787.7075 | 1190351.6649 | 2627789.1243 | 1190353.6169 | 2627791.0765 | 1190355.2157 | 2627793.5424 | 1190356.2166 | 2627797.2066 | 1190356.9673 | 2627801.2172 | 1190357.0081 | 2627808.0277 | 1190356.7062 | 2627820.4145 | 1190356.5493
6 | 2627721.9482 | 1190310.5942 | 2627729.5112 | 1190310.8404 | 2627746.3139 | 1190313.1416 | 2627757.4608 | 1190315.0164 | 2627763.8061 | 1190316.3909 | 2627767.9254 | 1190317.6663 | 2627771.5406 | 1190319.1171 | 2627774.7119 | 1190320.9216 | 2627777.1667 | 1190322.6784 | 2627779.4894 | 1190324.9681 | 2627781.1187 | 1190327.1324 | 2627782.3966 | 1190329.4618 | 2627783.4739 | 1190332.2794 | 2627784.2746 | 1190335.5515 | 2627784.8085 | 1190338.8224 | 2627785.7597 | 1190345.2481
7 | 2627820.4145 | 1190356.5493 | 2627822.1578 | 1190356.5272 | 2627823.012 | 1190356.5596
8 | 2627684.276 | 1190275.1569 | 2627691.8612 | 1190287.1205 | 2627701.767 | 1190296.8492 | 2627712.4353 | 1190304.9472 | 2627721.9482 | 1190310.5942
9 | 2627838.0094 | 1190357.4406 | 2627831.1843 | 1190356.8693 | 2627823.012 | 1190356.5596
10 | 2627684.276 | 1190275.1569 | 2627534.3264 | 1190107.6773
11 | 2627684.276 | 1190275.1569 | 2627714.2445 | 1190198.9658
12 | 2628107.0728 | 1190612.459 | 2627914.6059 | 1190616.4288
13 | 2628107.0728 | 1190612.459 | 2628062.157 | 1190403.8281
14 | 2627914.6059 | 1190616.4288 | 2627903.6932 | 1190618.4603
15 | 2628073.3204 | 1190364.5242 | 2628072.7453 | 1190371.7254 | 2628071.5175 | 1190388.0394 | 2628070.3742 | 1190392.8366 | 2628068.7932 | 1190396.6535 | 2628065.2176 | 1190401.4282 | 2628062.157 | 1190403.8281
16 | 2627871.4966 | 1190365.3721 | 2627874.6183 | 1190363.0743 | 2627879.1435 | 1190360.6719 | 2627885.0107 | 1190358.2645 | 2627890.353 | 1190357.2444 | 2627895.5717 | 1190356.5683 | 2627901.2378 | 1190356.4168 | 2627907.2981 | 1190356.7674 | 2627935.5496 | 1190359.9117 | 2627947.61 | 1190360.4349 | 2627966.0686 | 1190360.7989 | 2627971.6251 | 1190361.2473 | 2627976.5918 | 1190362.2821 | 2627980.8464 | 1190363.9584 | 2627986.5742 | 1190366.9311 | 2627990.8386 | 1190369.7748 | 2627994.7558 | 1190373.4839 | 2627998.7383 | 1190377.8938 | 2628018.9447 | 1190402.3568 | 2628024.4427 | 1190407.1739 | 2628029.6448 | 1190410.022 | 2628035.5078 | 1190411.7836 | 2628041.0565 | 1190412.2765 | 2628047.0761 | 1190411.5376 | 2628052.9798 | 1190409.4863 | 2628058.9038 | 1190406.3791 | 2628062.157 | 1190403.8281
17 | 2627838.0094 | 1190357.4406 | 2627840.6052 | 1190357.6579 | 2627841.5896 | 1190357.6753
18 | 2627534.0539 | 1190090.6337 | 2627535.0891 | 1190097.6755 | 2627535.3403 | 1190101.1007 | 2627535.2863 | 1190102.8903 | 2627534.9956 | 1190104.7566 | 2627534.3264 | 1190107.6773
19 | 2627866.1182 | 1190357.7542 | 2627854.3526 | 1190357.7773 | 2627847.4291 | 1190357.7785 | 2627841.5896 | 1190357.6753
20 | 2627534.0539 | 1190090.6337 | 2627541.6875 | 1190088.8455 | 2627546.3811 | 1190087.9889 | 2627550.2565 | 1190087.6176 | 2627555.2754 | 1190087.3071 | 2627559.4462 | 1190087.3708 | 2627564.6684 | 1190087.6505 | 2627573.1429 | 1190088.7233 | 2627584.185 | 1190090.2527 | 2627594.7715 | 1190091.3909 | 2627603.4699 | 1190091.8645 | 2627616.2255 | 1190092.2346 | 2627633.6948 | 1190092.3262 | 2627641.1024 | 1190091.6155 | 2627647.6346 | 1190090.5562 | 2627653.5594 | 1190088.9382 | 2627658.8289 | 1190087.1949 | 2627665.3455 | 1190084.568 | 2627686.1723 | 1190074.2808 | 2627702.0968 | 1190065.9366
21 | 2627796.4941 | 1189971.2696 | 2627702.0968 | 1190065.9366
22 | 2627866.1182 | 1190357.7542 | 2627865.3156 | 1190354.8934 | 2627864.3356 | 1190345.9174 | 2627864.4635 | 1190338.0805 | 2627864.8408 | 1190334.0245 | 2627865.5568 | 1190330.8928 | 2627866.5836 | 1190328.1739 | 2627867.7218 | 1190326.0892 | 2627868.9338 | 1190324.5385 | 2627872.0307 | 1190321.0177 | 2627875.5092 | 1190317.4319 | 2627882.2192 | 1190310.8929 | 2627883.9361 | 1190308.9888 | 2627885.2948 | 1190307.0385 | 2627886.3791 | 1190305.0647 | 2627887.1889 | 1190303.1119 | 2627887.6386 | 1190301.502
23 | 2627866.1182 | 1190357.7542 | 2627871.4966 | 1190365.3721
24 | 2627876.2408 | 1190222.4291 | 2627874.068 | 1190223.9865 | 2627871.7852 | 1190226.2327 | 2627870.1889 | 1190228.4486 | 2627867.918 | 1190233.0517 | 2627866.3846 | 1190238.1361 | 2627865.4132 | 1190243.6901 | 2627865.0591 | 1190247.7017 | 2627865.3684 | 1190251.7053 | 2627866.1881 | 1190255.8002 | 2627867.9495 | 1190260.711 | 2627870.8954 | 1190266.7279 | 2627874.7755 | 1190273.5162 | 2627882.4195 | 1190284.2241 | 2627884.8854 | 1190288.5045 | 2627886.5367 | 1190292.5032 | 2627887.4279 | 1190295.9759 | 2627887.728 | 1190298.6676 | 2627887.6386 | 1190301.502
25 | 2627887.6386 | 1190301.502 | 2627897.9292 | 1190303.8511 | 2627910.1365 | 1190307.2542 | 2627912.7576 | 1190307.6555 | 2627914.7633 | 1190307.6093 | 2627916.3278 | 1190307.3053 | 2627918.002 | 1190306.3904 | 2627919.2281 | 1190305.0731 | 2627919.9608 | 1190303.3089 | 2627920.1083 | 1190301.0973 | 2627919.3511 | 1190296.6804 | 2627918.8543 | 1190292.1565
26 | 2627876.2408 | 1190222.4291 | 2627880.3472 | 1190221.5589 | 2627886.0996 | 1190220.9297 | 2627895.6417 | 1190220.296 | 2627900.3653 | 1190219.5175 | 2627903.581 | 1190218.3541 | 2627906.0115 | 1190217.1314 | 2627908.9205 | 1190214.6881
27 | 2627876.2408 | 1190222.4291 | 2627873.7262 | 1190217.1368 | 2627870.9818 | 1190212.0658 | 2627861.4175 | 1190197.7915 | 2627844.1359 | 1190173.8137
28 | 2627908.9205 | 1190214.6881 | 2627910.7343 | 1190216.5309 | 2627912.5493 | 1190218.129 | 2627915.9562 | 1190220.1126 | 2627917.9571 | 1190221.0891 | 2627922.3493 | 1190222.6993 | 2627926.7441 | 1190223.7759 | 2627934.0284 | 1190224.9216 | 2627941.2158 | 1190225.6221 | 2627952.5005 | 1190225.7414 | 2627964.4953 | 1190225.6862 | 2627970.7602 | 1190226.3269 | 2627976.2909 | 1190227.4533 | 2627982.4053 | 1190229.305 | 2627998.4836 | 1190234.9164 | 2628007.5292 | 1190237.7268 | 2628021.3929 | 1190240.7598 | 2628027.2598 | 1190241.7211 | 2628032.4667 | 1190241.9678 | 2628037.0898 | 1190241.4891 | 2628044.6645 | 1190239.3537
29 | 2627936.7428 | 1190081.002 | 2627937.1894 | 1190088.2412 | 2627937.3497 | 1190098.0361 | 2627935.6675 | 1190107.1998 | 2627934.3943 | 1190116.9769 | 2627929.3858 | 1190139.5878 | 2627919.4734 | 1190190.2242 | 2627917.4918 | 1190198.197 | 2627915.3763 | 1190203.8123 | 2627914.0948 | 1190207.1971 | 2627911.6201 | 1190211.3544 | 2627908.9205 | 1190214.6881
30 | 2627828.8468 | 1190149.2144 | 2627832.3688 | 1190157.6019 | 2627834.2968 | 1190161.1461 | 2627837.0769 | 1190165.1167 | 2627843.128 | 1190172.4153 | 2627844.1359 | 1190173.8137
31 | 2627807.1556 | 1190602.2055 | 2627810.4509 | 1190615.0441 | 2627812.0056 | 1190620.1318 | 2627813.3951 | 1190623.0287 | 2627815.4102 | 1190625.8506 | 2627818.0056 | 1190628.4974 | 2627820.6964 | 1190630.2886 | 2627823.6869 | 1190631.581 | 2627827.3052 | 1190632.3204 | 2627831.8792 | 1190632.5084 | 2627838.1796 | 1190631.9929 | 2627857.5523 | 1190629.0813 | 2627876.0158 | 1190624.9316 | 2627900.7398 | 1190619.0101 | 2627903.6932 | 1190618.4603
32 | 2628137.6636 | 1190310.2969 | 2628122.73 | 1190311.0717 | 2628117.0153 | 1190311.8008 | 2628110.6262 | 1190313.2716 | 2628105.2638 | 1190315.3032 | 2628100.3803 | 1190317.6704 | 2628095.7219 | 1190320.8058 | 2628090.3185 | 1190325.0828 | 2628086.335 | 1190329.0218 | 2628082.4154 | 1190333.9616 | 2628079.6492 | 1190338.4844 | 2628077.4222 | 1190343.4655 | 2628075.8223 | 1190348.0605 | 2628074.4113 | 1190354.6574 | 2628073.3204 | 1190364.5242
33 | 2628073.3204 | 1190364.5242 | 2628069.4132 | 1190358.7028 | 2628067.8754 | 1190351.6585 | 2628068.2696 | 1190340.7546 | 2628069.6035 | 1190332.7121 | 2628071.9016 | 1190322.3173 | 2628077.4093 | 1190310.4145 | 2628088.3303 | 1190292.1226 | 2628099.2409 | 1190277.6993 | 2628117.5403 | 1190256.7851 | 2628130.101 | 1190238.4898 | 2628144.2098 | 1190220.1684 | 2628152.5815 | 1190212.2146 | 2628159.4347 | 1190206.1324 | 2628163.7719 | 1190201.5948 | 2628167.0416 | 1190197.0522 | 2628170.0136 | 1190189.3398 | 2628174.1649 | 1190175.6965 | 2628183.5956 | 1190140.3886 | 2628186.4185 | 1190127.1059 | 2628188.9618 | 1190114.8892 | 2628190.7661 | 1190102.5466 | 2628191.0554 | 1190094.5326 | 2628190.0466 | 1190072.3049 | 2628190.5619 | 1190058.3999
34 | 2628044.8091 | 1190239.3129 | 2628044.6645 | 1190239.3537
35 | 2627936.7428 | 1190081.002 | 2627942.3288 | 1190083.3737 | 2627947.4263 | 1190085.8432 | 2627967.0796 | 1190095.6944
36 | 2627926.9045 | 1190025.6822 | 2627926.5251 | 1190035.0855 | 2627927.9718 | 1190047.0208 | 2627935.1471 | 1190073.2459 | 2627936.7428 | 1190081.002
37 | 2627805.5828 | 1190596.0781 | 2627807.1556 | 1190602.2055
38 | 2628828.584 | 1189836.5019 | 2628828.8816 | 1189836.2605 | 2628851.8885 | 1189823.4865
39 | 2628814.1369 | 1189848.2183 | 2628828.584 | 1189836.5019
40 | 2628851.8885 | 1189823.4865 | 2628872.4573 | 1189812.0662
41 | 2628814.1369 | 1189848.2183 | 2628805.8842 | 1189854.9155 | 2628790.6052 | 1189871.4341
42 | 2628774.2538 | 1189889.1121 | 2628790.6052 | 1189871.4341
43 | 2628774.2538 | 1189889.1121 | 2628771.3435 | 1189892.2585 | 2628754.9216 | 1189909.215
44 | 2628754.9216 | 1189909.215 | 2628752.7822 | 1189911.4241 | 2628744.492 | 1189922.8016 | 2628738.3718 | 1189932.8559
45 | 2628775.186 | 1189724.0651 | 2628776.2516 | 1189710.185 | 2628778.6345 | 1189691.9645 | 2628781.9143 | 1189674.3597 | 2628783.3488 | 1189666.2512 | 2628789.0863 | 1189657.7186 | 2628792.326 | 1189648.4737 | 2628794.2742 | 1189638.222 | 2628801.5634 | 1189617.8462 | 2628808.6704 | 1189594.1232 | 2628807.8304 | 1189581.6792 | 2628801.9781 | 1189574.3806 | 2628789.9562 | 1189560.7711 | 2628782.0244 | 1189548.193 | 2628778.4166 | 1189540.1555
46 | 2628778.4166 | 1189540.1555 | 2628641.2617 | 1189444.4861
47 | 2628775.186 | 1189724.0651 | 2628766.7604 | 1189730.2057 | 2628758.618 | 1189740.9168 | 2628753.0637 | 1189754.1861 | 2628749.5287 | 1189761.4397 | 2628745.2264 | 1189763.309
48 | 2628775.186 | 1189724.0651 | 2628793.4082 | 1189715.2923 | 2628810.4232 | 1189708.6038 | 2628822.543 | 1189701.7917 | 2628834.3789 | 1189690.5982 | 2628847.4528 | 1189672.5292 | 2628861.2605 | 1189647.8047 | 2628874.0453 | 1189626.4549 | 2628881.3345 | 1189612.4825 | 2628886.0908 | 1189603.4562 | 2628889.8821 | 1189598.4829 | 2628894.6096 | 1189593.8699 | 2628902.6856 | 1189587.5388 | 2628915.2239 | 1189580.9957 | 2628939.9431 | 1189572.4548 | 2628949.7565 | 1189566.4212 | 2628953.6691 | 1189563.1606 | 2628953.2885 | 1189561.4467 | 2628952.2058 | 1189556.6723
49 | 2628641.2617 | 1189444.4861 | 2628638.6279 | 1189441.8499 | 2628635.9864 | 1189436.0565 | 2628629.2071 | 1189423.195 | 2628621.3648 | 1189414.1417 | 2628615.0366 | 1189403.5768
50 | 2628381.9594 | 1189643.1592 | 2628407.0741 | 1189645.8907 | 2628419.0835 | 1189646.2033 | 2628430.1709 | 1189644.7662 | 2628439.5253 | 1189642.1091 | 2628448.4718 | 1189638.6386 | 2628455.5738 | 1189634.9592 | 2628461.3743 | 1189630.7512 | 2628499.8516 | 1189594.5924 | 2628535.8729 | 1189553.8086 | 2628578.6657 | 1189505.2421 | 2628627.9856 | 1189458.5969 | 2628641.2617 | 1189444.4861
51 | 2628745.2264 | 1189763.309 | 2628743.6907 | 1189771.8617 | 2628738.1367 | 1189783.4857 | 2628727.7705 | 1189799.9671 | 2628707.5533 | 1189828.8968 | 2628691.3728 | 1189849.3302 | 2628676.0121 | 1189865.7878 | 2628656.1327 | 1189886.3593 | 2628651.2405 | 1189893.6064 | 2628649.3977 | 1189897.8332 | 2628649.068 | 1189901.4002 | 2628649.5601 | 1189903.7482
52 | 2628745.2264 | 1189763.309 | 2628743.3484 | 1189758.9643 | 2628742.787 | 1189751.9912 | 2628744.2254 | 1189743.0378 | 2628744.9543 | 1189737.3605 | 2628743.1751 | 1189733.0719 | 2628739.1912 | 1189730.5626 | 2628734.3908 | 1189731.34 | 2628728.5666 | 1189737.2819 | 2628725.0654 | 1189741.5961
53 | 2628890.0746 | 1189555.3831 | 2628912.6833 | 1189549.6112 | 2628929.9785 | 1189546.6152 | 2628941.0628 | 1189547.458 | 2628948.9354 | 1189551.6872 | 2628952.2058 | 1189556.6723
54 | 2628952.2058 | 1189556.6723 | 2628960.4749 | 1189537.2241 | 2628958.9039 | 1189521.4414 | 2628947.1145 | 1189503.9529 | 2628902.5457 | 1189442.572 | 2628897.316 | 1189432.6859 | 2628884.1087 | 1189435.5794 | 2628880.0566 | 1189430.4245
55 | 2628477.7828 | 1189742.6438 | 2628381.9594 | 1189643.1592
56 | 2628381.9594 | 1189643.1592 | 2628385.4436 | 1189636.9168 | 2628390.9769 | 1189629.5168 | 2628396.0536 | 1189617.1232 | 2628398.3666 | 1189606.9732 | 2628401.1876 | 1189603.9434
57 | 2628317.7352 | 1189637.9528 | 2628327.6157 | 1189636.9101 | 2628337.0929 | 1189637.3106 | 2628381.9594 | 1189643.1592
58 | 2628649.5601 | 1189903.7482 | 2628650.6998 | 1189906.2106 | 2628653.5672 | 1189909.3815 | 2628657.6641 | 1189912.1581 | 2628672.4413 | 1189920.3998 | 2628690.4936 | 1189927.8457 | 2628695.0322 | 1189930.2676
59 | 2628725.0654 | 1189741.5961 | 2628721.233 | 1189746.3183 | 2628715.1244 | 1189749.5685 | 2628708.0377 | 1189748.4451 | 2628701.7671 | 1189744.1239
60 | 2628880.0566 | 1189430.4245 | 2628854.2669 | 1189397.6155 | 2628854.9573 | 1189392.027 | 2628860.5893 | 1189386.4734 | 2628902.6443 | 1189354.1142
61 | 2628731.7977 | 1189946.1643 | 2628723.7643 | 1189943.7468 | 2628709.6232 | 1189938.0538 | 2628695.0322 | 1189930.2676
62 | 2628705.9908 | 1189737.9742 | 2628701.7671 | 1189744.1239
63 | 2628881.472 | 1190242.2524 | 2628878.8756 | 1190235.1472 | 2628875.9515 | 1190229.5635 | 2628873.67 | 1190226.7287 | 2628872.2391 | 1190225.4961
64 | 2628881.472 | 1190242.2524 | 2628875.2604 | 1190247.9811 | 2628868.4735 | 1190252.8288 | 2628865.6409 | 1190254.1953
65 | 2628881.472 | 1190242.2524 | 2628886.1848 | 1190242.1639
66 | 2629005.6726 | 1189985.2258 | 2628990.9305 | 1189999.8068 | 2628985.2287 | 1190004.1037 | 2628980.4711 | 1190005.5259 | 2628976.4062 | 1190005.6285
67 | 2629005.6726 | 1189985.2258 | 2629010.7826 | 1189991.3538 | 2629012.5242 | 1189995.4533 | 2629013.7985 | 1190001.5961 | 2629015.9038 | 1190010.9112 | 2629019.1791 | 1190019.5317 | 2629026.7834 | 1190031.7861 | 2629032.1221 | 1190039.4716 | 2629034.3095 | 1190041.2943 | 2629037.7224 | 1190041.9779 | 2629041.027 | 1190041.3936 | 2629060.2175 | 1190034.1271 | 2629069.9906 | 1190031.5509 | 2629087.4118 | 1190029.0229 | 2629097.9361 | 1190024.0935
68 | 2629005.6726 | 1189985.2258 | 2629007.5481 | 1189983.2353
69 | 2628477.7828 | 1189742.6438 | 2628409.154 | 1189510.8589
70 | 2628477.7828 | 1189742.6438 | 2628339.6423 | 1189901.5242
71 | 2628415.5946 | 1189489.3588 | 2628417.9952 | 1189494.5285 | 2628419.8962 | 1189503.7424 | 2628417.2781 | 1189509.055 | 2628409.154 | 1189510.8589
72 | 2628265.006 | 1189852.6151 | 2628263.7266 | 1189866.2752 | 2628263.8447 | 1189868.7215 | 2628265.2327 | 1189875.1537 | 2628271.5367 | 1189878.9188 | 2628303.8775 | 1189883.6961 | 2628326.4718 | 1189887.0268 | 2628337.4285 | 1189890.5471 | 2628340.6371 | 1189894.1642 | 2628339.6423 | 1189901.5242
73 | 2628731.7977 | 1189946.1643 | 2628737.6974 | 1189933.9638 | 2628738.3718 | 1189932.8559
74 | 2628731.7977 | 1189946.1643 | 2628723.4606 | 1189964.1451 | 2628696.2244 | 1190030.5501 | 2628663.2148 | 1190110.0457 | 2628659.8119 | 1190120.0237
75 | 2628658.9225 | 1190122.6319 | 2628668.7526 | 1190109.6609 | 2628690.4129 | 1190083.306 | 2628693.9973 | 1190081.6222 | 2628700.2049 | 1190081.9638
76 | 2628658.9225 | 1190122.6319 | 2628656.3257 | 1190133.0695 | 2628655.0451 | 1190142.5462 | 2628654.0217 | 1190152.4466 | 2628653.3724 | 1190168.6522 | 2628653.8309 | 1190189.1764 | 2628655.1514 | 1190206.4475 | 2628661.0641 | 1190244.0514 | 2628669.3503 | 1190290.7826
77 | 2628658.9225 | 1190122.6319 | 2628659.8119 | 1190120.0237
78 | 2628676.2721 | 1190331.0149 | 2628675.505 | 1190322.4067 | 2628674.433 | 1190315.3756 | 2628669.3503 | 1190290.7826
79 | 2628669.3503 | 1190290.7826 | 2628681.4285 | 1190297.1771 | 2628719.3571 | 1190320.8046 | 2628755.852 | 1190344.4254 | 2628782.1696 | 1190358.0034 | 2628803.8089 | 1190366.056 | 2628821.7929 | 1190368.3881 | 2628832.8551 | 1190365.5843 | 2628840.4562 | 1190357.8722 | 2628837.8755 | 1190341.1509 | 2628838.5471 | 1190329.937 | 2628846.1415 | 1190323.648 | 2628845.5747 | 1190314.6738 | 2628839.865 | 1190311.1889 | 2628842.1536 | 1190303.04 | 2628850.759 | 1190299.0015 | 2628855.6861 | 1190295.5678 | 2628851.2217 | 1190288.4092 | 2628849.6089 | 1190282.8874 | 2628860.2723 | 1190277.4358 | 2628853.7771 | 1190267.6215 | 2628851.3493 | 1190261.9068 | 2628851.3493 | 1190261.9068
80 | 2628676.2721 | 1190331.0149 | 2628686.132 | 1190340.4449 | 2628690.8325 | 1190346.0815 | 2628695.5763 | 1190353.8417 | 2628705.9058 | 1190373.4572 | 2628715.3969 | 1190389.8224 | 2628721.1673 | 1190396.5314 | 2628727.2394 | 1190402.3636 | 2628744.472 | 1190413.4855
81 | 2628574.9983 | 1190435.9653 | 2628619.7168 | 1190396.4575 | 2628637.84 | 1190380.8134 | 2628651.1388 | 1190367.9034 | 2628661.4174 | 1190356.7354 | 2628668.0027 | 1190349.3296 | 2628671.9197 | 1190343.4341 | 2628674.3988 | 1190338.4544 | 2628675.9507 | 1190334.4375 | 2628676.2721 | 1190331.0149
82 | 2628851.3493 | 1190261.9068 | 2628855.9394 | 1190258.8886
83 | 2628347.6062 | 1190069.2639 | 2628349.6192 | 1190082.985 | 2628350.5919 | 1190096.5969 | 2628350.1467 | 1190108.5011 | 2628348.7777 | 1190120.6456 | 2628347.6661 | 1190125.8069
84 | 2628343.3076 | 1190140.6046 | 2628344.835 | 1190136.8467 | 2628346.9767 | 1190129.0082 | 2628347.6661 | 1190125.8069
85 | 2628574.9983 | 1190435.9653 | 2628573.4822 | 1190432.5006 | 2628572.5665 | 1190427.8605 | 2628572.5218 | 1190421.2345 | 2628574.1819 | 1190408.9025 | 2628574.1722 | 1190402.9215 | 2628573.0161 | 1190395.9233 | 2628571.0312 | 1190390.033 | 2628565.8169 | 1190376.0757
86 | 2628855.9394 | 1190258.8886 | 2628856.0154 | 1190258.8387 | 2628865.6409 | 1190254.1953
87 | 2628567.7538 | 1190338.1366 | 2628568.8051 | 1190335.56 | 2628572.2221 | 1190320.9685 | 2628574.7053 | 1190315.0994 | 2628577.9072 | 1190312.0352
88 | 2628566.5855 | 1190341.0001 | 2628567.7538 | 1190338.1366
89 | 2628402.5061 | 1189417.3474 | 2628403.6151 | 1189412.5561
90 | 2628402.5061 | 1189417.3474 | 2628401.8182 | 1189425.7263 | 2628399.5173 | 1189433.2973
91 | 2628399.5173 | 1189433.2973 | 2628399.1725 | 1189436.8531 | 2628394.9156 | 1189446.8271
92 | 2628399.5173 | 1189433.2973 | 2628394.314 | 1189436.9857 | 2628389.7194 | 1189444.8602
93 | 2628415.5946 | 1189489.3588 | 2628408.5041 | 1189488.9806 | 2628401.2494 | 1189487.8345 | 2628393.0294 | 1189484.3937 | 2628387.4041 | 1189480.5873 | 2628383.7102 | 1189476.3342 | 2628380.8341 | 1189470.1173 | 2628380.668 | 1189463.3129 | 2628382.1983 | 1189457.417 | 2628385.0184 | 1189452.9168 | 2628389.7194 | 1189444.8602
94 | 2628258.2851 | 1189668.2441 | 2628268.8894 | 1189657.6329 | 2628282.5347 | 1189650.6602 | 2628311.52 | 1189639.5688 | 2628317.7352 | 1189637.9528
95 | 2628258.2851 | 1189668.2441 | 2628262.381 | 1189632.4999 | 2628259.5335 | 1189615.3329 | 2628210.8227 | 1189539.9079 | 2628124.9159 | 1189435.6045
96 | 2628258.2851 | 1189668.2441 | 2628253.992 | 1189685.7088
97 | 2628190.5619 | 1190058.3999 | 2628192.3097 | 1190056.4515 | 2628198.3793 | 1190054.1836
98 | 2628212.5833 | 1190048.8762 | 2628198.3793 | 1190054.1836
99 | 2628124.9159 | 1189435.6045 | 2628113.566 | 1189439.2977 | 2628084.4951 | 1189449.0111
100 | 2627960.9008 | 1190029.4507 | 2627963.3611 | 1190030.7659 | 2627966.279 | 1190032.9696 | 2627968.4109 | 1190033.6688 | 2627970.6761 | 1190033.5571 | 2627977.1148 | 1190031.5753
101 | 2627926.9045 | 1190025.6822 | 2627951.1303 | 1190025.7618 | 2627955.4731 | 1190026.5491 | 2627960.9008 | 1190029.4507
102 | 2628057.3369 | 1190097.6738 | 2628061.6509 | 1190093.2139 | 2628062.8958 | 1190089.5511 | 2628063.3228 | 1190086.2847 | 2628057.6707 | 1190070.3608 | 2628043.8834 | 1190044.3936 | 2628039.3049 | 1190033.6776 | 2628035.2339 | 1190028.5559 | 2628031.3536 | 1190026.7034 | 2628027.2684 | 1190026.273 | 2627989.7513 | 1190029.4661 | 2627983.4137 | 1190029.6366 | 2627977.1148 | 1190031.5753
103 | 2627926.9045 | 1190025.6822 | 2627927.6012 | 1190016.8919 | 2627929.2384 | 1190007.5612 | 2627931.0499 | 1189998.4648 | 2627935.1705 | 1189979.8741 | 2627936.3504 | 1189973.7652 | 2627937.3482 | 1189967.4665 | 2627938.1241 | 1189959.6993 | 2627938.7388 | 1189948.8742 | 2627939.4117 | 1189933.7693 | 2627940.047 | 1189915.2624 | 2627940.4244 | 1189873.5642 | 2627940.5584 | 1189866.0719 | 2627940.4306 | 1189860.7685 | 2627940.0573 | 1189857.4205 | 2627939.1472 | 1189854.726 | 2627937.2923 | 1189851.8491
104 | 2627937.2923 | 1189851.8491 | 2627943.2176 | 1189843.639 | 2627951.6102 | 1189832.9058 | 2627959.4257 | 1189823.2704 | 2627964.8988 | 1189817.2149 | 2627971.351 | 1189810.5081 | 2627988.7114 | 1189793.2799 | 2627992.8929 | 1189789.4529 | 2627996.8034 | 1189786.5252 | 2628000.8612 | 1189784.6987 | 2628004.4873 | 1189783.8819 | 2628008.2941 | 1189783.555 | 2628013.3121 | 1189783.4896 | 2628022.9058 | 1189783.401 | 2628027.6588 | 1189782.9563 | 2628031.0713 | 1189782.1496 | 2628034.9679 | 1189780.5447 | 2628038.2103 | 1189778.6033 | 2628041.2644 | 1189776.1718 | 2628043.1963 | 1189774.0019 | 2628045.3005 | 1189770.8545 | 2628047.5714 | 1189766.3072 | 2628048.6647 | 1189762.4436 | 2628049.2809 | 1189759.5005 | 2628049.6321 | 1189756.1559 | 2628049.6177 | 1189751.0753 | 2628046.9164 | 1189725.3823 | 2628046.3523 | 1189715.5634 | 2628045.9976 | 1189698.4637 | 2628047.984 | 1189690.7914
105 | 2628047.984 | 1189690.7914 | 2628050.9833 | 1189679.2069
106 | 2627931.304 | 1189366.2295 | 2627935.1174 | 1189371.072 | 2627956.8831 | 1189408.649 | 2627989.2096 | 1189472.6116 | 2628019.0508 | 1189519.9539 | 2628034.5228 | 1189538.1914 | 2628051.3002 | 1189562.6496 | 2628068.5794 | 1189623.2293 | 2628067.3965 | 1189638.065 | 2628055.0531 | 1189663.4874 | 2628050.9833 | 1189679.2069
107 | 2627931.304 | 1189366.2295 | 2627937.3012 | 1189360.6878 | 2627950.5189 | 1189352.2338
108 | 2629097.9361 | 1190024.0935 | 2629093.1914 | 1190032.2749 | 2629066.4641 | 1190101.46 | 2628989.6125 | 1190176.1278 | 2628943.2256 | 1190209.7439 | 2628927.8603 | 1190214.5612 | 2628918.6401 | 1190217.9852 | 2628913.4199 | 1190222.0845 | 2628910.6337 | 1190224.2722 | 2628903.2761 | 1190232.0298 | 2628896.2494 | 1190237.5655 | 2628891.1803 | 1190240.387 | 2628886.1848 | 1190242.1639
109 | 2628137.6636 | 1190310.2969 | 2628146.1989 | 1190309.7033 | 2628151.9897 | 1190309.041
110 | 2628137.6636 | 1190310.2969 | 2628133.3354 | 1190314.5566 | 2628130.1927 | 1190316.9186
111 | 2628151.9897 | 1190309.041 | 2628154.0417 | 1190308.8063 | 2628160.4013 | 1190307.1352
112 | 2628130.1927 | 1190316.9186 | 2628128.308 | 1190318.335 | 2628123.2784 | 1190321.7424
113 | 2628168.9393 | 1190303.8179 | 2628166.6033 | 1190304.9299 | 2628160.4013 | 1190307.1352 | 2628160.4013 | 1190307.1352
114 | 2628120.6762 | 1190323.4649 | 2628121.936 | 1190322.6519 | 2628123.2784 | 1190321.7424
115 | 2628130.0014 | 1190389.681 | 2628132.6433 | 1190392.1503 | 2628149.3851 | 1190407.3481 | 2628155.6942 | 1190413.1475 | 2628162.6688 | 1190423.3634 | 2628175.4806 | 1190445.68 | 2628183.4001 | 1190457.6458 | 2628190.2302 | 1190464.5149 | 2628195.3185 | 1190467.2403 | 2628199.4634 | 1190467.8934 | 2628203.6134 | 1190467.4461 | 2628206.6563 | 1190465.7039 | 2628209.1624 | 1190462.8634
116 | 2628289.6838 | 1190591.7734 | 2628209.1624 | 1190462.8634
117 | 2628130.0014 | 1190389.681 | 2628117.3838 | 1190377.9045 | 2628111.9158 | 1190371.5866 | 2628109.458 | 1190367.2505 | 2628108.6511 | 1190365.3457 | 2628107.9782 | 1190362.4966 | 2628107.4571 | 1190356.5354 | 2628107.3966 | 1190348.2974 | 2628107.7248 | 1190343.363 | 2628109.3954 | 1190336.7117 | 2628112.3427 | 1190330.978 | 2628114.6889 | 1190328.2209 | 2628117.3011 | 1190325.6429 | 2628120.6762 | 1190323.4649
118 | 2628289.6838 | 1190591.7734 | 2628294.6645 | 1190631.796 | 2628296.0013 | 1190634.4927 | 2628298.5498 | 1190637.3284 | 2628301.4961 | 1190641.5112 | 2628302.8329 | 1190644.2079 | 2628303.3616 | 1190646.9007 | 2628302.6747 | 1190650.2548
119 | 2628289.6838 | 1190591.7734 | 2628294.5122 | 1190395.9472
120 | 2628238.1973 | 1190788.4468 | 2628236.8767 | 1190770.9757 | 2628234.5476 | 1190752.3326 | 2628233.0183 | 1190743.554 | 2628230.0531 | 1190733.6792 | 2628207.1496 | 1190688.1471 | 2628205.3707 | 1190682.1689 | 2628204.3026 | 1190677.4503 | 2628204.6276 | 1190671.5709 | 2628205.6685 | 1190665.8727 | 2628206.2873 | 1190659.1498 | 2628206.226 | 1190652.7239 | 2628204.1711 | 1190629.2461 | 2628204.1339 | 1190619.3295 | 2628205.8918 | 1190611.9561 | 2628207.8631 | 1190607.841 | 2628212.5377 | 1190604.4723 | 2628219.1496 | 1190602.5801 | 2628225.5825 | 1190601.4654 | 2628233.8519 | 1190602.1936 | 2628244.4799 | 1190604.0224 | 2628253.0491 | 1190604.2407 | 2628261.2693 | 1190602.4673 | 2628272.4675 | 1190598.1511 | 2628283.9358 | 1190593.1581 | 2628289.6838 | 1190591.7734
121 | 2628174.5818 | 1190301.132 | 2628174.5818 | 1190301.132 | 2628168.9393 | 1190303.8179
122 | 2628336.7779 | 1190155.5853 | 2628331.5784 | 1190163.4427 | 2628326.3837 | 1190170.2884 | 2628320.6139 | 1190176.2088 | 2628313.6088 | 1190182.1344 | 2628304.7997 | 1190188.9965 | 2628294.2549 | 1190195.239 | 2628279.1209 | 1190202.8605 | 2628268.4384 | 1190209.2247 | 2628257.4341 | 1190217.5328 | 2628235.3905 | 1190235.1272 | 2628225.503 | 1190242.7292 | 2628220.4361 | 1190246.763 | 2628215.4438 | 1190251.1419 | 2628211.5786 | 1190255.8484 | 2628207.6267 | 1190261.1327 | 2628202.9819 | 1190269.4708 | 2628196.9729 | 1190279.27 | 2628191.1263 | 1190286.98 | 2628185.7452 | 1190292.9801 | 2628180.8227 | 1190297.137 | 2628174.5818 | 1190301.132
123 | 2628336.7779 | 1190155.5853 | 2628340.1134 | 1190148.4639 | 2628343.3076 | 1190140.6046
124 | 2628548.6503 | 1190347.1035 | 2628336.7779 | 1190155.5853
125 | 2628548.6503 | 1190347.1035 | 2628551.6873 | 1190354.6553 | 2628557.6345 | 1190362.7324 | 2628562.4105 | 1190366.9574
126 | 2628562.4105 | 1190366.9574 | 2628565.8169 | 1190376.0757
127 | 2628562.4105 | 1190366.9574 | 2628561.7578 | 1190359.906 | 2628561.8988 | 1190354.3371 | 2628563.5356 | 1190348.4751 | 2628566.5855 | 1190341.0001
128 | 2628607.9868 | 1190703.71 | 2628632.0006 | 1190670.996 | 2628650.6225 | 1190654.5206 | 2628660.5251 | 1190648.5425 | 2628664.0136 | 1190646.1135 | 2628668.0359 | 1190642.075 | 2628675.2812 | 1190636.9069 | 2628683.7599 | 1190633.7124 | 2628692.7723 | 1190632.1213 | 2628706.7097 | 1190632.2548 | 2628719.9311 | 1190633.8078 | 2628757.4299 | 1190638.49 | 2628758.9994 | 1190638.958

## bus_geodata
| x | y | coords
0 | 2628376.274 | 1190928.9345
1 | 2628393.5499 | 1190908.489
2 | 2628259.6843 | 1190946.4282
3 | 2628268.6977 | 1190923.7406
4 | 2627785.7597 | 1190345.2481
5 | 2627820.4145 | 1190356.5493
6 | 2627721.9482 | 1190310.5942
7 | 2627823.012 | 1190356.5596
8 | 2627684.276 | 1190275.1569
9 | 2628107.0728 | 1190612.459
10 | 2627914.6059 | 1190616.4288
11 | 2628062.157 | 1190403.8281
12 | 2627838.0094 | 1190357.4406
13 | 2627534.3264 | 1190107.6773
14 | 2627714.2445 | 1190198.9658
15 | 2627841.5896 | 1190357.6753
16 | 2627534.0539 | 1190090.6337
17 | 2627702.0968 | 1190065.9366
18 | 2627866.1182 | 1190357.7542
19 | 2627887.6386 | 1190301.502
20 | 2627871.4966 | 1190365.3721
21 | 2627876.2408 | 1190222.4291
22 | 2627918.8543 | 1190292.1565
23 | 2627908.9205 | 1190214.6881
24 | 2627844.1359 | 1190173.8137
25 | 2627903.6932 | 1190618.4603
26 | 2628073.3204 | 1190364.5242
27 | 2628044.6645 | 1190239.3537
28 | 2627936.7428 | 1190081.002
29 | 2627828.8468 | 1190149.2144
30 | 2627807.1556 | 1190602.2055
31 | 2627805.5828 | 1190596.0781
32 | 2628828.584 | 1189836.5019
33 | 2628851.8885 | 1189823.4865
34 | 2628814.1369 | 1189848.2183
35 | 2628872.4573 | 1189812.0662
36 | 2628790.6052 | 1189871.4341
37 | 2628774.2538 | 1189889.1121
38 | 2628754.9216 | 1189909.215
39 | 2628778.4166 | 1189540.1555
40 | 2628775.186 | 1189724.0651
41 | 2628641.2617 | 1189444.4861
42 | 2628745.2264 | 1189763.309
43 | 2628952.2058 | 1189556.6723
44 | 2628615.0366 | 1189403.5768
45 | 2628381.9594 | 1189643.1592
46 | 2628649.5601 | 1189903.7482
47 | 2628725.0654 | 1189741.5961
48 | 2628890.0746 | 1189555.3831
49 | 2628880.0566 | 1189430.4245
50 | 2628695.0322 | 1189930.2676
51 | 2628701.7671 | 1189744.1239
52 | 2628902.6443 | 1189354.1142
53 | 2628872.2391 | 1190225.4961
54 | 2628881.472 | 1190242.2524
55 | 2628976.4062 | 1190005.6285
56 | 2629005.6726 | 1189985.2258
57 | 2628705.9908 | 1189737.9742
58 | 2628477.7828 | 1189742.6438
59 | 2628409.154 | 1189510.8589
60 | 2628339.6423 | 1189901.5242
61 | 2628731.7977 | 1189946.1643
62 | 2628700.2049 | 1190081.9638
63 | 2628658.9225 | 1190122.6319
64 | 2628669.3503 | 1190290.7826
65 | 2628659.8119 | 1190120.0237
66 | 2628676.2721 | 1190331.0149
67 | 2628851.3493 | 1190261.9068
68 | 2628347.6062 | 1190069.2639
69 | 2628347.6661 | 1190125.8069
70 | 2628744.472 | 1190413.4855
71 | 2628574.9983 | 1190435.9653
72 | 2628855.9394 | 1190258.8886
73 | 2628738.3718 | 1189932.8559
74 | 2628577.9072 | 1190312.0352
75 | 2628567.7538 | 1190338.1366
76 | 2628403.6151 | 1189412.5561
77 | 2628402.5061 | 1189417.3474
78 | 2628399.5173 | 1189433.2972
79 | 2628394.9156 | 1189446.8271
80 | 2628389.7194 | 1189444.8602
81 | 2628415.5946 | 1189489.3588
82 | 2628401.1876 | 1189603.9434
83 | 2628265.006 | 1189852.6151
84 | 2628317.7352 | 1189637.9528
85 | 2628258.2851 | 1189668.2441
86 | 2628190.5619 | 1190058.3999
87 | 2628198.3793 | 1190054.1836
88 | 2628253.992 | 1189685.7088
89 | 2628124.9159 | 1189435.6045
90 | 2628212.5833 | 1190048.8762
91 | 2627960.9008 | 1190029.4507
92 | 2627977.1148 | 1190031.5753
93 | 2627926.9045 | 1190025.6822
94 | 2628057.3369 | 1190097.6738
95 | 2627937.2923 | 1189851.8491
96 | 2628047.984 | 1189690.7914
97 | 2628050.9833 | 1189679.2069
98 | 2627931.304 | 1189366.2295
99 | 2627950.5189 | 1189352.2338
100 | 2628084.4951 | 1189449.0111
101 | 2629007.5481 | 1189983.2353
102 | 2629097.9361 | 1190024.0935
103 | 2628886.1848 | 1190242.1639
104 | 2628865.6409 | 1190254.1953
105 | 2628137.6636 | 1190310.2969
106 | 2628151.9897 | 1190309.041
107 | 2628130.1927 | 1190316.9185
108 | 2628160.4013 | 1190307.1352
109 | 2628123.2784 | 1190321.7424
110 | 2628209.1624 | 1190462.8634
111 | 2628130.0014 | 1190389.681
112 | 2628289.6838 | 1190591.7734
113 | 2628120.6762 | 1190323.4649
114 | 2628302.6747 | 1190650.2548
115 | 2628294.5122 | 1190395.9472
116 | 2628238.1973 | 1190788.4468
117 | 2628168.9393 | 1190303.8179
118 | 2628174.5818 | 1190301.132
119 | 2628336.7779 | 1190155.5853
120 | 2628343.3076 | 1190140.6046
121 | 2628548.6503 | 1190347.1035
122 | 2628562.4105 | 1190366.9574
123 | 2627967.0796 | 1190095.6944
124 | 2628044.8091 | 1190239.3129
125 | 2627796.4941 | 1189971.2696
126 | 2628607.9868 | 1190703.71
127 | 2628758.9994 | 1190638.958
128 | 2628566.5855 | 1190341.0001
129 | 2628565.8169 | 1190376.0757
130 | 2628347.6062 | 1190069.2639

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1