## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_904-2_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_904-2_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_904-2_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_904-2_0_6_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_904-2_0_6_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_904-2_0_6_node_44 | 0.4 | n |  | TRUE
6 | bus_LV_904-2_0_6_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_904-2_0_6_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_904-2_0_6_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_904-2_0_6_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_904-2_0_6_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_904-2_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_904-2_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_904-2_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_904-2_0_6_node_55 | 0.4 | n |  | TRUE
15 | bus_LV_904-2_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_904-2_0_6_node_103 | 0.4 | n |  | TRUE
17 | bus_LV_904-2_0_6_node_101 | 0.4 | n |  | TRUE
18 | bus_LV_904-2_0_6_node_110 | 0.4 | n |  | TRUE
19 | bus_LV_904-2_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_904-2_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_904-2_0_6_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_904-2_0_6_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_904-2_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_904-2_0_6_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_904-2_0_6_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_904-2_0_6_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_904-2_0_6_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_904-2_0_6_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_904-2_0_6_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_904-2_0_6_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_904-2_0_6_node_317 | 0.4 | n |  | TRUE
32 | bus_LV_904-2_0_6_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_904-2_0_6_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_904-2_0_6_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_904-2_0_6_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_904-2_0_6_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_904-2_0_6_node_47 | 0.4 | n |  | TRUE
38 | bus_LV_904-2_0_6_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_904-2_0_6_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_904-2_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_904-2_0_6_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_904-2_0_6_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_904-2_0_6_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_904-2_0_6_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_904-2_0_6_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_904-2_0_6_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_904-2_0_6_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_904-2_0_6_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_904-2_0_6_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_904-2_0_6_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_904-2_0_6_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_904-2_0_6_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_904-2_0_6_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_904-2_0_6_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_904-2_0_6_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_904-2_0_6_node_63 | 0.4 | n |  | TRUE
57 | bus_LV_904-2_0_6_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_904-2_0_6_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_904-2_0_6_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_904-2_0_6_node_66 | 0.4 | n |  | TRUE
61 | bus_LV_904-2_0_6_node_109 | 0.4 | n |  | TRUE
62 | bus_LV_904-2_0_6_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_904-2_0_6_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_904-2_0_6_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_904-2_0_6_node_76 | 0.4 | n |  | TRUE
66 | bus_LV_904-2_0_6_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_904-2_0_6_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_904-2_0_6_node_262 | 0.4 | n |  | TRUE
69 | bus_LV_904-2_0_6_node_324 | 0.4 | n |  | TRUE
70 | bus_LV_904-2_0_6_node_326 | 0.4 | n |  | TRUE
71 | bus_LV_904-2_0_6_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_904-2_0_6_node_327 | 0.4 | n |  | TRUE
73 | bus_LV_904-2_0_6_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_904-2_0_6_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_904-2_0_6_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_904-2_0_6_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_904-2_0_6_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_904-2_0_6_node_77 | 0.4 | n |  | TRUE
79 | bus_LV_904-2_0_6_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_904-2_0_6_node_91 | 0.4 | n |  | TRUE
81 | bus_LV_904-2_0_6_node_90 | 0.4 | n |  | TRUE
82 | bus_LV_904-2_0_6_node_87 | 0.4 | n |  | TRUE
83 | bus_LV_904-2_0_6_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_904-2_0_6_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_904-2_0_6_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_904-2_0_6_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_904-2_0_6_node_107 | 0.4 | n |  | TRUE
88 | bus_LV_904-2_0_6_node_98 | 0.4 | n |  | TRUE
89 | bus_LV_904-2_0_6_node_99 | 0.4 | n |  | TRUE
90 | bus_LV_904-2_0_6_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_904-2_0_6_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_904-2_0_6_node_106 | 0.4 | n |  | TRUE
93 | bus_LV_904-2_0_6_node_104 | 0.4 | n |  | TRUE
94 | bus_LV_904-2_0_6_node_112 | 0.4 | n |  | TRUE
95 | bus_LV_904-2_0_6_node_105 | 0.4 | n |  | TRUE
96 | bus_LV_904-2_0_6_node_265 | 0.4 | n |  | TRUE
97 | bus_LV_904-2_0_6_node_111 | 0.4 | n |  | TRUE
98 | bus_LV_904-2_0_6_node_269 | 0.4 | n |  | TRUE
99 | bus_LV_904-2_0_6_node_256 | 0.4 | n |  | TRUE
100 | bus_LV_904-2_0_6_node_257 | 0.4 | n |  | TRUE
101 | bus_LV_904-2_0_6_node_258 | 0.4 | n |  | TRUE
102 | bus_LV_904-2_0_6_node_287 | 0.4 | n |  | TRUE
103 | bus_LV_904-2_0_6_node_259 | 0.4 | n |  | TRUE
104 | bus_LV_904-2_0_6_node_295 | 0.4 | n |  | TRUE
105 | bus_LV_904-2_0_6_node_288 | 0.4 | n |  | TRUE
106 | bus_LV_904-2_0_6_node_260 | 0.4 | n |  | TRUE
107 | bus_LV_904-2_0_6_node_261 | 0.4 | n |  | TRUE
108 | bus_LV_904-2_0_6_node_263 | 0.4 | n |  | TRUE
109 | bus_LV_904-2_0_6_node_264 | 0.4 | n |  | TRUE
110 | bus_LV_904-2_0_6_node_274 | 0.4 | n |  | TRUE
111 | bus_LV_904-2_0_6_node_275 | 0.4 | n |  | TRUE
112 | bus_LV_904-2_0_6_node_266 | 0.4 | n |  | TRUE
113 | bus_LV_904-2_0_6_node_267 | 0.4 | n |  | TRUE
114 | bus_LV_904-2_0_6_node_268 | 0.4 | n |  | TRUE
115 | bus_LV_904-2_0_6_node_270 | 0.4 | n |  | TRUE
116 | bus_LV_904-2_0_6_node_273 | 0.4 | n |  | TRUE
117 | bus_LV_904-2_0_6_node_272 | 0.4 | n |  | TRUE
118 | bus_LV_904-2_0_6_node_271 | 0.4 | n |  | TRUE
119 | bus_LV_904-2_0_6_node_277 | 0.4 | n |  | TRUE
120 | bus_LV_904-2_0_6_node_278 | 0.4 | n |  | TRUE
121 | bus_LV_904-2_0_6_node_276 | 0.4 | n |  | TRUE
122 | bus_LV_904-2_0_6_node_323 | 0.4 | n |  | TRUE
123 | bus_LV_904-2_0_6_node_279 | 0.4 | n |  | TRUE
124 | bus_LV_904-2_0_6_node_280 | 0.4 | n |  | TRUE
125 | bus_LV_904-2_0_6_node_310 | 0.4 | n |  | TRUE
126 | bus_LV_904-2_0_6_node_309 | 0.4 | n |  | TRUE
127 | bus_LV_904-2_0_6_node_286 | 0.4 | n |  | TRUE
128 | bus_LV_904-2_0_6_node_311 | 0.4 | n |  | TRUE
129 | bus_LV_904-2_0_6_node_283 | 0.4 | n |  | TRUE
130 | bus_LV_904-2_0_6_node_284 | 0.4 | n |  | TRUE
131 | bus_LV_904-2_0_6_node_285 | 0.4 | n |  | TRUE
132 | bus_LV_904-2_0_6_node_296 | 0.4 | n |  | TRUE
133 | bus_LV_904-2_0_6_node_289 | 0.4 | n |  | TRUE
134 | bus_LV_904-2_0_6_node_290 | 0.4 | n |  | TRUE
135 | bus_LV_904-2_0_6_node_292 | 0.4 | n |  | TRUE
136 | bus_LV_904-2_0_6_node_293 | 0.4 | n |  | TRUE
137 | bus_LV_904-2_0_6_node_294 | 0.4 | n |  | TRUE
138 | bus_LV_904-2_0_6_node_321 | 0.4 | n |  | TRUE
139 | bus_MV_107_0_node_40 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_904-2_0_6_load_0 | 0 | 0.0016908 | 0.00042376 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_904-2_0_6_load_3 | 2 | 0.00042975 | 0.00010771 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_904-2_0_6_load_4 | 3 | 0.00026196 | 6.5653e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_904-2_0_6_load_25 | 4 | 0.0019692 | 0.00049352 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_904-2_0_6_load_31 | 7 | 0.00021877 | 5.4828e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_904-2_0_6_load_30 | 8 | 0.0010587 | 0.00026535 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_904-2_0_6_load_6 | 9 | 0.00077557 | 0.00019438 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_904-2_0_6_load_7 | 10 | 0.040366 | 0.010117 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_904-2_0_6_load_9 | 12 | 0.015275 | 0.0038283 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_904-2_0_6_load_55 | 14 | 0.0042267 | 0.0010593 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_904-2_0_6_load_103 | 16 | 0.0014242 | 0.00035693 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_904-2_0_6_load_110 | 18 | 0.0021145 | 0.00052994 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_904-2_0_6_load_12 | 19 | 0.0029446 | 0.00073798 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_904-2_0_6_load_13 | 20 | 0.0013755 | 0.00034472 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_904-2_0_6_load_16 | 23 | 0.0017844 | 0.00044722 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_904-2_0_6_load_56 | 24 | 0.0021596 | 0.00054125 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_904-2_0_6_load_45 | 26 | 0.00068747 | 0.0001723 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_904-2_0_6_load_317 | 31 | 0.0070349 | 0.0017631 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_904-2_0_6_load_40 | 33 | 0.010391 | 0.0026043 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_904-2_0_6_load_21 | 34 | 0.00055009 | 0.00013787 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_904-2_0_6_load_24 | 36 | 0.00032769 | 8.2126e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_904-2_0_6_load_47 | 37 | 0.0016637 | 0.00041695 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_904-2_0_6_load_29 | 38 | 0.0016128 | 0.00040419 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_904-2_0_6_load_52 | 39 | 0.00034935 | 8.7555e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_904-2_0_6_load_26 | 40 | 0.00044377 | 0.00011122 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_904-2_0_6_load_27 | 41 | 0.00055671 | 0.00013953 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_904-2_0_6_load_37 | 43 | 0.0017317 | 0.00043401 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_904-2_0_6_load_32 | 44 | 0.0013765 | 0.00034499 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_904-2_0_6_load_33 | 45 | 0.0007064 | 0.00017704 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_904-2_0_6_load_34 | 46 | 0.00058354 | 0.00014625 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_904-2_0_6_load_54 | 48 | 0.0063165 | 0.0015831 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_904-2_0_6_load_41 | 49 | 0.002793 | 0.00069999 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_904-2_0_6_load_38 | 50 | 0.00039108 | 9.8015e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_904-2_0_6_load_39 | 51 | 0.00043713 | 0.00010955 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_904-2_0_6_load_43 | 52 | 0.00048339 | 0.00012115 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_904-2_0_6_load_46 | 53 | 0.0032893 | 0.00082437 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_904-2_0_6_load_48 | 54 | 0.0014882 | 0.00037297 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_904-2_0_6_load_108 | 57 | 0.0007928 | 0.00019869 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_904-2_0_6_load_66 | 60 | 0.0014473 | 0.00036273 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_904-2_0_6_load_109 | 61 | 0.0010004 | 0.00025072 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_904-2_0_6_load_58 | 62 | 0.00019877 | 4.9816e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_904-2_0_6_load_59 | 63 | 0.00016459 | 4.125e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_904-2_0_6_load_61 | 64 | 0.00081391 | 0.00020399 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_904-2_0_6_load_262 | 68 | 0.00092504 | 0.00023184 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_904-2_0_6_load_324 | 69 | 0.0048131 | 0.0012063 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_904-2_0_6_load_326 | 70 | 0.00018025 | 4.5175e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_904-2_0_6_load_327 | 72 | 0.00056479 | 0.00014155 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_904-2_0_6_load_71 | 73 | 0.0001269 | 3.1804e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_904-2_0_6_load_73 | 75 | 0.00031094 | 7.7929e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_904-2_0_6_load_78 | 79 | 0.00010233 | 2.5647e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_904-2_0_6_load_91 | 80 | 0.00052372 | 0.00013126 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_904-2_0_6_load_87 | 82 | 0.00075382 | 0.00018892 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_904-2_0_6_load_86 | 83 | 0.00046641 | 0.00011689 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_904-2_0_6_load_85 | 84 | 0.00099366 | 0.00024904 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_904-2_0_6_load_88 | 85 | 0.00087882 | 0.00022025 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_904-2_0_6_load_89 | 86 | 0.00016552 | 4.1482e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_904-2_0_6_load_107 | 87 | 0.0017174 | 0.00043043 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_904-2_0_6_load_98 | 88 | 0.00064294 | 0.00016114 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_904-2_0_6_load_99 | 89 | 8.5291e-05 | 2.1376e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_904-2_0_6_load_100 | 90 | 0.00076054 | 0.00019061 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_904-2_0_6_load_102 | 91 | 0.00017113 | 4.2888e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_904-2_0_6_load_106 | 92 | 0.00024223 | 6.0709e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_904-2_0_6_load_265 | 96 | 9.3814e-05 | 2.3512e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_904-2_0_6_load_111 | 97 | 0.0060115 | 0.0015066 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_904-2_0_6_load_269 | 98 | 7.617e-05 | 1.909e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_904-2_0_6_load_256 | 99 | 0.00061842 | 0.00015499 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_904-2_0_6_load_287 | 102 | 0.00012352 | 3.0957e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_904-2_0_6_load_288 | 105 | 0.00061484 | 0.00015409 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_904-2_0_6_load_260 | 106 | 0.00010828 | 2.7139e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_904-2_0_6_load_261 | 107 | 0.00023411 | 5.8672e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_904-2_0_6_load_264 | 109 | 0.00010673 | 2.6748e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_904-2_0_6_load_274 | 110 | 0.00039871 | 9.9927e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_904-2_0_6_load_275 | 111 | 0.00018847 | 4.7236e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_904-2_0_6_load_267 | 113 | 0.0003513 | 8.8044e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_904-2_0_6_load_273 | 116 | 0.00012613 | 3.1612e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_904-2_0_6_load_272 | 117 | 0.00051818 | 0.00012987 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_904-2_0_6_load_271 | 118 | 6.6717e-05 | 1.6721e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_904-2_0_6_load_323 | 122 | 0.00047159 | 0.00011819 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_904-2_0_6_load_310 | 125 | 0.00019162 | 4.8024e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_904-2_0_6_load_309 | 126 | 0.00019404 | 4.8632e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_904-2_0_6_load_311 | 128 | 0.00025756 | 6.455e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_904-2_0_6_load_283 | 129 | 0.00017859 | 4.4758e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_904-2_0_6_load_285 | 131 | 0.00047125 | 0.00011811 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_904-2_0_6_load_296 | 132 | 8.3743e-05 | 2.0988e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_904-2_0_6_load_289 | 133 | 0.000131 | 3.2831e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_904-2_0_6_load_292 | 135 | 0.00044108 | 0.00011054 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_904-2_0_6_load_293 | 136 | 0.00012514 | 3.1363e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_904-2_0_6_load_321 | 138 | 0.00051221 | 0.00012837 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_904-2_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.28623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_904-2_0_6_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_904-2_0_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.088265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_904-2_0_6_line_3 | NAYY 4x150 SE | 2 | 4 | 0.021148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_904-2_0_6_line_4 | NAYY 4x150 SE | 3 | 5 | 0.48037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_904-2_0_6_line_5 | NAYY 4x150 SE | 4 | 39 | 0.0050777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_904-2_0_6_line_6 | NAYY 4x150 SE | 5 | 52 | 0.026908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_904-2_0_6_line_7 | NAYY 4x150 SE | 6 | 7 | 0.099577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_904-2_0_6_line_8 | NAYY 4x150 SE | 6 | 8 | 0.11642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_904-2_0_6_line_9 | NAYY 4x150 SE | 7 | 43 | 0.002042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_904-2_0_6_line_10 | NAYY 4x150 SE | 8 | 42 | 0.022776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_904-2_0_6_line_11 | NAYY 4x150 SE | 9 | 10 | 0.023244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_904-2_0_6_line_12 | NAYY 4x150 SE | 9 | 11 | 0.05379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_904-2_0_6_line_13 | NAYY 4x150 SE | 10 | 12 | 0.033122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_904-2_0_6_line_14 | NAYY 4x150 SE | 11 | 13 | 0.19002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_904-2_0_6_line_15 | NAYY 4x150 SE | 12 | 14 | 0.03052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_904-2_0_6_line_16 | NAYY 4x150 SE | 13 | 17 | 0.23689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_904-2_0_6_line_17 | NAYY 4x150 SE | 13 | 18 | 0.055566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_904-2_0_6_line_18 | NAYY 4x150 SE | 13 | 15 | 0.033263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_904-2_0_6_line_19 | NAYY 4x150 SE | 14 | 47 | 0.0029877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_904-2_0_6_line_20 | NAYY 4x150 SE | 15 | 16 | 0.043585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_904-2_0_6_line_21 | NAYY 4x150 SE | 17 | 91 | 0.011459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_904-2_0_6_line_22 | NAYY 4x150 SE | 17 | 89 | 0.15036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_904-2_0_6_line_23 | NAYY 4x150 SE | 18 | 97 | 0.012827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_904-2_0_6_line_24 | NAYY 4x150 SE | 19 | 20 | 0.0035328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_904-2_0_6_line_25 | NAYY 4x150 SE | 19 | 21 | 0.039858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_904-2_0_6_line_26 | NAYY 4x150 SE | 20 | 22 | 0.0081167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_904-2_0_6_line_27 | NAYY 4x150 SE | 21 | 23 | 0.01641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_904-2_0_6_line_28 | NAYY 4x150 SE | 22 | 24 | 0.030748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_904-2_0_6_line_29 | NAYY 4x150 SE | 22 | 25 | 0.011803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_904-2_0_6_line_30 | NAYY 4x150 SE | 23 | 26 | 0.033896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_904-2_0_6_line_31 | NAYY 4x150 SE | 25 | 49 | 0.0030317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_904-2_0_6_line_32 | NAYY 4x150 SE | 25 | 46 | 0.033942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_904-2_0_6_line_33 | NAYY 4x150 SE | 26 | 53 | 0.01311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_904-2_0_6_line_34 | NAYY 4x150 SE | 27 | 28 | 0.090046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_904-2_0_6_line_35 | NAYY 4x150 SE | 27 | 29 | 0.39291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
36 | LV_904-2_0_6_line_36 | NAYY 4x150 SE | 28 | 32 | 0.015245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_904-2_0_6_line_37 | NAYY 4x150 SE | 28 | 33 | 0.01891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_904-2_0_6_line_38 | NAYY 4x150 SE | 29 | 37 | 0.078683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_904-2_0_6_line_39 | NAYY 4x150 SE | 29 | 35 | 0.069404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_904-2_0_6_line_40 | NAYY 4x150 SE | 30 | 31 | 0.019437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_904-2_0_6_line_41 | NAYY 4x150 SE | 30 | 32 | 0.015928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_904-2_0_6_line_42 | NAYY 4x150 SE | 33 | 49 | 0.034222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_904-2_0_6_line_43 | NAYY 4x150 SE | 34 | 35 | 0.010765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_904-2_0_6_line_44 | NAYY 4x150 SE | 35 | 36 | 0.030861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_904-2_0_6_line_45 | NAYY 4x150 SE | 36 | 38 | 0.18318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_904-2_0_6_line_46 | NAYY 4x150 SE | 37 | 54 | 0.027163 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_904-2_0_6_line_47 | NAYY 4x150 SE | 38 | 41 | 0.19152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_904-2_0_6_line_48 | NAYY 4x150 SE | 40 | 41 | 0.004608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_904-2_0_6_line_49 | NAYY 4x150 SE | 40 | 42 | 0.026279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_904-2_0_6_line_50 | NAYY 4x150 SE | 43 | 50 | 0.014207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_904-2_0_6_line_51 | NAYY 4x150 SE | 44 | 45 | 0.002121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_904-2_0_6_line_52 | NAYY 4x150 SE | 44 | 46 | 0.022126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_904-2_0_6_line_53 | NAYY 4x150 SE | 45 | 47 | 0.03462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_904-2_0_6_line_54 | NAYY 4x150 SE | 47 | 48 | 0.010711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_904-2_0_6_line_55 | NAYY 4x150 SE | 50 | 51 | 0.0019581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_904-2_0_6_line_56 | NAYY 4x150 SE | 51 | 52 | 0.012102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_904-2_0_6_line_57 | NAYY 4x150 SE | 55 | 56 | 0.067175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_904-2_0_6_line_58 | NAYY 4x150 SE | 55 | 57 | 0.055863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_904-2_0_6_line_59 | NAYY 4x150 SE | 56 | 69 | 0.28632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_904-2_0_6_line_60 | NAYY 4x150 SE | 56 | 66 | 0.4539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_904-2_0_6_line_61 | NAYY 4x150 SE | 57 | 87 | 0.066221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_904-2_0_6_line_62 | NAYY 4x150 SE | 58 | 59 | 0.037363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_904-2_0_6_line_63 | NAYY 4x150 SE | 58 | 60 | 0.01027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_904-2_0_6_line_64 | NAYY 4x150 SE | 59 | 61 | 0.024956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_904-2_0_6_line_65 | NAYY 4x150 SE | 61 | 81 | 0.079883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_904-2_0_6_line_66 | NAYY 4x150 SE | 62 | 63 | 0.024283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_904-2_0_6_line_67 | NAYY 4x150 SE | 63 | 64 | 0.027102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_904-2_0_6_line_68 | NAYY 4x150 SE | 64 | 65 | 0.021111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_904-2_0_6_line_69 | NAYY 4x150 SE | 65 | 80 | 0.079621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_904-2_0_6_line_70 | NAYY 4x150 SE | 65 | 76 | 0.044402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_904-2_0_6_line_71 | NAYY 4x150 SE | 66 | 67 | 0.17567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_904-2_0_6_line_72 | NAYY 4x150 SE | 66 | 68 | 0.35112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_904-2_0_6_line_73 | NAYY 4x150 SE | 67 | 70 | 0.011905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_904-2_0_6_line_74 | NAYY 4x150 SE | 67 | 71 | 0.40818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_904-2_0_6_line_75 | NAYY 4x150 SE | 68 | 109 | 0.01931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_904-2_0_6_line_76 | NAYY 4x150 SE | 68 | 106 | 0.0099294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_904-2_0_6_line_77 | NAYY 4x150 SE | 71 | 72 | 0.013144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_904-2_0_6_line_78 | NAYY 4x150 SE | 73 | 74 | 0.040562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_904-2_0_6_line_79 | NAYY 4x150 SE | 74 | 77 | 0.10285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_904-2_0_6_line_80 | NAYY 4x150 SE | 75 | 76 | 0.0070439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_904-2_0_6_line_81 | NAYY 4x150 SE | 75 | 77 | 0.1144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_904-2_0_6_line_82 | NAYY 4x150 SE | 76 | 78 | 0.21458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_904-2_0_6_line_83 | NAYY 4x150 SE | 77 | 79 | 0.009955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_904-2_0_6_line_84 | NAYY 4x150 SE | 78 | 81 | 0.27354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_904-2_0_6_line_85 | NAYY 4x150 SE | 78 | 82 | 0.18758 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_904-2_0_6_line_86 | NAYY 4x150 SE | 79 | 83 | 0.021534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_904-2_0_6_line_87 | NAYY 4x150 SE | 81 | 87 | 0.028474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_904-2_0_6_line_88 | NAYY 4x150 SE | 82 | 85 | 0.073217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_904-2_0_6_line_89 | NAYY 4x150 SE | 83 | 84 | 0.020141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_904-2_0_6_line_90 | NAYY 4x150 SE | 85 | 86 | 0.0030614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_904-2_0_6_line_91 | NAYY 4x150 SE | 88 | 89 | 0.0071095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_904-2_0_6_line_92 | NAYY 4x150 SE | 88 | 90 | 0.045674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_904-2_0_6_line_93 | NAYY 4x150 SE | 91 | 92 | 0.010161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_904-2_0_6_line_94 | NAYY 4x150 SE | 92 | 93 | 0.010318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_904-2_0_6_line_95 | NAYY 4x150 SE | 93 | 94 | 0.21909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_904-2_0_6_line_96 | NAYY 4x150 SE | 94 | 98 | 0.13946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_904-2_0_6_line_97 | NAYY 4x150 SE | 94 | 95 | 0.015114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_904-2_0_6_line_98 | NAYY 4x150 SE | 95 | 96 | 0.26861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_904-2_0_6_line_99 | NAYY 4x150 SE | 96 | 112 | 0.042484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_904-2_0_6_line_100 | NAYY 4x150 SE | 98 | 109 | 0.017576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_904-2_0_6_line_101 | NAYY 4x150 SE | 99 | 100 | 0.21314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_904-2_0_6_line_102 | NAYY 4x150 SE | 100 | 101 | 0.022217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_904-2_0_6_line_103 | NAYY 4x150 SE | 101 | 102 | 0.036859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_904-2_0_6_line_104 | NAYY 4x150 SE | 102 | 105 | 0.018551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_904-2_0_6_line_105 | NAYY 4x150 SE | 103 | 104 | 0.13294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_904-2_0_6_line_106 | NAYY 4x150 SE | 103 | 105 | 0.079649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_904-2_0_6_line_107 | NAYY 4x150 SE | 104 | 135 | 0.027682 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_904-2_0_6_line_108 | NAYY 4x150 SE | 104 | 137 | 0.24914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_904-2_0_6_line_109 | NAYY 4x150 SE | 106 | 107 | 0.0014332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_904-2_0_6_line_110 | NAYY 4x150 SE | 107 | 108 | 0.14912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_904-2_0_6_line_111 | NAYY 4x150 SE | 108 | 110 | 0.031934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_904-2_0_6_line_112 | NAYY 4x150 SE | 108 | 111 | 0.044493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_904-2_0_6_line_113 | NAYY 4x150 SE | 110 | 120 | 0.049957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_904-2_0_6_line_114 | NAYY 4x150 SE | 112 | 113 | 0.013251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_904-2_0_6_line_115 | NAYY 4x150 SE | 113 | 114 | 0.038767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_904-2_0_6_line_116 | NAYY 4x150 SE | 114 | 115 | 0.046827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_904-2_0_6_line_117 | NAYY 4x150 SE | 115 | 116 | 0.026573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_904-2_0_6_line_118 | NAYY 4x150 SE | 115 | 117 | 0.013917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_904-2_0_6_line_119 | NAYY 4x150 SE | 116 | 119 | 0.11235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_904-2_0_6_line_120 | NAYY 4x150 SE | 117 | 118 | 0.017677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_904-2_0_6_line_121 | NAYY 4x150 SE | 119 | 121 | 0.022307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_904-2_0_6_line_122 | NAYY 4x150 SE | 120 | 123 | 0.022991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_904-2_0_6_line_123 | NAYY 4x150 SE | 120 | 124 | 0.11121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_904-2_0_6_line_124 | NAYY 4x150 SE | 121 | 122 | 0.012036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_904-2_0_6_line_125 | NAYY 4x150 SE | 123 | 125 | 0.006062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_904-2_0_6_line_126 | NAYY 4x150 SE | 123 | 126 | 0.011271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_904-2_0_6_line_127 | NAYY 4x150 SE | 124 | 127 | 0.090036 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_904-2_0_6_line_128 | NAYY 4x150 SE | 124 | 128 | 0.12356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_904-2_0_6_line_129 | NAYY 4x150 SE | 127 | 132 | 0.017028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_904-2_0_6_line_130 | NAYY 4x150 SE | 128 | 136 | 0.0058707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_904-2_0_6_line_131 | NAYY 4x150 SE | 129 | 130 | 0.010124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_904-2_0_6_line_132 | NAYY 4x150 SE | 130 | 131 | 0.021905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_904-2_0_6_line_133 | NAYY 4x150 SE | 131 | 132 | 0.0022641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_904-2_0_6_line_134 | NAYY 4x150 SE | 133 | 134 | 0.014351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_904-2_0_6_line_135 | NAYY 4x150 SE | 134 | 135 | 0.04241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_904-2_0_6_line_136 | NAYY 4x150 SE | 134 | 136 | 0.22468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_904-2_0_6_line_137 | NAYY 4x150 SE | 137 | 138 | 0.032557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_904-2_0_6_trafo_7 | 0.25 MVA 20/0.4 kV | 139 | 10 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41
0 | 2622222.4776 | 1189824.1876 | 2622212.9138 | 1189830.689 | 2622209.7295 | 1189831.8778 | 2622202.9222 | 1189833.2756 | 2622195.676 | 1189833.7824 | 2622186.7095 | 1189833.4157 | 2622174.8174 | 1189832.349 | 2622166.6753 | 1189831.7964 | 2622104.5079 | 1189832.5897 | 2622078.311 | 1189833.327 | 2622037.6047 | 1189835.5341 | 2621970.9555 | 1189837.8576 | 2621938.8127 | 1189837.7852
1 | 2622293.9354 | 1189835.114 | 2622288.9825 | 1189834.0839 | 2622272.0126 | 1189832.798 | 2622230.8477 | 1189827.0312 | 2622226.0864 | 1189825.7351 | 2622222.4776 | 1189824.1876
2 | 2622222.4776 | 1189824.1876 | 2622217.4323 | 1189821.3452 | 2622213.4035 | 1189817.884 | 2622209.4675 | 1189814.0897 | 2622204.7681 | 1189808.4248 | 2622200.4821 | 1189802.3391 | 2622196.9354 | 1189796.3784 | 2622186.9006 | 1189775.5858 | 2622178.3091 | 1189752.1528 | 2622177.729 | 1189750.3336
3 | 2622293.9354 | 1189835.114 | 2622302.8924 | 1189835.9588 | 2622308.0773 | 1189842.2481 | 2622310.6703 | 1189845.2941
4 | 2622024.2301 | 1189500.9083 | 2622006.418 | 1189514.8058 | 2621998.4221 | 1189522.0692 | 2621986.1691 | 1189536.0651 | 2621974.9465 | 1189551.9212 | 2621953.73 | 1189585.5058 | 2621949.0487 | 1189595.6384 | 2621946.051 | 1189606.2553 | 2621944.2478 | 1189619.6891 | 2621944.1784 | 1189632.4067 | 2621945.886 | 1189642.9963 | 2621949.3082 | 1189653.9146 | 2621956.2099 | 1189666.3686 | 2621966.8094 | 1189681.0707 | 2621973.6834 | 1189688.5443 | 2621985.8353 | 1189697.8826 | 2622014.3535 | 1189715.163 | 2622028.154 | 1189722.0061 | 2622035.9059 | 1189725.0473 | 2622041.5362 | 1189726.4576 | 2622046.6896 | 1189726.899 | 2622052.6853 | 1189726.3985 | 2622060.6526 | 1189724.7714 | 2622066.6491 | 1189722.0031 | 2622074.1473 | 1189717.2948 | 2622079.1229 | 1189712.1882 | 2622086.7261 | 1189703.834 | 2622092.2577 | 1189698.9295 | 2622097.2295 | 1189694.8568 | 2622103.6724 | 1189690.9562 | 2622108.0929 | 1189689.5718 | 2622115.3565 | 1189688.5313 | 2622121.395 | 1189688.8649 | 2622125.6676 | 1189690.3592 | 2622128.6285 | 1189691.8598 | 2622134.3013 | 1189696.2163 | 2622150.7831 | 1189712.0855 | 2622163.9253 | 1189725.7524 | 2622169.3063 | 1189732.7093 | 2622172.7341 | 1189737.8691 | 2622175.6933 | 1189743.9499 | 2622177.729 | 1189750.3336
5 | 2622310.6703 | 1189845.2941 | 2622313.9617 | 1189849.1605
6 | 2622024.2301 | 1189500.9083 | 2622033.5897 | 1189496.1068 | 2622049.0502 | 1189490.6686
7 | 2622123.85 | 1189403.6567 | 2622124.2524 | 1189414.475 | 2622123.5578 | 1189427.0457 | 2622121.7851 | 1189440.4018 | 2622120.0914 | 1189446.7878 | 2622117.997 | 1189452.2385 | 2622114.3698 | 1189457.6613 | 2622110.0831 | 1189462.0256 | 2622104.736 | 1189466.4749 | 2622097.0692 | 1189471.3048 | 2622090.8787 | 1189474.9395 | 2622078.7871 | 1189480.2089 | 2622077.6417 | 1189480.6118
8 | 2622123.85 | 1189403.6567 | 2622134.6236 | 1189402.1956 | 2622150.2315 | 1189398.8848 | 2622236.6893 | 1189375.3739
9 | 2622077.6417 | 1189480.6118 | 2622075.7154 | 1189481.2894
10 | 2622259.0236 | 1189371.0837 | 2622253.7367 | 1189371.5866 | 2622238.6399 | 1189374.8435 | 2622236.6893 | 1189375.3739
11 | 2623222.6265 | 1189430.0615 | 2623203.1975 | 1189417.3015
12 | 2623266.8299 | 1189460.6981 | 2623242.8507 | 1189443.6517 | 2623237.1924 | 1189439.6277 | 2623222.6265 | 1189430.0615
13 | 2623178.4971 | 1189395.3328 | 2623198.8462 | 1189414.4438 | 2623203.1975 | 1189417.3015
14 | 2623266.8299 | 1189460.6981 | 2623274.4275 | 1189466.0971 | 2623290.1042 | 1189480.51 | 2623306.8144 | 1189495.883 | 2623315.5226 | 1189505.8776 | 2623338.4896 | 1189534.0374 | 2623368.7422 | 1189577.1001 | 2623383.8302 | 1189595.7021 | 2623390.7083 | 1189603.6664
15 | 2623160.9431 | 1189370.3658 | 2623178.4971 | 1189395.3328 | 2623178.4971 | 1189395.3328
16 | 2623577.3726 | 1189748.2957 | 2623565.3971 | 1189735.4641 | 2623548.7479 | 1189722.3918 | 2623526.4806 | 1189708.775 | 2623466.3054 | 1189671.6531 | 2623416.7699 | 1189630.0709 | 2623390.7083 | 1189603.6664
17 | 2623390.7083 | 1189603.6664 | 2623374.4681 | 1189620.4676 | 2623357.8357 | 1189638.1455 | 2623350.7905 | 1189641.7781
18 | 2623390.7083 | 1189603.6664 | 2623383.8302 | 1189595.7021 | 2623392.1826 | 1189589.3424 | 2623399.9192 | 1189582.48 | 2623401.3502 | 1189581.2294
19 | 2623159.2247 | 1189367.9217 | 2623160.9431 | 1189370.3658
20 | 2623401.3502 | 1189581.2294 | 2623406.2762 | 1189575.4566 | 2623411.8948 | 1189570.0424 | 2623436.6542 | 1189556.5584
21 | 2623577.3726 | 1189748.2957 | 2623584.9586 | 1189756.8838
22 | 2623577.3726 | 1189748.2957 | 2623503.9582 | 1189810.7963 | 2623460.9933 | 1189843.4144
23 | 2623339.3897 | 1189647.6565 | 2623350.7905 | 1189641.7781
24 | 2623201.6152 | 1189288.4864 | 2623205.1449 | 1189288.3397
25 | 2623244.815 | 1189289.0332 | 2623234.0157 | 1189287.1459 | 2623220.4234 | 1189287.7047 | 2623205.1449 | 1189288.3397
26 | 2623193.5056 | 1189288.8234 | 2623201.6152 | 1189288.4864
27 | 2623244.815 | 1189289.0332 | 2623248.3034 | 1189294.1271 | 2623248.9743 | 1189304.3408
28 | 2623193.5056 | 1189288.8234 | 2623186.3796 | 1189258.9122
29 | 2623193.5056 | 1189288.8234 | 2623181.8371 | 1189290.8127
30 | 2623258.8855 | 1189336.5881 | 2623256.3448 | 1189330.6554 | 2623249.2684 | 1189308.8164 | 2623248.9743 | 1189304.3408
31 | 2623181.8371 | 1189290.8127 | 2623178.8293 | 1189291.1919
32 | 2623181.8371 | 1189290.8127 | 2623184.595 | 1189319.1717 | 2623185.1213 | 1189324.5958
33 | 2623264.0463 | 1189348.6392 | 2623258.8855 | 1189336.5881
34 | 2623050.8579 | 1189279.9358 | 2623063.916 | 1189275.5281 | 2623068.4428 | 1189274.3893 | 2623072.374 | 1189273.4595 | 2623077.3873 | 1189272.7339 | 2623084.8402 | 1189272.2512 | 2623088.3169 | 1189272.4869 | 2623095.4805 | 1189273.8263 | 2623100.1563 | 1189275.6119 | 2623106.2367 | 1189278.9927 | 2623110.6102 | 1189282.0222 | 2623115.2386 | 1189286.1867 | 2623119.1719 | 1189290.6598 | 2623123.6095 | 1189296.8357 | 2623127.2768 | 1189303.0086
35 | 2622698.5699 | 1189387.4386 | 2622731.8963 | 1189385.486 | 2622791.851 | 1189382.2339 | 2622820.2651 | 1189382.5754 | 2622824.95 | 1189381.9373 | 2622828.0956 | 1189381.0043 | 2622830.0474 | 1189379.1219 | 2622831.0941 | 1189376.6356 | 2622833.7764 | 1189365.1842 | 2622835.3194 | 1189360.521 | 2622836.7188 | 1189357.5247 | 2622838.8284 | 1189354.2644 | 2622842.4432 | 1189350.276 | 2622864.5444 | 1189330.2051 | 2622866.6652 | 1189328.0232 | 2622867.763 | 1189326.1486 | 2622868.1531 | 1189323.8377 | 2622868.0739 | 1189320.6135 | 2622880.8167 | 1189318.8167 | 2622900.4304 | 1189315.1451 | 2622967.526 | 1189303.4176 | 2622974.7376 | 1189302.2001 | 2622997.3742 | 1189297.8067 | 2623005.954 | 1189295.7941 | 2623012.314 | 1189293.8952 | 2623023.5921 | 1189290.2477 | 2623036.086 | 1189285.7932 | 2623050.8579 | 1189279.9358
36 | 2623127.2768 | 1189303.0086 | 2623130.4085 | 1189309.6576 | 2623133.7212 | 1189316.8297
37 | 2623127.2768 | 1189303.0086 | 2623145.2448 | 1189297.1131
38 | 2622698.5699 | 1189387.4386 | 2622698.9034 | 1189396.0222 | 2622699.139 | 1189414.3773 | 2622698.6086 | 1189419.5113 | 2622697.3544 | 1189426.488 | 2622695.5689 | 1189432.7957 | 2622692.5568 | 1189438.7875 | 2622690.1441 | 1189441.5576 | 2622678.0336 | 1189447.6373 | 2622669.9797 | 1189451.6539
39 | 2622629.1084 | 1189391.912 | 2622698.5699 | 1189387.4386
40 | 2623119.1753 | 1189323.4104 | 2623115.6911 | 1189325.109 | 2623113.6611 | 1189327.458 | 2623112.9806 | 1189329.89 | 2623115.1548 | 1189339.5924
41 | 2623119.1753 | 1189323.4104 | 2623133.7212 | 1189316.8297
42 | 2623178.8293 | 1189291.1919 | 2623153.5982 | 1189294.3722 | 2623145.2448 | 1189297.1131
43 | 2622629.1084 | 1189391.912 | 2622619.5597 | 1189396.8815
44 | 2622629.1084 | 1189391.912 | 2622618.6009 | 1189393.5622 | 2622610.5821 | 1189394.5102 | 2622598.493 | 1189395.7224
45 | 2622430.2223 | 1189458.9647 | 2622437.2549 | 1189455.1918 | 2622460.397 | 1189447.9412 | 2622471.1394 | 1189446.6585 | 2622479.7906 | 1189445.8127 | 2622487.8188 | 1189444.3642 | 2622494.0402 | 1189442.7533 | 2622501.6922 | 1189439.925 | 2622509.3709 | 1189436.0851 | 2622516.1122 | 1189432.0971 | 2622535.1687 | 1189418.2391 | 2622553.9998 | 1189405.5365 | 2622559.7389 | 1189402.4009 | 2622566.4125 | 1189400.1914 | 2622575.8842 | 1189398.1816 | 2622593.4853 | 1189396.2245 | 2622598.493 | 1189395.7224
46 | 2622669.9797 | 1189451.6539 | 2622659.1843 | 1189457.0377 | 2622657.8436 | 1189458.6668 | 2622656.7686 | 1189460.6082 | 2622656.7014 | 1189464.2766 | 2622657.3925 | 1189471.344
47 | 2622430.2223 | 1189458.9647 | 2622422.9119 | 1189462.8867 | 2622408.2686 | 1189469.2909 | 2622401.8813 | 1189470.4232 | 2622395.9585 | 1189469.7119 | 2622363.9985 | 1189463.2782 | 2622325.4129 | 1189456.3976 | 2622312.1376 | 1189451.8236 | 2622303.5057 | 1189445.4214 | 2622285.7971 | 1189425.056 | 2622270.0632 | 1189406.8658 | 2622266.9859 | 1189401.7516 | 2622266.4522 | 1189400.6778
48 | 2622266.4522 | 1189400.6778 | 2622264.4015 | 1189396.5513
49 | 2622259.0236 | 1189371.0837 | 2622259.0023 | 1189374.7633 | 2622259.9395 | 1189383.2046 | 2622263.1557 | 1189394.0445 | 2622264.4015 | 1189396.5513
50 | 2622062.3134 | 1189486.0034 | 2622075.7154 | 1189481.2894
51 | 2623186.7113 | 1189348.5566 | 2623187.3453 | 1189347.5195 | 2623187.2579 | 1189346.6183
52 | 2623185.1213 | 1189324.5958 | 2623187.2579 | 1189346.6183
53 | 2623159.2247 | 1189367.9217 | 2623181.996 | 1189356.2701 | 2623186.7113 | 1189348.5566
54 | 2623159.2247 | 1189367.9217 | 2623154.441 | 1189358.3384
55 | 2622062.3134 | 1189486.0034 | 2622060.4662 | 1189486.6532
56 | 2622060.4662 | 1189486.6532 | 2622049.0502 | 1189490.6686
57 | 2622935.8282 | 1189928.3045 | 2622948.3242 | 1189930.8981 | 2622957.2282 | 1189933.578 | 2622965.1287 | 1189937.4547 | 2622994.3348 | 1189959.2781
58 | 2622935.8282 | 1189928.3045 | 2622880.4303 | 1189921.1098
59 | 2623053.5806 | 1189706.4939 | 2623067.3641 | 1189711.5162 | 2623072.3211 | 1189719.3728 | 2623070.3554 | 1189730.8268 | 2623060.4742 | 1189758.1144 | 2623043.3164 | 1189783.851 | 2623035.4214 | 1189792.4141 | 2623027.1465 | 1189800.6089 | 2623024.2357 | 1189809.9582 | 2623021.3935 | 1189851.1246 | 2623018.2986 | 1189908.4431 | 2623015.5132 | 1189934.8019 | 2623007.221 | 1189947.5769 | 2622994.3348 | 1189959.2781
60 | 2622994.3348 | 1189959.2781 | 2623005.5934 | 1189972.317 | 2623007.5155 | 1189978.1386 | 2623040.0838 | 1189966.2906 | 2623077.6564 | 1189953.9618 | 2623132.7682 | 1189953.396 | 2623201.4953 | 1189971.582 | 2623268.2049 | 1190006.5255 | 2623298.5942 | 1190031.5789 | 2623317.4846 | 1190068.2495 | 2623329.2727 | 1190080.2128 | 2623344.9944 | 1190088.5005 | 2623364.7084 | 1190093.7467 | 2623382.3388 | 1190101.4195
61 | 2622880.4303 | 1189921.1098 | 2622838.8182 | 1189915.7056 | 2622829.7575 | 1189914.0925 | 2622823.6258 | 1189912.2793 | 2622818.0393 | 1189909.4788 | 2622816.0978 | 1189908.0452
62 | 2622883.4252 | 1189822.4373 | 2622899.2847 | 1189808.9684 | 2622907.111 | 1189794.3795
63 | 2622907.111 | 1189794.3795 | 2622907.5628 | 1189784.1196
64 | 2622883.4252 | 1189822.4373 | 2622881.6443 | 1189827.5221 | 2622878.9856 | 1189832.8036 | 2622874.277 | 1189837.7438 | 2622868.7278 | 1189841.7261
65 | 2622801.7334 | 1189884.0478 | 2622806.8457 | 1189883.2223 | 2622812.6422 | 1189880.9432 | 2622819.5277 | 1189877.0339 | 2622868.7278 | 1189841.7261
66 | 2622698.7215 | 1190218.6587 | 2622707.9577 | 1190215.2897 | 2622713.3439 | 1190212.5086 | 2622716.012 | 1190210.7066 | 2622718.5389 | 1190207.9036 | 2622719.3387 | 1190206.7597
67 | 2622698.7215 | 1190218.6587 | 2622695.8016 | 1190219.7238 | 2622691.8761 | 1190221.3543 | 2622689.8791 | 1190223.1588 | 2622684.4231 | 1190239.3146
68 | 2622675.2357 | 1190258.2331 | 2622682.2601 | 1190245.7197 | 2622684.4231 | 1190239.3146
69 | 2622675.2357 | 1190258.2331 | 2622694.9542 | 1190264.3109 | 2622714.6944 | 1190272.69 | 2622734.0248 | 1190286.5706 | 2622744.3367 | 1190295.9146
70 | 2622675.2357 | 1190258.2331 | 2622656.941 | 1190258.7754 | 2622632.1726 | 1190267.3754
71 | 2623314.9852 | 1190238.4522 | 2623331.8462 | 1190192.9158 | 2623327.316 | 1190181.381 | 2623324.3327 | 1190164.2047 | 2623324.6451 | 1190138.7814 | 2623332.9937 | 1190123.3834 | 2623342.3938 | 1190116.0383 | 2623361.3822 | 1190109.8089 | 2623382.3388 | 1190101.4195
72 | 2623382.3388 | 1190101.4195 | 2623398.0125 | 1190106.361 | 2623444.9865 | 1190133.1696 | 2623469.3309 | 1190151.5078 | 2623497.2152 | 1190155.7526 | 2623547.7929 | 1190152.0378 | 2623585.2696 | 1190156.3095 | 2623614.5201 | 1190144.6961 | 2623655.2894 | 1190143.5561 | 2623706.3311 | 1190134.4083 | 2623716.4122 | 1190132.3582
73 | 2623314.9852 | 1190238.4522 | 2623326.9085 | 1190239.0766
74 | 2623314.9852 | 1190238.4522 | 2623267.0781 | 1190245.859 | 2623183.302 | 1190269.1471 | 2623170.6861 | 1190272.1332 | 2623157.7174 | 1190273.6951 | 2623142.836 | 1190272.9484 | 2623142.8409 | 1190277.6287 | 2623141.7692 | 1190282.6606 | 2623139.2964 | 1190289.1767 | 2623135.0756 | 1190296.1752 | 2623122.5715 | 1190309.7453 | 2623103.9787 | 1190330.2846 | 2623098.4608 | 1190337.5005 | 2623085.4984 | 1190361.2299 | 2623083.2075 | 1190364.1003 | 2623080.5599 | 1190366.5248 | 2623066.1292 | 1190377.5418 | 2623061.7334 | 1190382.5053 | 2623059.4662 | 1190387.1212 | 2623058.1681 | 1190391.5853 | 2623057.4889 | 1190395.696 | 2623057.2482 | 1190400.7866 | 2623057.8534 | 1190406.0139 | 2623063.3091 | 1190428.8025 | 2623065.9688 | 1190443.0203 | 2623069.8282 | 1190466.5143 | 2623069.9938 | 1190473.0183
75 | 2623716.4122 | 1190132.3582 | 2623714.4018 | 1190113.1529
76 | 2623716.4122 | 1190132.3582 | 2623716.1747 | 1190142.2847
77 | 2623069.9938 | 1190473.0183 | 2623061.3319 | 1190482.9236
78 | 2622453.0638 | 1190400.4063 | 2622445.6655 | 1190396.899 | 2622431.4265 | 1190395.7118 | 2622414.9525 | 1190403.1763
79 | 2622453.0638 | 1190400.4063 | 2622459.9933 | 1190392.6726 | 2622466.5556 | 1190387.3276 | 2622483.317 | 1190376.6959 | 2622510.8006 | 1190361.6354 | 2622518.9242 | 1190356.7744 | 2622527.5113 | 1190350.3143 | 2622533.2257 | 1190345.3999 | 2622536.8456 | 1190341.856
80 | 2622632.1726 | 1190267.3754 | 2622629.1022 | 1190270.7545 | 2622627.1688 | 1190272.3047
81 | 2622536.8456 | 1190341.856 | 2622552.4228 | 1190325.8283 | 2622560.1201 | 1190318.7868 | 2622567.9059 | 1190312.5461 | 2622580.2832 | 1190303.9659 | 2622625.2245 | 1190273.8637 | 2622627.1688 | 1190272.3047
82 | 2622674.5533 | 1190061.582 | 2622675.1764 | 1190072.2456 | 2622673.8149 | 1190081.4231 | 2622671.4976 | 1190089.2629 | 2622659.1281 | 1190115.8191 | 2622656.7854 | 1190122.3359 | 2622656.1067 | 1190128.4144 | 2622660.1102 | 1190180.8128 | 2622660.2745 | 1190185.7716 | 2622659.7296 | 1190190.7388 | 2622657.6438 | 1190199.8913 | 2622644.4196 | 1190234.7932 | 2622636.0833 | 1190259.5527 | 2622634.4905 | 1190263.3709 | 2622632.1726 | 1190267.3754
83 | 2622536.8456 | 1190341.856 | 2622543.5377 | 1190349.2261
84 | 2622801.7334 | 1189884.0478 | 2622797.4699 | 1189884.2428 | 2622754.0828 | 1189879.5312 | 2622741.7545 | 1189878.9286 | 2622732.6026 | 1189879.2163 | 2622724.0124 | 1189882.2298 | 2622718.9477 | 1189886.5907 | 2622713.0458 | 1189894.5615 | 2622702.8532 | 1189920.0141 | 2622676.2007 | 1189966.7047 | 2622671.4251 | 1189977.3367 | 2622668.1365 | 1189987.9633 | 2622665.6989 | 1190003.4178 | 2622666.3466 | 1190021.6966 | 2622668.7117 | 1190039.5261 | 2622674.5533 | 1190061.582
85 | 2622674.5533 | 1190061.582 | 2622669.7896 | 1190061.0193 | 2622652.7609 | 1190059.3207 | 2622646.7691 | 1190074.9953 | 2622636.2016 | 1190111.0412 | 2622621.0235 | 1190138.3095 | 2622600.5251 | 1190150.8722 | 2622569.7448 | 1190178.4821 | 2622560.3861 | 1190189.8603
86 | 2622558.8441 | 1190364.0727 | 2622555.503 | 1190362.4037 | 2622543.5377 | 1190349.2261
87 | 2622801.7334 | 1189884.0478 | 2622805.9842 | 1189895.1809 | 2622809.3855 | 1189901.1304 | 2622813.4539 | 1189906.0929 | 2622816.0978 | 1189908.0452
88 | 2622560.3861 | 1190189.8603 | 2622535.6338 | 1190219.9536 | 2622521.255 | 1190237.6312 | 2622510.8216 | 1190242.3845
89 | 2622558.8441 | 1190364.0727 | 2622558.8441 | 1190364.0727 | 2622562.9147 | 1190364.3881 | 2622566.1957 | 1190363.8002 | 2622569.5052 | 1190361.7004 | 2622576.5698 | 1190356.4443
90 | 2622508.0357 | 1190243.6538 | 2622510.8216 | 1190242.3845
91 | 2623455.9297 | 1189848.4 | 2623460.6757 | 1189843.6554 | 2623460.9933 | 1189843.4144
92 | 2623455.9297 | 1189848.4 | 2623441.9885 | 1189862.3367 | 2623431.3461 | 1189863.518 | 2623421.8453 | 1189851.5844
93 | 2623584.9586 | 1189756.8838 | 2623589.4438 | 1189761.9615 | 2623591.3661 | 1189764.7488
94 | 2623597.2235 | 1189773.2425 | 2623591.3661 | 1189764.7488
95 | 2623597.2235 | 1189773.2425 | 2623604.1481 | 1189786.6991 | 2623641.2934 | 1189871.7237 | 2623657.8978 | 1189899.8596 | 2623684.3251 | 1189931.5362 | 2623707.6623 | 1189955.8523 | 2623710.1152 | 1189958.4078
96 | 2623710.1152 | 1189958.4078 | 2623704.516 | 1189968.5799 | 2623702.0541 | 1189983.7338 | 2623702.2313 | 1190000.6323 | 2623707.8006 | 1190050.0917 | 2623712.572 | 1190095.6723
97 | 2623710.1152 | 1189958.4078 | 2623707.6623 | 1189955.8523 | 2623710.6436 | 1189952.051 | 2623716.2025 | 1189948.2376
98 | 2623716.2025 | 1189948.2376 | 2623724.3446 | 1189956.4297 | 2623731.9058 | 1189963.0631 | 2623749.4193 | 1189977.1176 | 2623761.0486 | 1189984.7121 | 2623772.8915 | 1189988.4277 | 2623784.9528 | 1189990.9212 | 2623791.4921 | 1189991.7587 | 2623805.4233 | 1189991.9029 | 2623814.611 | 1189990.2274 | 2623828.5384 | 1189985.5913 | 2623842.0644 | 1189978.3079 | 2623860.3141 | 1189966.3519 | 2623889.4713 | 1189938.3308 | 2623895.4258 | 1189932.8405 | 2623901.3682 | 1189930.4185 | 2623906.6839 | 1189930.2396 | 2623912.4106 | 1189930.2624 | 2623920.9996 | 1189931.5195 | 2623937.9616 | 1189934.6444 | 2623950.0237 | 1189936.9382
99 | 2623987.656 | 1189936.8885 | 2623984.5854 | 1189936.2648 | 2623980.7172 | 1189932.9809 | 2623973.5715 | 1189929.2837 | 2623967.4347 | 1189928.8479 | 2623961.0971 | 1189929.0337 | 2623956.8108 | 1189931.1289 | 2623953.1247 | 1189933.7711 | 2623950.0237 | 1189936.9382
100 | 2623712.572 | 1190095.6723 | 2623714.4018 | 1190113.1529
101 | 2623020.132 | 1190769.6841 | 2622976.7331 | 1190749.885 | 2622946.4428 | 1190735.4503 | 2622934.9478 | 1190728.725 | 2622929.0964 | 1190723.6333 | 2622925.9523 | 1190718.3963 | 2622924.4021 | 1190711.0531 | 2622924.675 | 1190703.4724 | 2622926.697 | 1190695.0979 | 2622930.3194 | 1190688.9307 | 2622940.8133 | 1190678.3318 | 2622949.1015 | 1190670.2815 | 2622952.4724 | 1190666.0922 | 2622954.0985 | 1190661.5738 | 2622954.3706 | 1190656.2053 | 2622954.01 | 1190650.8344 | 2622953.0877 | 1190646.7732 | 2622951.4394 | 1190643.1538 | 2622949.1487 | 1190640.0212 | 2622947.5189 | 1190625.6957
102 | 2623020.132 | 1190769.6841 | 2623020.0239 | 1190791.8954
103 | 2623020.0239 | 1190791.8954 | 2623025.9277 | 1190799.1997 | 2623044.1319 | 1190811.8652 | 2623048.854 | 1190814.2498
104 | 2623048.854 | 1190814.2498 | 2623054.3365 | 1190817.0183 | 2623057.6426 | 1190817.7647 | 2623060.8227 | 1190817.5657 | 2623066.3276 | 1190815.6367
105 | 2623248.4374 | 1190711.2556 | 2623216.1261 | 1190726.5831 | 2623184.5326 | 1190737.7557 | 2623175.5963 | 1190741.79 | 2623145.2072 | 1190758.9818 | 2623127.9278 | 1190767.4864
106 | 2623127.9278 | 1190767.4864 | 2623120.708 | 1190777.2193 | 2623116.0473 | 1190783.727 | 2623110.5684 | 1190788.8419 | 2623103.2229 | 1190793.6162 | 2623090.8842 | 1190800.161 | 2623079.6502 | 1190806.9325 | 2623071.9312 | 1190813.673 | 2623066.3276 | 1190815.6367
107 | 2623248.4374 | 1190711.2556 | 2623252.3081 | 1190692.2495 | 2623254.5312 | 1190684.2675
108 | 2623217.4657 | 1190933.9427 | 2623222.7497 | 1190931.8732 | 2623238.7926 | 1190929.5563 | 2623248.2375 | 1190928.0032 | 2623248.986 | 1190909.9632 | 2623247.992 | 1190889.0593 | 2623246.446 | 1190868.9316 | 2623240.1728 | 1190819.3365 | 2623239.5896 | 1190802.6031 | 2623241.028 | 1190783.6098 | 2623248.4374 | 1190711.2556
109 | 2623716.1747 | 1190142.2847 | 2623715.6655 | 1190143.6244
110 | 2623642.7453 | 1190273.2643 | 2623647.3851 | 1190268.4467 | 2623652.45 | 1190260.2512 | 2623672.28 | 1190228.1791 | 2623712.9769 | 1190150.6988 | 2623715.6655 | 1190143.6244
111 | 2623642.7453 | 1190273.2643 | 2623620.031 | 1190284.6364 | 2623614.1785 | 1190287.5365
112 | 2623642.7453 | 1190273.2643 | 2623641.9553 | 1190278.2972 | 2623640.4736 | 1190290.5201 | 2623640.0188 | 1190303.3695 | 2623639.4378 | 1190317.5859
113 | 2623569.4161 | 1190309.7173 | 2623614.1785 | 1190287.5365
114 | 2623987.656 | 1189936.8885 | 2623980.823 | 1189940.8299 | 2623977.956 | 1189945.3624
115 | 2623964.5413 | 1189981.1974 | 2623965.6724 | 1189971.0298 | 2623973.479 | 1189952.4401 | 2623977.956 | 1189945.3624
116 | 2623935.7602 | 1190014.2889 | 2623947.1109 | 1189999.9266 | 2623952.8693 | 1189992.0009 | 2623955.001 | 1189983.3048 | 2623964.5413 | 1189981.1974
117 | 2623935.7602 | 1190014.2889 | 2623931.499 | 1190019.6747 | 2623921.1472 | 1190036.442
118 | 2623935.7602 | 1190014.2889 | 2623935.6518 | 1190028.205
119 | 2623869.2506 | 1190135.0768 | 2623870.2591 | 1190130.7563 | 2623875.2809 | 1190120.0929 | 2623881.0092 | 1190113.9124 | 2623888.2773 | 1190104.0583 | 2623897.3452 | 1190090.3205 | 2623904.6378 | 1190074.3188 | 2623911.3593 | 1190056.2138 | 2623918.0523 | 1190041.4549 | 2623921.1472 | 1190036.442
120 | 2623941.1557 | 1190044.4263 | 2623940.9934 | 1190044.3257 | 2623935.6038 | 1190034.3656 | 2623935.6518 | 1190028.205
121 | 2623878.7266 | 1190154.7916 | 2623875.736 | 1190151.3335 | 2623872.2801 | 1190146.0169 | 2623870.8821 | 1190142.8319 | 2623869.2506 | 1190135.0768
122 | 2623569.4161 | 1190309.7173 | 2623564.0886 | 1190303.2819 | 2623559.0501 | 1190297.0255 | 2623554.7235 | 1190292.0058
123 | 2623495.5479 | 1190388.6028 | 2623511.1515 | 1190356.747 | 2623517.1736 | 1190347.4434 | 2623522.7106 | 1190341.2952 | 2623528.7172 | 1190335.9715 | 2623546.1827 | 1190323.2666 | 2623569.4161 | 1190309.7173
124 | 2623878.7266 | 1190154.7916 | 2623879.812 | 1190156.0411 | 2623886.942 | 1190163.6068
125 | 2623554.7235 | 1190292.0058 | 2623558.8357 | 1190287.5418
126 | 2623554.7235 | 1190292.0058 | 2623545.7231 | 1190298.7904
127 | 2623495.5479 | 1190388.6028 | 2623500.0307 | 1190392.678 | 2623504.4651 | 1190397.3979 | 2623507.8576 | 1190403.4033 | 2623512.2903 | 1190416.3608 | 2623513.8664 | 1190432.4756 | 2623515.0149 | 1190452.6574 | 2623515.2547 | 1190473.1692
128 | 2623495.5479 | 1190388.6028 | 2623476.5649 | 1190418.9556 | 2623469.4142 | 1190434.158 | 2623465.7433 | 1190444.7381 | 2623459.4198 | 1190472.6726 | 2623457.2798 | 1190479.8014 | 2623455.593 | 1190484.1415 | 2623452.8407 | 1190487.955 | 2623449.3426 | 1190491.4209 | 2623441.4588 | 1190496.5311
129 | 2623515.2547 | 1190473.1692 | 2623515.3166 | 1190478.7613 | 2623519.686 | 1190489.3296
130 | 2623441.4588 | 1190496.5311 | 2623440.0855 | 1190497.4213 | 2623436.4253 | 1190499.5497
131 | 2623534.1629 | 1190508.5177 | 2623535.2728 | 1190513.2579 | 2623538.3175 | 1190517.5418
132 | 2623534.1629 | 1190508.5177 | 2623527.3769 | 1190498.7859 | 2623520.551 | 1190491.4219
133 | 2623520.551 | 1190491.4219 | 2623519.686 | 1190489.3296
134 | 2623268.1253 | 1190644.1075 | 2623271.7044 | 1190647.223 | 2623276.5848 | 1190652.9561 | 2623277.9444 | 1190654.5262
135 | 2623268.1253 | 1190644.1075 | 2623263.428 | 1190658.0077 | 2623256.1124 | 1190678.5903 | 2623254.5312 | 1190684.2675
136 | 2623268.1253 | 1190644.1075 | 2623275.0668 | 1190629.56 | 2623278.898 | 1190622.7268 | 2623283.3521 | 1190616.5186 | 2623289.8139 | 1190609.6622 | 2623335.3933 | 1190572.6975 | 2623397.1325 | 1190523.4007 | 2623413.6512 | 1190512.7929 | 2623436.4253 | 1190499.5497
137 | 2623190.2773 | 1190918.2515 | 2623200.5026 | 1190919.9252 | 2623206.8241 | 1190923.6183 | 2623214.7131 | 1190930.0856 | 2623217.4657 | 1190933.9427

## bus_geodata
| x | y | coords
0 | 2621938.8127 | 1189837.7852
1 | 2622222.4776 | 1189824.1876
2 | 2622293.9354 | 1189835.114
3 | 2622177.729 | 1189750.3336
4 | 2622310.6703 | 1189845.2941
5 | 2622024.2301 | 1189500.9083
6 | 2622123.85 | 1189403.6567
7 | 2622077.6417 | 1189480.6118
8 | 2622236.6893 | 1189375.3739
9 | 2623222.6265 | 1189430.0615
10 | 2623203.1975 | 1189417.3015
11 | 2623266.8299 | 1189460.6981
12 | 2623178.4971 | 1189395.3328
13 | 2623390.7083 | 1189603.6664
14 | 2623160.9431 | 1189370.3658
15 | 2623401.3502 | 1189581.2294
16 | 2623436.6542 | 1189556.5584
17 | 2623577.3726 | 1189748.2957
18 | 2623350.7905 | 1189641.7781
19 | 2623205.1449 | 1189288.3397
20 | 2623201.6152 | 1189288.4864
21 | 2623244.815 | 1189289.0332
22 | 2623193.5056 | 1189288.8234
23 | 2623248.9743 | 1189304.3408
24 | 2623186.3796 | 1189258.9122
25 | 2623181.8371 | 1189290.8127
26 | 2623258.8855 | 1189336.5881
27 | 2623050.8579 | 1189279.9358
28 | 2623127.2768 | 1189303.0086
29 | 2622698.5699 | 1189387.4386
30 | 2623119.1753 | 1189323.4104
31 | 2623115.1548 | 1189339.5924
32 | 2623133.7212 | 1189316.8297
33 | 2623145.2448 | 1189297.1131
34 | 2622619.5597 | 1189396.8815
35 | 2622629.1084 | 1189391.912
36 | 2622598.493 | 1189395.7224
37 | 2622669.9797 | 1189451.6539
38 | 2622430.2223 | 1189458.9647
39 | 2622313.9617 | 1189849.1605
40 | 2622264.4015 | 1189396.5513
41 | 2622266.4522 | 1189400.6778
42 | 2622259.0236 | 1189371.0837
43 | 2622075.7154 | 1189481.2894
44 | 2623187.2579 | 1189346.6183
45 | 2623186.7113 | 1189348.5566
46 | 2623185.1213 | 1189324.5958
47 | 2623159.2247 | 1189367.9217
48 | 2623154.441 | 1189358.3384
49 | 2623178.8293 | 1189291.1919
50 | 2622062.3134 | 1189486.0034
51 | 2622060.4662 | 1189486.6532
52 | 2622049.0502 | 1189490.6686
53 | 2623264.0463 | 1189348.6392
54 | 2622657.3925 | 1189471.344
55 | 2622935.8282 | 1189928.3045
56 | 2622994.3348 | 1189959.2781
57 | 2622880.4303 | 1189921.1098
58 | 2622907.111 | 1189794.3795
59 | 2622883.4252 | 1189822.4373
60 | 2622907.5628 | 1189784.1196
61 | 2622868.7278 | 1189841.7261
62 | 2622719.3387 | 1190206.7597
63 | 2622698.7215 | 1190218.6587
64 | 2622684.4231 | 1190239.3146
65 | 2622675.2357 | 1190258.2331
66 | 2623382.3388 | 1190101.4195
67 | 2623314.9852 | 1190238.4522
68 | 2623716.4122 | 1190132.3582
69 | 2623053.5806 | 1189706.4939
70 | 2623326.9085 | 1190239.0766
71 | 2623069.9938 | 1190473.0183
72 | 2623061.3319 | 1190482.9236
73 | 2622414.9525 | 1190403.1763
74 | 2622453.0638 | 1190400.4063
75 | 2622627.1688 | 1190272.3047
76 | 2622632.1726 | 1190267.3754
77 | 2622536.8456 | 1190341.856
78 | 2622674.5533 | 1190061.582
79 | 2622543.5377 | 1190349.2261
80 | 2622744.3367 | 1190295.9146
81 | 2622801.7334 | 1189884.0478
82 | 2622560.3861 | 1190189.8603
83 | 2622558.8441 | 1190364.0727
84 | 2622576.5698 | 1190356.4443
85 | 2622510.8216 | 1190242.3845
86 | 2622508.0357 | 1190243.6538
87 | 2622816.0978 | 1189908.0452
88 | 2623455.9297 | 1189848.4
89 | 2623460.9933 | 1189843.4144
90 | 2623421.8453 | 1189851.5844
91 | 2623584.9586 | 1189756.8838
92 | 2623591.3661 | 1189764.7488
93 | 2623597.2235 | 1189773.2425
94 | 2623710.1152 | 1189958.4078
95 | 2623716.2025 | 1189948.2376
96 | 2623950.0237 | 1189936.9382
97 | 2623339.3897 | 1189647.6565
98 | 2623712.572 | 1190095.6723
99 | 2622947.5189 | 1190625.6957
100 | 2623020.132 | 1190769.6841
101 | 2623020.0239 | 1190791.8954
102 | 2623048.854 | 1190814.2498
103 | 2623127.9278 | 1190767.4864
104 | 2623248.4374 | 1190711.2556
105 | 2623066.3276 | 1190815.6367
106 | 2623716.1747 | 1190142.2847
107 | 2623715.6655 | 1190143.6244
108 | 2623642.7453 | 1190273.2643
109 | 2623714.4018 | 1190113.1529
110 | 2623614.1785 | 1190287.5365
111 | 2623639.4378 | 1190317.5859
112 | 2623987.656 | 1189936.8885
113 | 2623977.956 | 1189945.3624
114 | 2623964.5413 | 1189981.1974
115 | 2623935.7602 | 1190014.2889
116 | 2623921.1472 | 1190036.442
117 | 2623935.6518 | 1190028.205
118 | 2623941.1557 | 1190044.4263
119 | 2623869.2506 | 1190135.0768
120 | 2623569.4161 | 1190309.7173
121 | 2623878.7266 | 1190154.7916
122 | 2623886.942 | 1190163.6068
123 | 2623554.7235 | 1190292.0058
124 | 2623495.5479 | 1190388.6028
125 | 2623558.8357 | 1190287.5418
126 | 2623545.7231 | 1190298.7904
127 | 2623515.2547 | 1190473.1692
128 | 2623441.4588 | 1190496.5311
129 | 2623538.3175 | 1190517.5418
130 | 2623534.1629 | 1190508.5177
131 | 2623520.551 | 1190491.4219
132 | 2623519.686 | 1190489.3296
133 | 2623277.9444 | 1190654.5262
134 | 2623268.1253 | 1190644.1075
135 | 2623254.5312 | 1190684.2675
136 | 2623436.4253 | 1190499.5497
137 | 2623217.4657 | 1190933.9427
138 | 2623190.2773 | 1190918.2515
139 | 2623159.2247 | 1189367.9217

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1