## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_907-7_1_2_node_41 | 0.4 | n |  | TRUE
1 | bus_LV_907-7_1_2_node_42 | 0.4 | n |  | TRUE
2 | bus_LV_907-7_1_2_node_43 | 0.4 | n |  | TRUE
3 | bus_LV_907-7_1_2_node_44 | 0.4 | n |  | TRUE
4 | bus_LV_907-7_1_2_node_45 | 0.4 | n |  | TRUE
5 | bus_LV_907-7_1_2_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_907-7_1_2_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_907-7_1_2_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_907-7_1_2_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_907-7_1_2_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_907-7_1_2_node_49 | 0.4 | n |  | TRUE
11 | bus_LV_907-7_1_2_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_907-7_1_2_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_907-7_1_2_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_907-7_1_2_node_58 | 0.4 | n |  | TRUE
15 | bus_LV_907-7_1_2_node_106 | 0.4 | n |  | TRUE
16 | bus_LV_907-7_1_2_node_55 | 0.4 | n |  | TRUE
17 | bus_LV_907-7_1_2_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_907-7_1_2_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_907-7_1_2_node_59 | 0.4 | n |  | TRUE
20 | bus_LV_907-7_1_2_node_60 | 0.4 | n |  | TRUE
21 | bus_LV_907-7_1_2_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_907-7_1_2_node_62 | 0.4 | n |  | TRUE
23 | bus_LV_907-7_1_2_node_63 | 0.4 | n |  | TRUE
24 | bus_LV_907-7_1_2_node_64 | 0.4 | n |  | TRUE
25 | bus_LV_907-7_1_2_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_907-7_1_2_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_907-7_1_2_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_907-7_1_2_node_68 | 0.4 | n |  | TRUE
29 | bus_LV_907-7_1_2_node_71 | 0.4 | n |  | TRUE
30 | bus_LV_907-7_1_2_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_907-7_1_2_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_907-7_1_2_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_907-7_1_2_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_907-7_1_2_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_907-7_1_2_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_907-7_1_2_node_76 | 0.4 | n |  | TRUE
37 | bus_LV_907-7_1_2_node_77 | 0.4 | n |  | TRUE
38 | bus_LV_907-7_1_2_node_105 | 0.4 | n |  | TRUE
39 | bus_LV_907-7_1_2_node_103 | 0.4 | n |  | TRUE
40 | bus_LV_907-7_1_2_node_97 | 0.4 | n |  | TRUE
41 | bus_LV_907-7_1_2_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_907-7_1_2_node_99 | 0.4 | n |  | TRUE
43 | bus_LV_907-7_1_2_node_100 | 0.4 | n |  | TRUE
44 | bus_LV_907-7_1_2_node_101 | 0.4 | n |  | TRUE
45 | bus_LV_907-7_1_2_node_104 | 0.4 | n |  | TRUE
46 | bus_LV_907-7_1_2_node_114 | 0.4 | n |  | TRUE
47 | bus_LV_907-7_1_2_node_107 | 0.4 | n |  | TRUE
48 | bus_LV_907-7_1_2_node_108 | 0.4 | n |  | TRUE
49 | bus_LV_907-7_1_2_node_109 | 0.4 | n |  | TRUE
50 | bus_LV_907-7_1_2_node_110 | 0.4 | n |  | TRUE
51 | bus_LV_907-7_1_2_node_111 | 0.4 | n |  | TRUE
52 | bus_LV_907-7_1_2_node_112 | 0.4 | n |  | TRUE
53 | bus_LV_907-7_1_2_node_113 | 0.4 | n |  | TRUE
54 | bus_LV_907-7_1_2_node_115 | 0.4 | n |  | TRUE
55 | bus_MV_199_0_node_203 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_907-7_1_2_load_41 | 0 | 0.013031 | 0.0032659 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_907-7_1_2_load_42 | 1 | 0.0024257 | 0.00060794 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_907-7_1_2_load_44 | 3 | 0.0026988 | 0.00067639 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_907-7_1_2_load_45 | 4 | 0.0014213 | 0.0003562 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_907-7_1_2_load_46 | 5 | 0.0013034 | 0.00032665 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_907-7_1_2_load_47 | 6 | 0.0041979 | 0.0010521 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_907-7_1_2_load_48 | 7 | 0.00095153 | 0.00023848 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_907-7_1_2_load_54 | 8 | 0.0038297 | 0.00095981 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_907-7_1_2_load_51 | 9 | 0.00094953 | 0.00023798 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_907-7_1_2_load_49 | 10 | 0.002423 | 0.00060727 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_907-7_1_2_load_50 | 11 | 0.0023727 | 0.00059465 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_907-7_1_2_load_52 | 12 | 0.00094579 | 0.00023704 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_907-7_1_2_load_53 | 13 | 0.0024096 | 0.0006039 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_907-7_1_2_load_58 | 14 | 0.00094688 | 0.00023731 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_907-7_1_2_load_106 | 15 | 0.0051164 | 0.0012823 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_907-7_1_2_load_55 | 16 | 0.0021392 | 0.00053613 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_907-7_1_2_load_56 | 17 | 0.0020525 | 0.00051439 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_907-7_1_2_load_60 | 20 | 0.0020982 | 0.00052586 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_907-7_1_2_load_61 | 21 | 0.0053545 | 0.001342 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_907-7_1_2_load_62 | 22 | 0.0018784 | 0.00047078 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_907-7_1_2_load_63 | 23 | 0.002147 | 0.00053808 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_907-7_1_2_load_64 | 24 | 0.002609 | 0.00065387 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_907-7_1_2_load_65 | 25 | 0.0024141 | 0.00060503 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_907-7_1_2_load_66 | 26 | 0.00075604 | 0.00018948 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_907-7_1_2_load_68 | 28 | 0.0013302 | 0.00033337 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_907-7_1_2_load_70 | 30 | 0.0013902 | 0.00034842 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_907-7_1_2_load_78 | 31 | 0.0014533 | 0.00036422 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_907-7_1_2_load_80 | 32 | 0.00023137 | 5.7987e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_907-7_1_2_load_74 | 34 | 0.00078255 | 0.00019613 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_907-7_1_2_load_75 | 35 | 0.00060514 | 0.00015166 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_907-7_1_2_load_76 | 36 | 0.00035752 | 8.9602e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_907-7_1_2_load_77 | 37 | 0.0010948 | 0.0002744 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_907-7_1_2_load_105 | 38 | 0.0022536 | 0.0005648 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_907-7_1_2_load_97 | 40 | 0.00063143 | 0.00015825 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_907-7_1_2_load_98 | 41 | 0.0004922 | 0.00012336 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_907-7_1_2_load_100 | 43 | 0.00020554 | 5.1512e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_907-7_1_2_load_101 | 44 | 0.0012251 | 0.00030704 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_907-7_1_2_load_104 | 45 | 0.00023509 | 5.8918e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_907-7_1_2_load_107 | 47 | 0.00081364 | 0.00020392 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_907-7_1_2_load_108 | 48 | 0.0010316 | 0.00025855 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_907-7_1_2_load_110 | 50 | 0.00032193 | 8.0684e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_907-7_1_2_load_111 | 51 | 0.001224 | 0.00030677 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_907-7_1_2_load_112 | 52 | 0.00026961 | 6.7571e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_907-7_1_2_load_113 | 53 | 0.00038741 | 9.7094e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_907-7_1_2_load_115 | 54 | 0.00080513 | 0.00020179 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_907-7_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.030106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_907-7_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.12355 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_907-7_1_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0024037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_907-7_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.082862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_907-7_1_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.012133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_907-7_1_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.048358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_907-7_1_2_line_6 | NAYY 4x150 SE | 4 | 7 | 0.022127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_907-7_1_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.026784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_907-7_1_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.0066603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_907-7_1_2_line_9 | NAYY 4x150 SE | 8 | 15 | 0.025847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_907-7_1_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.011876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_907-7_1_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.0059066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_907-7_1_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.0018677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_907-7_1_2_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0040007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_907-7_1_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.0033941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_907-7_1_2_line_15 | NAYY 4x150 SE | 14 | 17 | 0.008649 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_907-7_1_2_line_16 | NAYY 4x150 SE | 15 | 47 | 0.22236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_907-7_1_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.01535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_907-7_1_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.011906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_907-7_1_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.014645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_907-7_1_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.012835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_907-7_1_2_line_21 | NAYY 4x150 SE | 19 | 21 | 0.045909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_907-7_1_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.018958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_907-7_1_2_line_23 | NAYY 4x150 SE | 20 | 23 | 0.0061933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_907-7_1_2_line_24 | NAYY 4x150 SE | 21 | 24 | 0.011626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_907-7_1_2_line_25 | NAYY 4x150 SE | 24 | 25 | 0.012628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_907-7_1_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.014717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_907-7_1_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.1492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_907-7_1_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.041166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_907-7_1_2_line_29 | NAYY 4x150 SE | 27 | 29 | 0.23522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_907-7_1_2_line_30 | NAYY 4x150 SE | 28 | 30 | 0.023826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_907-7_1_2_line_31 | NAYY 4x150 SE | 29 | 32 | 0.062819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_907-7_1_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.03731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_907-7_1_2_line_33 | NAYY 4x150 SE | 32 | 40 | 0.0011875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_907-7_1_2_line_34 | NAYY 4x150 SE | 33 | 34 | 0.055191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_907-7_1_2_line_35 | NAYY 4x150 SE | 33 | 35 | 0.018066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_907-7_1_2_line_36 | NAYY 4x150 SE | 34 | 36 | 0.0052182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_907-7_1_2_line_37 | NAYY 4x150 SE | 35 | 37 | 0.032208 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_907-7_1_2_line_38 | NAYY 4x150 SE | 36 | 38 | 0.17479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_907-7_1_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.017372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_907-7_1_2_line_40 | NAYY 4x150 SE | 38 | 46 | 0.25243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_907-7_1_2_line_41 | NAYY 4x150 SE | 39 | 45 | 0.045484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_907-7_1_2_line_42 | NAYY 4x150 SE | 40 | 41 | 0.00053499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_907-7_1_2_line_43 | NAYY 4x150 SE | 41 | 42 | 0.22175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_907-7_1_2_line_44 | NAYY 4x150 SE | 42 | 43 | 0.039481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_907-7_1_2_line_45 | NAYY 4x150 SE | 43 | 44 | 0.028698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_907-7_1_2_line_46 | NAYY 4x150 SE | 46 | 54 | 0.002381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_907-7_1_2_line_47 | NAYY 4x150 SE | 46 | 53 | 0.032557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_907-7_1_2_line_48 | NAYY 4x150 SE | 47 | 48 | 0.0056587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_907-7_1_2_line_49 | NAYY 4x150 SE | 48 | 49 | 0.048824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_907-7_1_2_line_50 | NAYY 4x150 SE | 49 | 50 | 0.20021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_907-7_1_2_line_51 | NAYY 4x150 SE | 50 | 51 | 0.022857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_907-7_1_2_line_52 | NAYY 4x150 SE | 51 | 52 | 0.019881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_907-7_1_2_line_53 | NAYY 4x150 SE | 52 | 53 | 0.0084051 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_907-7_1_2_trafo_41 | 0.25 MVA 20/0.4 kV | 55 | 0 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2622152.2041 | 1197441.9438 | 2622175.8993 | 1197460.5163
1 | 2622052.9749 | 1197374.7138 | 2622053.3951 | 1197382.6419 | 2622062.0125 | 1197389.9219 | 2622093.2993 | 1197408.4583 | 2622140.4973 | 1197432.7678 | 2622152.2041 | 1197441.9438
2 | 2622175.8993 | 1197460.5163 | 2622177.7911 | 1197461.9992 | 2622177.7911 | 1197461.9992
3 | 2622052.9749 | 1197374.7138 | 2622057.4172 | 1197372.0732 | 2622066.3621 | 1197373.14 | 2622084.548 | 1197381.745 | 2622094.6384 | 1197384.0278 | 2622122.9867 | 1197389.8355 | 2622132.008 | 1197392.0304
4 | 2622052.9749 | 1197374.7138 | 2622043.6198 | 1197373.3453 | 2622040.9417 | 1197373.3355
5 | 2622173.3496 | 1197500.759 | 2622180.7076 | 1197497.0622 | 2622186.5026 | 1197486.9894 | 2622188.1422 | 1197476.1118 | 2622177.7911 | 1197461.9992
6 | 2622153.7158 | 1197396.1447 | 2622143.4022 | 1197394.8025 | 2622132.008 | 1197392.0304
7 | 2622149.4164 | 1197512.7831 | 2622173.3496 | 1197500.759
8 | 2622153.7158 | 1197396.1447 | 2622160.3205 | 1197397.0042
9 | 2622126.3201 | 1197524.3867 | 2622149.4164 | 1197512.7831
10 | 2622172.0974 | 1197398.5368 | 2622160.3205 | 1197397.0042
11 | 2622172.0974 | 1197398.5368 | 2622177.9547 | 1197399.299
12 | 2622179.8067 | 1197399.5401 | 2622177.9547 | 1197399.299
13 | 2622179.8067 | 1197399.5401 | 2622183.7739 | 1197400.0563
14 | 2622183.7739 | 1197400.0563 | 2622185.2549 | 1197400.2491 | 2622187.1519 | 1197400.3668
15 | 2622195.7842 | 1197400.9023 | 2622187.1519 | 1197400.3668
16 | 2622126.3201 | 1197524.3867 | 2622058.0232 | 1197735.9956
17 | 2622211.0975 | 1197401.0996 | 2622205.8363 | 1197401.526 | 2622195.7842 | 1197400.9023
18 | 2622222.4527 | 1197397.8745 | 2622214.7573 | 1197400.8031 | 2622211.0975 | 1197401.0996
19 | 2622222.4527 | 1197397.8745 | 2622235.0925 | 1197390.4173
20 | 2622222.4527 | 1197397.8745 | 2622230.4131 | 1197407.9427
21 | 2622235.0925 | 1197390.4173 | 2622233.6722 | 1197389.3893 | 2622227.0032 | 1197384.5619 | 2622194.6244 | 1197369.0039
22 | 2622235.0925 | 1197390.4173 | 2622244.804 | 1197383.9832 | 2622249.4654 | 1197378.3539
23 | 2622230.4131 | 1197407.9427 | 2622234.2542 | 1197412.8009
24 | 2622194.6244 | 1197369.0039 | 2622191.1194 | 1197367.3197 | 2622183.5146 | 1197365.8938
25 | 2622171.1029 | 1197363.5666 | 2622183.5146 | 1197365.8938
26 | 2622171.1029 | 1197363.5666 | 2622160.0902 | 1197361.5018 | 2622156.6378 | 1197360.8535
27 | 2622019.7472 | 1197306.0435 | 2622026.4016 | 1197308.6694 | 2622036.2134 | 1197312.2185 | 2622050.4307 | 1197318.9744 | 2622070.7258 | 1197331.8894 | 2622092.327 | 1197345.8209 | 2622122.5234 | 1197354.4481 | 2622156.6378 | 1197360.8535
28 | 2622019.7472 | 1197306.0435 | 2622020.5401 | 1197316.1741 | 2622035.885 | 1197324.8908 | 2622047.1113 | 1197332.1267
29 | 2622019.7472 | 1197306.0435 | 2621785.4595 | 1197285.1429
30 | 2622047.1113 | 1197332.1267 | 2622062.1135 | 1197341.7964 | 2622067.283 | 1197344.7972
31 | 2621785.4595 | 1197285.1429 | 2621782.6708 | 1197302.2086 | 2621776.926 | 1197313.3159 | 2621762.2485 | 1197324.1351 | 2621750.2182 | 1197332.7343
32 | 2622096.7761 | 1197366.1149 | 2622093.896 | 1197360.2456 | 2622067.283 | 1197344.7972
33 | 2621750.2182 | 1197332.7343 | 2621749.2521 | 1197333.4249
34 | 2621541.0071 | 1197629.4228 | 2621556.7286 | 1197624.4544 | 2621581.3061 | 1197604.999 | 2621588.6628 | 1197605.0255
35 | 2621541.0071 | 1197629.4228 | 2621523.7799 | 1197634.8621
36 | 2621588.6628 | 1197605.0255 | 2621591.9153 | 1197609.1061
37 | 2621493.0664 | 1197644.5597 | 2621523.7799 | 1197634.8621
38 | 2621591.9153 | 1197609.1061 | 2621751.3268 | 1197680.7878
39 | 2621476.1377 | 1197648.189 | 2621485.9669 | 1197646.8013 | 2621493.0664 | 1197644.5597
40 | 2621817.1981 | 1197924.4698 | 2621751.3268 | 1197680.7878
41 | 2621476.1377 | 1197648.189 | 2621473.9368 | 1197643.9344 | 2621470.884 | 1197641.4888 | 2621461.4988 | 1197637.9866 | 2621449.2416 | 1197638.9655 | 2621435.5239 | 1197643.5655
42 | 2621749.2521 | 1197333.4249 | 2621748.8169 | 1197333.736
43 | 2621748.8169 | 1197333.736 | 2621527.158 | 1197327.3658
44 | 2621527.158 | 1197327.3658 | 2621495.6581 | 1197351.1666
45 | 2621470.7467 | 1197365.2839 | 2621478.436 | 1197361.8651 | 2621494.1365 | 1197352.3163 | 2621495.6581 | 1197351.1666
46 | 2621817.1981 | 1197924.4698 | 2621815.0487 | 1197925.4939
47 | 2621817.1981 | 1197924.4698 | 2621838.555 | 1197917.2548 | 2621848.2376 | 1197914.7001
48 | 2622058.0232 | 1197735.9956 | 2622053.7475 | 1197739.7023
49 | 2622055.8587 | 1197776.7524 | 2622050.2155 | 1197772.6405 | 2622044.1076 | 1197768.5492 | 2622040.0496 | 1197759.9741 | 2622043.3511 | 1197750.6256 | 2622052.3809 | 1197740.8869 | 2622053.7475 | 1197739.7023
50 | 2621896.1434 | 1197897.4799 | 2622055.8587 | 1197776.7524
51 | 2621896.1434 | 1197897.4799 | 2621890.2086 | 1197900.9677 | 2621875.4526 | 1197907.083
52 | 2621875.4526 | 1197907.083 | 2621872.5522 | 1197908.285 | 2621856.3646 | 1197912.5559
53 | 2621856.3646 | 1197912.5559 | 2621848.2376 | 1197914.7001

## bus_geodata
| x | y | coords
0 | 2622152.2041 | 1197441.9438
1 | 2622175.8993 | 1197460.5163
2 | 2622052.9749 | 1197374.7138
3 | 2622177.7911 | 1197461.9992
4 | 2622132.008 | 1197392.0304
5 | 2622040.9417 | 1197373.3355
6 | 2622173.3496 | 1197500.759
7 | 2622153.7158 | 1197396.1447
8 | 2622149.4164 | 1197512.7831
9 | 2622160.3205 | 1197397.0042
10 | 2622172.0974 | 1197398.5368
11 | 2622177.9547 | 1197399.299
12 | 2622179.8067 | 1197399.5401
13 | 2622183.7739 | 1197400.0563
14 | 2622187.1519 | 1197400.3668
15 | 2622126.3201 | 1197524.3867
16 | 2622211.0975 | 1197401.0996
17 | 2622195.7842 | 1197400.9023
18 | 2622222.4527 | 1197397.8745
19 | 2622235.0925 | 1197390.4173
20 | 2622230.4131 | 1197407.9427
21 | 2622194.6244 | 1197369.0039
22 | 2622249.4654 | 1197378.3539
23 | 2622234.2542 | 1197412.8009
24 | 2622183.5146 | 1197365.8938
25 | 2622171.1029 | 1197363.5666
26 | 2622156.6378 | 1197360.8535
27 | 2622019.7472 | 1197306.0435
28 | 2622047.1113 | 1197332.1267
29 | 2621785.4595 | 1197285.1429
30 | 2622067.283 | 1197344.7972
31 | 2622096.7761 | 1197366.1149
32 | 2621750.2182 | 1197332.7343
33 | 2621541.0071 | 1197629.4228
34 | 2621588.6628 | 1197605.0255
35 | 2621523.7799 | 1197634.8621
36 | 2621591.9153 | 1197609.1061
37 | 2621493.0664 | 1197644.5597
38 | 2621751.3268 | 1197680.7878
39 | 2621476.1377 | 1197648.189
40 | 2621749.2521 | 1197333.4249
41 | 2621748.8169 | 1197333.736
42 | 2621527.158 | 1197327.3658
43 | 2621495.6581 | 1197351.1666
44 | 2621470.7467 | 1197365.2839
45 | 2621435.5239 | 1197643.5655
46 | 2621817.1981 | 1197924.4698
47 | 2622058.0232 | 1197735.9956
48 | 2622053.7475 | 1197739.7023
49 | 2622055.8587 | 1197776.7524
50 | 2621896.1434 | 1197897.4799
51 | 2621875.4526 | 1197907.083
52 | 2621856.3646 | 1197912.5559
53 | 2621848.2376 | 1197914.7001
54 | 2621815.0487 | 1197925.4939
55 | 2622052.9749 | 1197374.7138

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1