## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_957-15_1_5_node_11 | 0.4 | n |  | TRUE
1 | bus_LV_957-15_1_5_node_27 | 0.4 | n |  | TRUE
2 | bus_LV_957-15_1_5_node_24 | 0.4 | n |  | TRUE
3 | bus_LV_957-15_1_5_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_957-15_1_5_node_109 | 0.4 | n |  | TRUE
5 | bus_LV_957-15_1_5_node_106 | 0.4 | n |  | TRUE
6 | bus_LV_957-15_1_5_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_957-15_1_5_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_957-15_1_5_node_66 | 0.4 | n |  | TRUE
9 | bus_LV_957-15_1_5_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_957-15_1_5_node_70 | 0.4 | n |  | TRUE
11 | bus_LV_957-15_1_5_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_957-15_1_5_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_957-15_1_5_node_80 | 0.4 | n |  | TRUE
14 | bus_LV_957-15_1_5_node_77 | 0.4 | n |  | TRUE
15 | bus_LV_957-15_1_5_node_56 | 0.4 | n |  | TRUE
16 | bus_LV_957-15_1_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_957-15_1_5_node_84 | 0.4 | n |  | TRUE
18 | bus_LV_957-15_1_5_node_152 | 0.4 | n |  | TRUE
19 | bus_LV_957-15_1_5_node_83 | 0.4 | n |  | TRUE
20 | bus_LV_957-15_1_5_node_82 | 0.4 | n |  | TRUE
21 | bus_LV_957-15_1_5_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_957-15_1_5_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_957-15_1_5_node_102 | 0.4 | n |  | TRUE
24 | bus_LV_957-15_1_5_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_957-15_1_5_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_957-15_1_5_node_110 | 0.4 | n |  | TRUE
27 | bus_LV_957-15_1_5_node_98 | 0.4 | n |  | TRUE
28 | bus_LV_957-15_1_5_node_159 | 0.4 | n |  | TRUE
29 | bus_LV_957-15_1_5_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_957-15_1_5_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_957-15_1_5_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_957-15_1_5_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_957-15_1_5_node_75 | 0.4 | n |  | TRUE
34 | bus_LV_957-15_1_5_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_957-15_1_5_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_957-15_1_5_node_73 | 0.4 | n |  | TRUE
37 | bus_LV_957-15_1_5_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_957-15_1_5_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_957-15_1_5_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_957-15_1_5_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_957-15_1_5_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_957-15_1_5_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_957-15_1_5_node_86 | 0.4 | n |  | TRUE
44 | bus_LV_957-15_1_5_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_957-15_1_5_node_74 | 0.4 | n |  | TRUE
46 | bus_LV_957-15_1_5_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_957-15_1_5_node_53 | 0.4 | n |  | TRUE
48 | bus_LV_957-15_1_5_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_957-15_1_5_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_957-15_1_5_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_957-15_1_5_node_147 | 0.4 | n |  | TRUE
52 | bus_LV_957-15_1_5_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_957-15_1_5_node_132 | 0.4 | n |  | TRUE
54 | bus_LV_957-15_1_5_node_129 | 0.4 | n |  | TRUE
55 | bus_LV_957-15_1_5_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_957-15_1_5_node_151 | 0.4 | n |  | TRUE
57 | bus_LV_957-15_1_5_node_149 | 0.4 | n |  | TRUE
58 | bus_LV_957-15_1_5_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_957-15_1_5_node_139 | 0.4 | n |  | TRUE
60 | bus_LV_957-15_1_5_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_957-15_1_5_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_957-15_1_5_node_164 | 0.4 | n |  | TRUE
63 | bus_LV_957-15_1_5_node_133 | 0.4 | n |  | TRUE
64 | bus_LV_957-15_1_5_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_957-15_1_5_node_144 | 0.4 | n |  | TRUE
66 | bus_LV_957-15_1_5_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_957-15_1_5_node_87 | 0.4 | n |  | TRUE
68 | bus_LV_957-15_1_5_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_957-15_1_5_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_957-15_1_5_node_99 | 0.4 | n |  | TRUE
71 | bus_LV_957-15_1_5_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_957-15_1_5_node_123 | 0.4 | n |  | TRUE
73 | bus_LV_957-15_1_5_node_124 | 0.4 | n |  | TRUE
74 | bus_LV_957-15_1_5_node_122 | 0.4 | n |  | TRUE
75 | bus_LV_957-15_1_5_node_148 | 0.4 | n |  | TRUE
76 | bus_LV_957-15_1_5_node_130 | 0.4 | n |  | TRUE
77 | bus_LV_957-15_1_5_node_150 | 0.4 | n |  | TRUE
78 | bus_LV_957-15_1_5_node_131 | 0.4 | n |  | TRUE
79 | bus_LV_957-15_1_5_node_154 | 0.4 | n |  | TRUE
80 | bus_LV_957-15_1_5_node_155 | 0.4 | n |  | TRUE
81 | bus_LV_957-15_1_5_node_156 | 0.4 | n |  | TRUE
82 | bus_LV_957-15_1_5_node_153 | 0.4 | n |  | TRUE
83 | bus_LV_957-15_1_5_node_161 | 0.4 | n |  | TRUE
84 | bus_LV_957-15_1_5_node_163 | 0.4 | n |  | TRUE
85 | bus_LV_957-15_1_5_node_101 | 0.4 | n |  | TRUE
86 | bus_LV_957-15_1_5_node_121 | 0.4 | n |  | TRUE
87 | bus_LV_957-15_1_5_node_143 | 0.4 | n |  | TRUE
88 | bus_LV_957-15_1_5_node_55 | 0.4 | n |  | TRUE
89 | bus_LV_957-15_1_5_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_957-15_1_5_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_957-15_1_5_node_96 | 0.4 | n |  | TRUE
92 | bus_LV_957-15_1_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_957-15_1_5_node_97 | 0.4 | n |  | TRUE
94 | bus_LV_957-15_1_5_node_57 | 0.4 | n |  | TRUE
95 | bus_LV_957-15_1_5_node_58 | 0.4 | n |  | TRUE
96 | bus_LV_957-15_1_5_node_59 | 0.4 | n |  | TRUE
97 | bus_LV_957-15_1_5_node_60 | 0.4 | n |  | TRUE
98 | bus_LV_957-15_1_5_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_957-15_1_5_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_957-15_1_5_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_957-15_1_5_node_61 | 0.4 | n |  | TRUE
102 | bus_LV_957-15_1_5_node_62 | 0.4 | n |  | TRUE
103 | bus_LV_957-15_1_5_node_64 | 0.4 | n |  | TRUE
104 | bus_LV_957-15_1_5_node_65 | 0.4 | n |  | TRUE
105 | bus_LV_957-15_1_5_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_957-15_1_5_node_72 | 0.4 | n |  | TRUE
107 | bus_LV_957-15_1_5_node_92 | 0.4 | n |  | TRUE
108 | bus_LV_957-15_1_5_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_957-15_1_5_node_79 | 0.4 | n |  | TRUE
110 | bus_LV_957-15_1_5_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_957-15_1_5_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_957-15_1_5_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_957-15_1_5_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_957-15_1_5_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_957-15_1_5_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_957-15_1_5_node_158 | 0.4 | n |  | TRUE
117 | bus_LV_957-15_1_5_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_957-15_1_5_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_957-15_1_5_node_113 | 0.4 | n |  | TRUE
120 | bus_LV_957-15_1_5_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_957-15_1_5_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_957-15_1_5_node_135 | 0.4 | n |  | TRUE
123 | bus_LV_957-15_1_5_node_136 | 0.4 | n |  | TRUE
124 | bus_LV_957-15_1_5_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_957-15_1_5_node_120 | 0.4 | n |  | TRUE
126 | bus_LV_957-15_1_5_node_116 | 0.4 | n |  | TRUE
127 | bus_LV_957-15_1_5_node_134 | 0.4 | n |  | TRUE
128 | bus_LV_957-15_1_5_node_117 | 0.4 | n |  | TRUE
129 | bus_LV_957-15_1_5_node_119 | 0.4 | n |  | TRUE
130 | bus_LV_957-15_1_5_node_145 | 0.4 | n |  | TRUE
131 | bus_LV_957-15_1_5_node_127 | 0.4 | n |  | TRUE
132 | bus_LV_957-15_1_5_node_128 | 0.4 | n |  | TRUE
133 | bus_LV_957-15_1_5_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_957-15_1_5_node_146 | 0.4 | n |  | TRUE
135 | bus_LV_957-15_1_5_node_137 | 0.4 | n |  | TRUE
136 | bus_LV_957-15_1_5_node_126 | 0.4 | n |  | TRUE
137 | bus_LV_957-15_1_5_node_165 | 0.4 | n |  | TRUE
138 | bus_LV_957-15_1_5_node_140 | 0.4 | n |  | TRUE
139 | bus_LV_957-15_1_5_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_957-15_1_5_node_141 | 0.4 | n |  | TRUE
141 | bus_LV_957-15_1_5_node_142 | 0.4 | n |  | TRUE
142 | bus_LV_957-15_1_5_node_157 | 0.4 | n |  | TRUE
143 | bus_LV_957-15_1_5_node_162 | 0.4 | n |  | TRUE
144 | bus_LV_957-15_1_5_node_160 | 0.4 | n |  | TRUE
145 | bus_LV_957-15_1_5_node_166 | 0.4 | n |  | TRUE
146 | bus_MV_183_0_node_134 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_957-15_1_5_load_27 | 1 | 0.00012533 | 3.1411e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_957-15_1_5_load_24 | 2 | 0.00064186 | 0.00016087 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_957-15_1_5_load_109 | 4 | 0.00025401 | 6.3661e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_957-15_1_5_load_106 | 5 | 0.00041368 | 0.00010368 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_957-15_1_5_load_66 | 8 | 0.00035037 | 8.7812e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_957-15_1_5_load_70 | 10 | 0.00025431 | 6.3737e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_957-15_1_5_load_67 | 11 | 0.0063274 | 0.0015858 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_957-15_1_5_load_80 | 13 | 0.0019995 | 0.00050112 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_957-15_1_5_load_77 | 14 | 0.0018571 | 0.00046544 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_957-15_1_5_load_56 | 15 | 0.0085278 | 0.0021373 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_957-15_1_5_load_152 | 18 | 0.00063583 | 0.00015935 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_957-15_1_5_load_83 | 19 | 0.0013128 | 0.00032903 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_957-15_1_5_load_82 | 20 | 0.00023299 | 5.8393e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_957-15_1_5_load_63 | 22 | 0.00076105 | 0.00019074 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_957-15_1_5_load_102 | 23 | 0.0020957 | 0.00052524 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_957-15_1_5_load_78 | 24 | 0.0016017 | 0.00040142 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_957-15_1_5_load_68 | 25 | 0.0053938 | 0.0013518 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_957-15_1_5_load_98 | 27 | 0.0006788 | 0.00017012 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_957-15_1_5_load_159 | 28 | 0.00019496 | 4.8861e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_957-15_1_5_load_28 | 29 | 0.0033284 | 0.00083418 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_957-15_1_5_load_29 | 30 | 0.0020779 | 0.00052077 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_957-15_1_5_load_71 | 32 | 0.0064511 | 0.0016168 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_957-15_1_5_load_76 | 35 | 0.0010022 | 0.00025117 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_957-15_1_5_load_73 | 36 | 0.009575 | 0.0023997 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_957-15_1_5_load_31 | 37 | 0.00085602 | 0.00021454 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_957-15_1_5_load_32 | 38 | 0.00032937 | 8.2549e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_957-15_1_5_load_35 | 41 | 0.001125 | 0.00028195 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_957-15_1_5_load_36 | 42 | 0.00025598 | 6.4155e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_957-15_1_5_load_86 | 43 | 0.00037914 | 9.5022e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_957-15_1_5_load_81 | 44 | 0.00028576 | 7.1619e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_957-15_1_5_load_74 | 45 | 0.0019148 | 0.00047989 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_957-15_1_5_load_53 | 47 | 0.00079851 | 0.00020012 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_957-15_1_5_load_51 | 48 | 0.0014777 | 0.00037036 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_957-15_1_5_load_147 | 51 | 0.00011427 | 2.8639e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_957-15_1_5_load_132 | 53 | 0.00025871 | 6.4839e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_957-15_1_5_load_129 | 54 | 0.00011126 | 2.7886e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_957-15_1_5_load_151 | 56 | 0.00013846 | 3.4702e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_957-15_1_5_load_149 | 57 | 0.00013617 | 3.4129e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_957-15_1_5_load_139 | 59 | 0.00016585 | 4.1566e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_957-15_1_5_load_164 | 62 | 0.00045122 | 0.00011309 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_957-15_1_5_load_133 | 63 | 0.00015214 | 3.813e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_957-15_1_5_load_144 | 65 | 0.0012346 | 0.00030941 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_957-15_1_5_load_87 | 67 | 0.00034207 | 8.5731e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_957-15_1_5_load_85 | 68 | 0.0016654 | 0.00041739 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_957-15_1_5_load_99 | 70 | 0.0023477 | 0.00058839 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_957-15_1_5_load_122 | 74 | 0.00077213 | 0.00019351 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_957-15_1_5_load_148 | 75 | 0.00041788 | 0.00010473 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_957-15_1_5_load_130 | 76 | 0.00013759 | 3.4483e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_957-15_1_5_load_150 | 77 | 0.000212 | 5.3133e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_957-15_1_5_load_155 | 80 | 0.00010425 | 2.6127e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_957-15_1_5_load_153 | 82 | 0.00025528 | 6.398e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_957-15_1_5_load_161 | 83 | 0.0002304 | 5.7744e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_957-15_1_5_load_163 | 84 | 0.00026991 | 6.7646e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_957-15_1_5_load_101 | 85 | 0.00049794 | 0.0001248 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_957-15_1_5_load_143 | 87 | 0.00048507 | 0.00012157 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_957-15_1_5_load_55 | 88 | 0.0024466 | 0.00061317 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_957-15_1_5_load_54 | 89 | 0.0017851 | 0.00044739 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_957-15_1_5_load_93 | 90 | 0.0054197 | 0.0013583 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_957-15_1_5_load_96 | 91 | 0.0002697 | 6.7593e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_957-15_1_5_load_57 | 94 | 0.0039174 | 0.00098178 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_957-15_1_5_load_58 | 95 | 0.003405 | 0.00085338 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_957-15_1_5_load_59 | 96 | 0.0078184 | 0.0019595 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_957-15_1_5_load_60 | 97 | 0.0030942 | 0.00077549 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_957-15_1_5_load_89 | 100 | 0.003854 | 0.00096589 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_957-15_1_5_load_61 | 101 | 0.0016734 | 0.00041939 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_957-15_1_5_load_62 | 102 | 0.0009103 | 0.00022814 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_957-15_1_5_load_65 | 104 | 0.0035692 | 0.00089452 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_957-15_1_5_load_103 | 105 | 0.00063884 | 0.00016011 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_957-15_1_5_load_72 | 106 | 0.0019352 | 0.000485 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_957-15_1_5_load_92 | 107 | 0.0026164 | 0.00065572 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_957-15_1_5_load_100 | 108 | 0.0039068 | 0.00097914 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_957-15_1_5_load_79 | 109 | 0.0016262 | 0.00040758 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_957-15_1_5_load_90 | 110 | 0.001404 | 0.00035188 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_957-15_1_5_load_88 | 111 | 0.0039198 | 0.00098239 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_957-15_1_5_load_104 | 112 | 0.00049568 | 0.00012423 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_957-15_1_5_load_105 | 113 | 0.00030254 | 7.5825e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_957-15_1_5_load_107 | 114 | 0.00030228 | 7.5758e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_957-15_1_5_load_108 | 115 | 0.00026465 | 6.6327e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_957-15_1_5_load_111 | 117 | 0.00012348 | 3.0947e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_957-15_1_5_load_112 | 118 | 0.00016167 | 4.0518e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_957-15_1_5_load_113 | 119 | 0.00016612 | 4.1634e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_957-15_1_5_load_114 | 120 | 0.00012361 | 3.0979e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_957-15_1_5_load_135 | 122 | 0.00045278 | 0.00011348 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_957-15_1_5_load_136 | 123 | 0.00012582 | 3.1533e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_957-15_1_5_load_116 | 126 | 0.00029373 | 7.3615e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_957-15_1_5_load_134 | 127 | 0.00014673 | 3.6775e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_957-15_1_5_load_117 | 128 | 0.00020243 | 5.0733e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_957-15_1_5_load_119 | 129 | 0.0012179 | 0.00030524 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_957-15_1_5_load_145 | 130 | 0.00014044 | 3.5198e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_957-15_1_5_load_125 | 133 | 0.00023588 | 5.9116e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_957-15_1_5_load_146 | 134 | 0.00016215 | 4.0639e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_957-15_1_5_load_137 | 135 | 0.00070787 | 0.00017741 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_957-15_1_5_load_126 | 136 | 0.00013755 | 3.4474e-05 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_957-15_1_5_load_165 | 137 | 0.00032703 | 8.1961e-05 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_957-15_1_5_load_140 | 138 | 0.00072285 | 0.00018116 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_957-15_1_5_load_138 | 139 | 0.00022257 | 5.5781e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_957-15_1_5_load_141 | 140 | 0.00017049 | 4.2729e-05 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_957-15_1_5_load_142 | 141 | 0.00071952 | 0.00018033 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_957-15_1_5_load_157 | 142 | 0.00010443 | 2.6172e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_957-15_1_5_load_162 | 143 | 0.001199 | 0.00030049 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_957-15_1_5_load_166 | 145 | 0.0010527 | 0.00026384 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_957-15_1_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.1281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_957-15_1_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.25524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_957-15_1_5_line_2 | NAYY 4x150 SE | 1 | 18 | 0.03394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_957-15_1_5_line_3 | NAYY 4x150 SE | 2 | 7 | 0.019714 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_957-15_1_5_line_4 | NAYY 4x150 SE | 3 | 4 | 0.047058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_957-15_1_5_line_5 | NAYY 4x150 SE | 3 | 5 | 0.030329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_957-15_1_5_line_6 | NAYY 4x150 SE | 4 | 10 | 0.0068861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_957-15_1_5_line_7 | NAYY 4x150 SE | 5 | 17 | 0.021318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_957-15_1_5_line_8 | NAYY 4x150 SE | 6 | 7 | 0.31603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_957-15_1_5_line_9 | NAYY 4x150 SE | 6 | 8 | 0.038476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_957-15_1_5_line_10 | NAYY 4x150 SE | 7 | 21 | 0.052303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_957-15_1_5_line_11 | NAYY 4x150 SE | 8 | 22 | 0.0047416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_957-15_1_5_line_12 | NAYY 4x150 SE | 9 | 10 | 0.0083596 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_957-15_1_5_line_13 | NAYY 4x150 SE | 9 | 11 | 0.024475 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_957-15_1_5_line_14 | NAYY 4x150 SE | 11 | 25 | 0.0070725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_957-15_1_5_line_15 | NAYY 4x150 SE | 12 | 13 | 0.012557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_957-15_1_5_line_16 | NAYY 4x150 SE | 12 | 14 | 0.01477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_957-15_1_5_line_17 | NAYY 4x150 SE | 13 | 23 | 0.021548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_957-15_1_5_line_18 | NAYY 4x150 SE | 14 | 24 | 0.020852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_957-15_1_5_line_19 | NAYY 4x150 SE | 15 | 16 | 0.27936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_957-15_1_5_line_20 | NAYY 4x150 SE | 16 | 46 | 0.72113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_957-15_1_5_line_21 | NAYY 4x150 SE | 17 | 105 | 0.014645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_957-15_1_5_line_22 | NAYY 4x150 SE | 17 | 103 | 0.024766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_957-15_1_5_line_23 | NAYY 4x150 SE | 19 | 20 | 0.0046939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_957-15_1_5_line_24 | NAYY 4x150 SE | 20 | 103 | 0.027491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_957-15_1_5_line_25 | NAYY 4x150 SE | 21 | 26 | 0.13125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_957-15_1_5_line_26 | NAYY 4x150 SE | 21 | 27 | 0.26539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_957-15_1_5_line_27 | NAYY 4x150 SE | 22 | 104 | 0.038854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_957-15_1_5_line_28 | NAYY 4x150 SE | 22 | 101 | 0.015678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_957-15_1_5_line_29 | NAYY 4x150 SE | 24 | 109 | 0.02533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_957-15_1_5_line_30 | NAYY 4x150 SE | 25 | 34 | 0.031903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_957-15_1_5_line_31 | NAYY 4x150 SE | 26 | 28 | 0.24173 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_957-15_1_5_line_32 | NAYY 4x150 SE | 28 | 116 | 0.01144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_957-15_1_5_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0063174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_957-15_1_5_line_34 | NAYY 4x150 SE | 30 | 31 | 0.014565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_957-15_1_5_line_35 | NAYY 4x150 SE | 31 | 32 | 0.040201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_957-15_1_5_line_36 | NAYY 4x150 SE | 31 | 33 | 0.010678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_957-15_1_5_line_37 | NAYY 4x150 SE | 32 | 34 | 0.0039365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_957-15_1_5_line_38 | NAYY 4x150 SE | 33 | 35 | 0.037564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_957-15_1_5_line_39 | NAYY 4x150 SE | 33 | 36 | 0.015064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_957-15_1_5_line_40 | NAYY 4x150 SE | 34 | 106 | 0.024964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_957-15_1_5_line_41 | NAYY 4x150 SE | 35 | 93 | 0.020689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_957-15_1_5_line_42 | NAYY 4x150 SE | 36 | 45 | 0.0045951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_957-15_1_5_line_43 | NAYY 4x150 SE | 37 | 38 | 0.027718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_957-15_1_5_line_44 | NAYY 4x150 SE | 37 | 39 | 0.042695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_957-15_1_5_line_45 | NAYY 4x150 SE | 38 | 40 | 0.041063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_957-15_1_5_line_46 | NAYY 4x150 SE | 39 | 41 | 0.022384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_957-15_1_5_line_47 | NAYY 4x150 SE | 39 | 42 | 0.067468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_957-15_1_5_line_48 | NAYY 4x150 SE | 40 | 43 | 0.038926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_957-15_1_5_line_49 | NAYY 4x150 SE | 41 | 44 | 0.015441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_957-15_1_5_line_50 | NAYY 4x150 SE | 42 | 45 | 0.017753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_957-15_1_5_line_51 | NAYY 4x150 SE | 43 | 69 | 0.028018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_957-15_1_5_line_52 | NAYY 4x150 SE | 46 | 47 | 0.027463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_957-15_1_5_line_53 | NAYY 4x150 SE | 46 | 48 | 0.031261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_957-15_1_5_line_54 | NAYY 4x150 SE | 47 | 70 | 0.0051384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_957-15_1_5_line_55 | NAYY 4x150 SE | 48 | 71 | 0.0071103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_957-15_1_5_line_56 | NAYY 4x150 SE | 49 | 50 | 0.76181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_957-15_1_5_line_57 | NAYY 4x150 SE | 49 | 51 | 0.041855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_957-15_1_5_line_58 | NAYY 4x150 SE | 50 | 63 | 0.28511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_957-15_1_5_line_59 | NAYY 4x150 SE | 50 | 58 | 0.049763 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_957-15_1_5_line_60 | NAYY 4x150 SE | 51 | 75 | 0.010009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_957-15_1_5_line_61 | NAYY 4x150 SE | 52 | 53 | 0.2187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_957-15_1_5_line_62 | NAYY 4x150 SE | 52 | 54 | 0.094419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_957-15_1_5_line_63 | NAYY 4x150 SE | 54 | 76 | 0.056915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_957-15_1_5_line_64 | NAYY 4x150 SE | 55 | 56 | 0.025128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
65 | LV_957-15_1_5_line_65 | NAYY 4x150 SE | 55 | 57 | 0.0071471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_957-15_1_5_line_66 | NAYY 4x150 SE | 56 | 64 | 0.090274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
67 | LV_957-15_1_5_line_67 | NAYY 4x150 SE | 57 | 77 | 0.0092881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_957-15_1_5_line_68 | NAYY 4x150 SE | 58 | 59 | 0.32982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_957-15_1_5_line_69 | NAYY 4x150 SE | 59 | 78 | 0.013785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_957-15_1_5_line_70 | NAYY 4x150 SE | 60 | 61 | 0.53337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
71 | LV_957-15_1_5_line_71 | NAYY 4x150 SE | 60 | 62 | 0.053179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
72 | LV_957-15_1_5_line_72 | NAYY 4x150 SE | 61 | 64 | 0.10552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_957-15_1_5_line_73 | NAYY 4x150 SE | 61 | 65 | 0.021105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_957-15_1_5_line_74 | NAYY 4x150 SE | 62 | 84 | 0.040277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_957-15_1_5_line_75 | NAYY 4x150 SE | 63 | 86 | 0.032354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_957-15_1_5_line_76 | NAYY 4x150 SE | 65 | 87 | 0.013689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_957-15_1_5_line_77 | NAYY 4x150 SE | 66 | 67 | 0.0088969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_957-15_1_5_line_78 | NAYY 4x150 SE | 66 | 68 | 0.008443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_957-15_1_5_line_79 | NAYY 4x150 SE | 67 | 85 | 0.049078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_957-15_1_5_line_80 | NAYY 4x150 SE | 68 | 69 | 0.10364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_957-15_1_5_line_81 | NAYY 4x150 SE | 71 | 88 | 0.012069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_957-15_1_5_line_82 | NAYY 4x150 SE | 72 | 73 | 0.021032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_957-15_1_5_line_83 | NAYY 4x150 SE | 72 | 74 | 0.021264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_957-15_1_5_line_84 | NAYY 4x150 SE | 73 | 136 | 0.016575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_957-15_1_5_line_85 | NAYY 4x150 SE | 73 | 134 | 0.016679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_957-15_1_5_line_86 | NAYY 4x150 SE | 76 | 78 | 0.054411 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_957-15_1_5_line_87 | NAYY 4x150 SE | 77 | 139 | 0.016021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
88 | LV_957-15_1_5_line_88 | NAYY 4x150 SE | 78 | 138 | 0.020418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_957-15_1_5_line_89 | NAYY 4x150 SE | 79 | 80 | 0.005686 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_957-15_1_5_line_90 | NAYY 4x150 SE | 79 | 81 | 0.26334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_957-15_1_5_line_91 | NAYY 4x150 SE | 79 | 82 | 0.010073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_957-15_1_5_line_92 | NAYY 4x150 SE | 80 | 142 | 0.033938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
93 | LV_957-15_1_5_line_93 | NAYY 4x150 SE | 81 | 83 | 0.21684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_957-15_1_5_line_94 | NAYY 4x150 SE | 83 | 143 | 0.021516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_957-15_1_5_line_95 | NAYY 4x150 SE | 84 | 143 | 0.015783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_957-15_1_5_line_96 | NAYY 4x150 SE | 86 | 127 | 0.039124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_957-15_1_5_line_97 | NAYY 4x150 SE | 86 | 121 | 0.16737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_957-15_1_5_line_98 | NAYY 4x150 SE | 86 | 124 | 0.21594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_957-15_1_5_line_99 | NAYY 4x150 SE | 87 | 140 | 0.03715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_957-15_1_5_line_100 | NAYY 4x150 SE | 88 | 91 | 0.024119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_957-15_1_5_line_101 | NAYY 4x150 SE | 89 | 90 | 0.034479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_957-15_1_5_line_102 | NAYY 4x150 SE | 90 | 92 | 0.020692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_957-15_1_5_line_103 | NAYY 4x150 SE | 91 | 93 | 0.0098618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_957-15_1_5_line_104 | NAYY 4x150 SE | 92 | 99 | 0.022468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_957-15_1_5_line_105 | NAYY 4x150 SE | 93 | 108 | 0.020803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_957-15_1_5_line_106 | NAYY 4x150 SE | 94 | 95 | 0.031522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_957-15_1_5_line_107 | NAYY 4x150 SE | 94 | 96 | 0.042341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_957-15_1_5_line_108 | NAYY 4x150 SE | 95 | 97 | 0.0036655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_957-15_1_5_line_109 | NAYY 4x150 SE | 97 | 98 | 0.013654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_957-15_1_5_line_110 | NAYY 4x150 SE | 98 | 99 | 0.028886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_957-15_1_5_line_111 | NAYY 4x150 SE | 98 | 100 | 0.014158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_957-15_1_5_line_112 | NAYY 4x150 SE | 99 | 108 | 0.027754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_957-15_1_5_line_113 | NAYY 4x150 SE | 100 | 111 | 0.027818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_957-15_1_5_line_114 | NAYY 4x150 SE | 101 | 102 | 0.002092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_957-15_1_5_line_115 | NAYY 4x150 SE | 102 | 103 | 0.10552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_957-15_1_5_line_116 | NAYY 4x150 SE | 105 | 112 | 0.018184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_957-15_1_5_line_117 | NAYY 4x150 SE | 106 | 107 | 0.005201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_957-15_1_5_line_118 | NAYY 4x150 SE | 109 | 110 | 0.022825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_957-15_1_5_line_119 | NAYY 4x150 SE | 110 | 111 | 0.023748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_957-15_1_5_line_120 | NAYY 4x150 SE | 112 | 113 | 0.019484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_957-15_1_5_line_121 | NAYY 4x150 SE | 113 | 114 | 0.0074908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_957-15_1_5_line_122 | NAYY 4x150 SE | 114 | 115 | 0.0097023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_957-15_1_5_line_123 | NAYY 4x150 SE | 116 | 144 | 0.003818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_957-15_1_5_line_124 | NAYY 4x150 SE | 116 | 142 | 0.019183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
125 | LV_957-15_1_5_line_125 | NAYY 4x150 SE | 117 | 118 | 0.002205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_957-15_1_5_line_126 | NAYY 4x150 SE | 117 | 119 | 0.014538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
127 | LV_957-15_1_5_line_127 | NAYY 4x150 SE | 118 | 120 | 0.010859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
128 | LV_957-15_1_5_line_128 | NAYY 4x150 SE | 119 | 121 | 0.068742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
129 | LV_957-15_1_5_line_129 | NAYY 4x150 SE | 120 | 122 | 0.0081609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
130 | LV_957-15_1_5_line_130 | NAYY 4x150 SE | 122 | 123 | 0.025006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
131 | LV_957-15_1_5_line_131 | NAYY 4x150 SE | 123 | 139 | 0.024014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
132 | LV_957-15_1_5_line_132 | NAYY 4x150 SE | 124 | 125 | 0.63518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
133 | LV_957-15_1_5_line_133 | NAYY 4x150 SE | 124 | 126 | 0.03729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_957-15_1_5_line_134 | NAYY 4x150 SE | 125 | 130 | 0.04131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_957-15_1_5_line_135 | NAYY 4x150 SE | 126 | 128 | 0.023212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_957-15_1_5_line_136 | NAYY 4x150 SE | 127 | 135 | 0.0048648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_957-15_1_5_line_137 | NAYY 4x150 SE | 128 | 129 | 0.0058995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_957-15_1_5_line_138 | NAYY 4x150 SE | 130 | 134 | 0.024564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_957-15_1_5_line_139 | NAYY 4x150 SE | 131 | 132 | 0.21597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_957-15_1_5_line_140 | NAYY 4x150 SE | 131 | 133 | 0.025542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_957-15_1_5_line_141 | NAYY 4x150 SE | 132 | 137 | 0.084203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_957-15_1_5_line_142 | NAYY 4x150 SE | 133 | 136 | 0.018798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_957-15_1_5_line_143 | NAYY 4x150 SE | 140 | 141 | 0.0038012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_957-15_1_5_line_144 | NAYY 4x150 SE | 144 | 145 | 0.024641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_957-15_1_5_trafo_33 | 0.25 MVA 20/0.4 kV | 146 | 39 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39
0 | 2624079.1414 | 1207964.6578 | 2624091.7296 | 1207942.4294 | 2624097.8422 | 1207934.8721 | 2624111.1323 | 1207927.1324 | 2624121.6023 | 1207917.4248 | 2624131.6477 | 1207905.5475 | 2624136.2476 | 1207896.0386 | 2624137.3707 | 1207887.1604 | 2624133.9602 | 1207871.3267 | 2624134.0083 | 1207859.4091
1 | 2624079.1414 | 1207964.6578 | 2624100.1584 | 1207967.5663 | 2624127.5295 | 1207968.9774 | 2624130.5554 | 1207974.615 | 2624103.2288 | 1208013.0707 | 2624103.4345 | 1208016.7514 | 2624106.022 | 1208021.7424 | 2624104.7019 | 1208026.7287 | 2624091.1932 | 1208034.0339 | 2624068.3149 | 1208049.7617 | 2624063.4964 | 1208058.8363 | 2624055.5246 | 1208095.8471 | 2624048.6356 | 1208133.9518 | 2624045.7098 | 1208142.0376
2 | 2624131.0661 | 1207827.7612 | 2624135.8516 | 1207834.0691 | 2624137.5622 | 1207839.7125 | 2624137.0948 | 1207848.1597 | 2624134.0083 | 1207859.4091
3 | 2624034.9684 | 1208158.077 | 2624042.9236 | 1208149.7376 | 2624045.7098 | 1208142.0376
4 | 2624008.7824 | 1208586.789 | 2624036.3541 | 1208592.4362 | 2624053.8234 | 1208596.0863 | 2624054.8396 | 1208596.4133
5 | 2624008.7824 | 1208586.789 | 2624010.8633 | 1208577.8146 | 2624019.7013 | 1208558.6369
6 | 2624061.39 | 1208598.5373 | 2624055.6075 | 1208596.6604 | 2624054.8396 | 1208596.4133
7 | 2624028.6239 | 1208539.2755 | 2624019.7013 | 1208558.6369
8 | 2624090.4429 | 1208371.1524 | 2624085.044 | 1208346.9839 | 2624070.0275 | 1208315.4947 | 2624031.6188 | 1208263.2444 | 2623994.6343 | 1208227.2203 | 2623984.8668 | 1208209.8381 | 2623965.0145 | 1208195.3727 | 2623962.578 | 1208188.7259 | 2623963.6213 | 1208182.5822 | 2623987.8381 | 1208168.438 | 2624011.3246 | 1208152.5456 | 2624017.3676 | 1208150.88 | 2624023.9035 | 1208151.3843 | 2624033.0553 | 1208155.5234 | 2624034.9684 | 1208158.077
9 | 2624090.4429 | 1208371.1524 | 2624092.1025 | 1208380.0085 | 2624093.9055 | 1208392.8785 | 2624092.7768 | 1208409.3096
10 | 2624079.0887 | 1208174.0522 | 2624067.9825 | 1208177.654 | 2624061.3759 | 1208177.7052 | 2624053.4699 | 1208175.7167 | 2624047.5754 | 1208172.6135 | 2624041.9555 | 1208167.3991 | 2624034.9684 | 1208158.077
11 | 2624092.4519 | 1208414.04 | 2624092.7768 | 1208409.3096
12 | 2624069.3412 | 1208601.1182 | 2624061.39 | 1208598.5373
13 | 2624069.3412 | 1208601.1182 | 2624085.3941 | 1208607.2751 | 2624091.9241 | 1208610.4987
14 | 2624091.9241 | 1208610.4987 | 2624098.2659 | 1208613.6294
15 | 2624049.0259 | 1208649.1967 | 2624038.8877 | 1208641.7882
16 | 2624049.0259 | 1208649.1967 | 2624060.9245 | 1208657.947
17 | 2624021.4898 | 1208629.0748 | 2624038.8877 | 1208641.7882
18 | 2624060.9245 | 1208657.947 | 2624068.2545 | 1208663.3375 | 2624077.2035 | 1208670.9575
19 | 2624312.9671 | 1209240.8838 | 2624296.5636 | 1209218.6269 | 2624284.0698 | 1209195.6411 | 2624274.0673 | 1209176.8233 | 2624250.3778 | 1209118.0276 | 2624243.3006 | 1209103.1794 | 2624233.3085 | 1209087.3634 | 2624218.31 | 1209072.7056 | 2624146.8364 | 1209027.2243
20 | 2624276.0772 | 1208756.7852 | 2624287.6379 | 1208770.1841 | 2624302.7865 | 1208789.1896 | 2624313.2747 | 1208804.6075 | 2624325.291 | 1208825.5681 | 2624346.8094 | 1208863.2212 | 2624371.6717 | 1208906.5689 | 2624381.6425 | 1208922.0293 | 2624386.9267 | 1208929.1548 | 2624393.9595 | 1208938.0996 | 2624413.6602 | 1208959.0251 | 2624419.6091 | 1208965.3418 | 2624496.3794 | 1209038.3411 | 2624529.6645 | 1209069.9507 | 2624506.1212 | 1209109.4986 | 2624471.1783 | 1209163.4858 | 2624460.3514 | 1209186.521 | 2624434.3957 | 1209206.5484 | 2624423.3787 | 1209203.5906 | 2624322.6976 | 1209216.2874 | 2624316.4334 | 1209216.5398 | 2624312.3494 | 1209218.969 | 2624312.0531 | 1209226.4053 | 2624314.7357 | 1209234.0205 | 2624312.9671 | 1209240.8838
21 | 2624028.6239 | 1208539.2755 | 2624041.3392 | 1208546.5412
22 | 2624039.9784 | 1208517.2532 | 2624028.6239 | 1208539.2755
23 | 2624015.2524 | 1208525.8993 | 2624011.1259 | 1208528.1363
24 | 2624039.9784 | 1208517.2532 | 2624033.9942 | 1208515.7395 | 2624015.2524 | 1208525.8993
25 | 2624079.0887 | 1208174.0522 | 2624088.438 | 1208166.8859 | 2624097.9511 | 1208160.5873 | 2624104.7741 | 1208157.7688 | 2624106.6815 | 1208150.4168 | 2624111.8244 | 1208140.0762 | 2624121.2515 | 1208128.7301 | 2624127.3809 | 1208124.4858 | 2624135.1384 | 1208123.7056 | 2624138.9009 | 1208125.7552 | 2624142.7645 | 1208129.1283 | 2624145.9569 | 1208133.0433 | 2624148.945 | 1208138.6029 | 2624152.5446 | 1208145.1989 | 2624156.352 | 1208149.3166 | 2624160.0078 | 1208151.4103 | 2624164.1844 | 1208152.5834 | 2624173.2554 | 1208152.2198
26 | 2624079.0887 | 1208174.0522 | 2624085.1729 | 1208175.3663 | 2624096.4375 | 1208177.7353 | 2624104.4787 | 1208180.1357 | 2624114.2278 | 1208186.9454 | 2624144.9489 | 1208220.7327 | 2624195.2853 | 1208274.7106 | 2624206.6732 | 1208284.1398 | 2624214.5275 | 1208289.4745 | 2624222.7137 | 1208291.6644 | 2624235.0753 | 1208289.6578 | 2624256.3159 | 1208283.9963 | 2624265.2606 | 1208279.1299 | 2624272.2599 | 1208270.3312 | 2624283.7648 | 1208260.2834 | 2624287.6817 | 1208259.8435
27 | 2624092.4519 | 1208414.04 | 2624130.7979 | 1208420.301
28 | 2624092.4519 | 1208414.04 | 2624091.1811 | 1208429.6665
29 | 2624096.4893 | 1208687.379 | 2624077.2035 | 1208670.9575
30 | 2624126.0583 | 1208629.2624 | 2624119.9772 | 1208625.4135 | 2624101.2653 | 1208615.1101 | 2624098.2659 | 1208613.6294
31 | 2624173.2554 | 1208152.2198 | 2624182.9217 | 1208140.0188 | 2624239.7308 | 1208078.9368 | 2624253.7066 | 1208061.4393 | 2624256.5253 | 1208052.5124 | 2624257.9433 | 1208008.4602 | 2624259.6129 | 1207977.3385 | 2624273.6228 | 1207953.3709 | 2624279.4975 | 1207947.9543
32 | 2624287.9084 | 1207940.1993 | 2624279.4975 | 1207947.9543
33 | 2624150.48 | 1208670.4654 | 2624154.2201 | 1208665.3741
34 | 2624162.8433 | 1208653.6357 | 2624154.2201 | 1208665.3741
35 | 2624162.8433 | 1208653.6357 | 2624144.9611 | 1208641.2121 | 2624129.3857 | 1208631.3659
36 | 2624162.8433 | 1208653.6357 | 2624171.6289 | 1208659.7412
37 | 2624126.0583 | 1208629.2624 | 2624129.3857 | 1208631.3659
38 | 2624171.6289 | 1208659.7412 | 2624189.2698 | 1208673.5425 | 2624200.3785 | 1208683.8667
39 | 2624171.6289 | 1208659.7412 | 2624180.7311 | 1208647.738
40 | 2624126.0583 | 1208629.2624 | 2624112.409 | 1208650.1645
41 | 2624215.5335 | 1208697.9513 | 2624200.3785 | 1208683.8667
42 | 2624180.7311 | 1208647.738 | 2624180.7311 | 1208647.738 | 2624185.2216 | 1208646.7629
43 | 2624282.9778 | 1208580.2268 | 2624284.1516 | 1208578.6295 | 2624287.7676 | 1208573.6302 | 2624290.4422 | 1208568.3048 | 2624292.644 | 1208563.3777 | 2624295.5347 | 1208555.6932
44 | 2624257.6957 | 1208614.6311 | 2624282.9778 | 1208580.2268
45 | 2624308.478 | 1208516.7604 | 2624306.5447 | 1208521.0994 | 2624297.5546 | 1208550.3236 | 2624295.5347 | 1208555.6932
46 | 2624257.6957 | 1208614.6311 | 2624254.7183 | 1208610.2722 | 2624250.5336 | 1208605.5748 | 2624243.1808 | 1208597.6455
47 | 2624257.6957 | 1208614.6311 | 2624253.194 | 1208620.6273 | 2624245.5063 | 1208630.5795 | 2624239.8236 | 1208635.3591 | 2624227.9799 | 1208642.9265 | 2624222.0342 | 1208645.1036 | 2624218.6018 | 1208646.0792 | 2624211.6927 | 1208647.7633 | 2624202.8239 | 1208646.989
48 | 2624308.478 | 1208516.7604 | 2624315.1979 | 1208509.3169 | 2624317.8512 | 1208507.4044 | 2624320.4335 | 1208506.103 | 2624323.2792 | 1208505.4587 | 2624325.8944 | 1208505.4248 | 2624328.6523 | 1208505.8141 | 2624331.8464 | 1208507.3501 | 2624334.7489 | 1208509.5854 | 2624337.6545 | 1208512.8991 | 2624339.4579 | 1208515.0443
49 | 2624233.3638 | 1208585.8852 | 2624234.2459 | 1208588.0101 | 2624243.1808 | 1208597.6455
50 | 2624185.2216 | 1208646.7629 | 2624189.5264 | 1208645.828 | 2624202.8239 | 1208646.989
51 | 2624357.9406 | 1208536.0946 | 2624347.3607 | 1208524.445 | 2624339.4579 | 1208515.0443
52 | 2624276.0772 | 1208756.7852 | 2624288.7371 | 1208752.2229 | 2624291.8305 | 1208750.4456 | 2624300.8784 | 1208745.2394
53 | 2624276.0772 | 1208756.7852 | 2624253.6747 | 1208734.9821
54 | 2624305.3322 | 1208742.6766 | 2624300.8784 | 1208745.2394
55 | 2624248.5769 | 1208730.0253 | 2624252.3097 | 1208733.6536 | 2624253.6747 | 1208734.9821
56 | 2625376.4464 | 1208793.0845 | 2625371.0725 | 1208785.8465 | 2625363.3644 | 1208782.3007 | 2625353.986 | 1208781.8496 | 2625343.3786 | 1208782.6273 | 2625330.6998 | 1208786.0866 | 2625317.6549 | 1208789.8335 | 2625303.375 | 1208792.619 | 2625289.0971 | 1208789.568 | 2625267.9527 | 1208779.8621 | 2625257.3591 | 1208771.9574 | 2625243.1531 | 1208757.2558 | 2625228.1586 | 1208734.8355 | 2625208.7769 | 1208689.2283 | 2625190.2528 | 1208633.0521 | 2625186.6719 | 1208616.9169 | 2625186.7104 | 1208604.1766 | 2625187.5898 | 1208592.1291 | 2625189.0387 | 1208587.4326 | 2625205.6872 | 1208590.8935 | 2625228.4917 | 1208583.8858 | 2625234.0881 | 1208579.9405 | 2625243.9275 | 1208577.5029 | 2625259.8465 | 1208573.7124 | 2625281.6589 | 1208574.8163 | 2625296.9364 | 1208577.1156 | 2625313.8765 | 1208574.5525 | 2625331.4292 | 1208569.1349 | 2625340.0552 | 1208566.0364 | 2625352.7622 | 1208568.5694 | 2625373.8334 | 1208567.0357 | 2625398.8118 | 1208554.7682 | 2625419.35 | 1208533.7659 | 2625442.6461 | 1208509.6181 | 2625451.0722 | 1208490.9991 | 2625458.4192 | 1208461.6139 | 2625463.3048 | 1208437.1989 | 2625480.3832 | 1208416.5712 | 2625495.3845 | 1208405.2843 | 2625520.1709 | 1208393.6947
57 | 2625376.4464 | 1208793.0845 | 2625361.1512 | 1208802.2803 | 2625345.3648 | 1208810.7737 | 2625339.8016 | 1208813.2315
58 | 2625520.1709 | 1208393.6947 | 2625521.225 | 1208383.6269 | 2625525.0609 | 1208343.3985 | 2625531.3194 | 1208310.9071 | 2625543.7033 | 1208275.3178 | 2625562.2546 | 1208228.6488 | 2625573.7721 | 1208205.5295 | 2625582.0057 | 1208187.677 | 2625584.8937 | 1208180.7743 | 2625584.9216 | 1208174.2708 | 2625584.5389 | 1208167.7655 | 2625584.1458 | 1208163.6949 | 2625576.8966 | 1208143.3414 | 2625576.9315 | 1208135.2037 | 2625576.554 | 1208127.4755 | 2625573.8247 | 1208122.1039
59 | 2625512.2833 | 1208442.7774 | 2625518.2451 | 1208412.0745 | 2625520.1709 | 1208393.6947
60 | 2625332.2092 | 1208819.1448 | 2625334.6723 | 1208815.4977 | 2625339.8016 | 1208813.2315
61 | 2625457.7073 | 1208933.9199 | 2625464.5859 | 1208946.5562 | 2625473.4704 | 1208966.5053 | 2625481.9797 | 1208979.9602 | 2625494.1267 | 1208999.5229 | 2625514.8314 | 1209021.1567 | 2625543.266 | 1209046.4367 | 2625560.7545 | 1209057.5288 | 2625575.3138 | 1209062.1603 | 2625577.4152 | 1209056.0214 | 2625581.0855 | 1209050.9453 | 2625585.1784 | 1209046.5826 | 2625589.7583 | 1209043.8674 | 2625596.5214 | 1209042.5622 | 2625604.0377 | 1209042.8501 | 2625605.114 | 1209042.9292
62 | 2625457.7073 | 1208933.9199 | 2625468.3687 | 1208920.4133 | 2625476.5537 | 1208913.6777 | 2625487.1706 | 1208908.8424 | 2625497.79 | 1208905.2301 | 2625510.4395 | 1208903.2496 | 2625519.4159 | 1208901.6648 | 2625528.4045 | 1208897.234 | 2625535.3663 | 1208890.3488 | 2625536.5847 | 1208888.7662
63 | 2625536.5847 | 1208888.7662 | 2625543.163 | 1208880.2209 | 2625548.0924 | 1208870.4809 | 2625550.1701 | 1208862.7743 | 2625548.181 | 1208849.7586 | 2625545.782 | 1208838.3641 | 2625545.3165 | 1208835.9875
64 | 2625278.8627 | 1208013.6907 | 2625269.1534 | 1207990.5145
65 | 2625278.8627 | 1208013.6907 | 2625285.9529 | 1208012.7908
66 | 2625220.504 | 1207915.0115 | 2625225.3427 | 1207928.6173 | 2625269.1534 | 1207990.5145
67 | 2625285.9529 | 1208012.7908 | 2625295.167 | 1208011.6212
68 | 2625512.2833 | 1208442.7774 | 2625511.6304 | 1208446.1432 | 2625509.4703 | 1208462.4431 | 2625511.3879 | 1208490.5003 | 2625516.9834 | 1208517.0946 | 2625518.5309 | 1208535.656 | 2625517.2064 | 1208559.2302 | 2625518.7794 | 1208573.6117 | 2625523.9724 | 1208598.2921 | 2625530.7176 | 1208642.2233 | 2625537.4812 | 1208681.8188 | 2625537.7822 | 1208707.4344 | 2625538.9355 | 1208723.9597 | 2625540.9171 | 1208736.9754 | 2625542.9084 | 1208747.7011 | 2625543.7005 | 1208754.4749 | 2625543.2599 | 1208761.5214 | 2625541.0892 | 1208769.1869
69 | 2625538.6463 | 1208782.7358 | 2625540.2884 | 1208772.0146 | 2625541.0892 | 1208769.1869
70 | 2624736.2045 | 1207914.1441 | 2624761.7233 | 1207916.7622 | 2624784.5308 | 1207916.8567 | 2624803.6317 | 1207925.2851 | 2624850.7948 | 1207955.3865 | 2624922.9386 | 1207992.9855 | 2624992.3374 | 1208023.2364 | 2625017.7829 | 1208026.8781 | 2625037.0844 | 1208032.6065 | 2625049.4111 | 1208035.5042 | 2625073.5405 | 1208041.164 | 2625094.0592 | 1208043.0623 | 2625096.366 | 1208022.3604 | 2625099.9001 | 1208006.3107 | 2625113.0642 | 1207983.6088 | 2625134.1469 | 1207959.9064 | 2625139.7286 | 1207946.9337 | 2625143.299 | 1207918.6774 | 2625139.6629 | 1207910.124
71 | 2624736.2045 | 1207914.1441 | 2624694.9287 | 1207888.6593 | 2624691.2741 | 1207885.7524
72 | 2625139.6629 | 1207910.124 | 2625144.2482 | 1207890.032 | 2625148.9586 | 1207885.3714 | 2625160.7628 | 1207886.0214 | 2625178.0963 | 1207891.5975 | 2625208.2063 | 1207908.8006 | 2625220.504 | 1207915.0115
73 | 2625139.6629 | 1207910.124 | 2625129.6516 | 1207918.8312 | 2625122.0328 | 1207920.6692
74 | 2624691.2741 | 1207885.7524 | 2624688.9574 | 1207883.9098 | 2624675.3753 | 1207870.0682 | 2624665.7748 | 1207854.9313 | 2624665.7748 | 1207854.9313
75 | 2625559.1692 | 1208093.2599 | 2625573.8247 | 1208122.1039
76 | 2625109.0971 | 1207919.4616 | 2625115.5649 | 1207922.2295 | 2625122.0328 | 1207920.6692
77 | 2624464.2033 | 1208536.9066 | 2624472.7569 | 1208534.4588
78 | 2624464.2033 | 1208536.9066 | 2624456.3713 | 1208540.0598
79 | 2624472.7569 | 1208534.4588 | 2624485.4221 | 1208530.8344 | 2624499.3293 | 1208520.7302 | 2624501.8387 | 1208505.6987 | 2624501.853 | 1208502.2238
80 | 2624357.9406 | 1208536.0946 | 2624366.9207 | 1208542.9684 | 2624376.3494 | 1208547.9763 | 2624386.6325 | 1208550.3751 | 2624404.7336 | 1208550.0821 | 2624423.5568 | 1208544.2223 | 2624451.6015 | 1208541.9801 | 2624456.3713 | 1208540.0598
81 | 2624248.5769 | 1208730.0253 | 2624239.9164 | 1208721.6189
82 | 2625877.8053 | 1208670.0863 | 2625858.4005 | 1208678.3292
83 | 2625858.4005 | 1208678.3292 | 2625850.2562 | 1208673.747 | 2625844.2316 | 1208663.4623
84 | 2625877.8053 | 1208670.0863 | 2625890.5352 | 1208669.0075 | 2625894.3336 | 1208668.9067
85 | 2625877.8053 | 1208670.0863 | 2625883.9538 | 1208654.582
86 | 2625538.6463 | 1208782.7358 | 2625543.1244 | 1208793.2275 | 2625543.0757 | 1208804.6114 | 2625542.627 | 1208813.5479 | 2625542.9923 | 1208824.122 | 2625545.3165 | 1208835.9875
87 | 2625295.167 | 1208011.6212 | 2625311.061 | 1208009.6038
88 | 2625538.6463 | 1208782.7358 | 2625534.9947 | 1208792.2923 | 2625533.4922 | 1208802.3693
89 | 2624327.2168 | 1207898.3468 | 2624322.737 | 1207901.8485
90 | 2624327.2168 | 1207898.3468 | 2624340.3275 | 1207888.0944 | 2624358.5979 | 1207863.544 | 2624362.3861 | 1207849.9963 | 2624389.3145 | 1207796.0315 | 2624391.3916 | 1207782.6214 | 2624381.4148 | 1207734.6095 | 2624382.3856 | 1207720.2832 | 2624418.2739 | 1207723.3424 | 2624441.9741 | 1207739.5816
91 | 2624327.2168 | 1207898.3468 | 2624318.0834 | 1207894.0979
92 | 2624302.0061 | 1207927.1903 | 2624314.8008 | 1207915.3836 | 2624317.2561 | 1207906.1329 | 2624322.737 | 1207901.8485
93 | 2624441.9741 | 1207739.5816 | 2624470.8591 | 1207750.2834 | 2624506.8854 | 1207760.4366 | 2624564.0656 | 1207792.0443 | 2624602.7533 | 1207820.4636 | 2624617.4769 | 1207828.5732 | 2624635.2571 | 1207833.5283
94 | 2624635.2571 | 1207833.5283 | 2624635.6569 | 1207833.6397 | 2624652.887 | 1207845.8204
95 | 2624652.887 | 1207845.8204 | 2624665.7748 | 1207854.9313
96 | 2625559.1692 | 1208093.2599 | 2625553.1957 | 1208131.9254
97 | 2625559.1692 | 1208093.2599 | 2625559.1901 | 1208088.3794 | 2625561.2588 | 1208081.0731 | 2625565.3673 | 1208073.2196 | 2625575.2518 | 1208062.2335 | 2625567.6122 | 1208054.9301 | 2625555.6862 | 1208043.7284 | 2625527.337 | 1208025.8307 | 2625463.4616 | 1207995.2969
98 | 2625559.1692 | 1208093.2599 | 2625559.1901 | 1208088.3794 | 2625561.2588 | 1208081.0731 | 2625565.3673 | 1208073.2196 | 2625575.2518 | 1208062.2335 | 2625582.2101 | 1208068.8781 | 2625597.3768 | 1208093.768 | 2625614.2943 | 1208119.8772 | 2625622.6239 | 1208131.1303 | 2625641.5394 | 1208141.5617 | 2625666.2005 | 1208154.1745 | 2625674.1452 | 1208161.2126 | 2625680.8941 | 1208179.3628 | 2625687.1146 | 1208189.5508 | 2625691.7868 | 1208190.2823
99 | 2625074.0552 | 1207907.6608 | 2625088.6998 | 1207910.7325 | 2625109.0971 | 1207919.4616
100 | 2624239.9164 | 1208721.6189 | 2624222.6098 | 1208704.8201
101 | 2624213.4667 | 1208757.7875 | 2624221.6691 | 1208765.2138 | 2624226.5836 | 1208768.0019 | 2624233.4728 | 1208769.3194 | 2624239.5611 | 1208769.4664 | 2624244.1183 | 1208768.4955
102 | 2624195.9058 | 1208746.8437 | 2624213.4667 | 1208757.7875
103 | 2624215.5335 | 1208697.9513 | 2624222.6098 | 1208704.8201
104 | 2624180.0972 | 1208731.1487 | 2624185.5632 | 1208738.5527 | 2624189.8416 | 1208742.639 | 2624195.9058 | 1208746.8437
105 | 2624215.5335 | 1208697.9513 | 2624200.3515 | 1208712.1741
106 | 2624191.6157 | 1208786.2408 | 2624175.4569 | 1208769.5626 | 2624169.9587 | 1208763.3459
107 | 2624191.6157 | 1208786.2408 | 2624212.2012 | 1208807.488 | 2624220.767 | 1208816.9415
108 | 2624169.9587 | 1208763.3459 | 2624167.5303 | 1208760.6002
109 | 2624158.4842 | 1208750.3721 | 2624167.5303 | 1208760.6002
110 | 2624158.4842 | 1208750.3721 | 2624172.7491 | 1208738.034 | 2624180.0972 | 1208731.1487
111 | 2624158.4842 | 1208750.3721 | 2624148.2148 | 1208740.6262
112 | 2624180.0972 | 1208731.1487 | 2624200.3515 | 1208712.1741
113 | 2624129.6189 | 1208719.9485 | 2624146.5196 | 1208739.0175 | 2624148.2148 | 1208740.6262
114 | 2624091.1811 | 1208429.6665 | 2624091.0115 | 1208431.7516
115 | 2624039.9784 | 1208517.2532 | 2624050.9979 | 1208506.7139 | 2624061.6449 | 1208499.964 | 2624071.6895 | 1208491.7665 | 2624085.2233 | 1208472.3101 | 2624090.1084 | 1208442.8578 | 2624091.0115 | 1208431.7516
116 | 2624041.3392 | 1208546.5412 | 2624057.1279 | 1208555.5631
117 | 2624112.409 | 1208650.1645 | 2624109.5652 | 1208654.5193
118 | 2624096.4893 | 1208687.379 | 2624113.8675 | 1208702.1763
119 | 2624129.6189 | 1208719.9485 | 2624113.8675 | 1208702.1763 | 2624113.8675 | 1208702.1763
120 | 2624074.0448 | 1208565.2297 | 2624057.1279 | 1208555.5631
121 | 2624074.0448 | 1208565.2297 | 2624080.5487 | 1208568.9461
122 | 2624088.9727 | 1208573.7597 | 2624080.5487 | 1208568.9461
123 | 2624286.1203 | 1207936.8235 | 2624287.9084 | 1207940.1993
124 | 2624287.9084 | 1207940.1993 | 2624302.0061 | 1207927.1903
125 | 2625380.7471 | 1208000.7585 | 2625378.5597 | 1208001.0362
126 | 2625380.7471 | 1208000.7585 | 2625395.1693 | 1207998.9279
127 | 2625367.7868 | 1208002.4036 | 2625378.5597 | 1208001.0362
128 | 2625463.4616 | 1207995.2969 | 2625439.9785 | 1207993.2402 | 2625395.1693 | 1207998.9279
129 | 2625367.7868 | 1208002.4036 | 2625359.6909 | 1208003.4312
130 | 2625334.884 | 1208006.5799 | 2625359.6909 | 1208003.4312
131 | 2625334.884 | 1208006.5799 | 2625311.061 | 1208009.6038
132 | 2625691.7868 | 1208190.2823 | 2625694.9244 | 1208190.785 | 2625701.9358 | 1208185.0119 | 2625704.9025 | 1208173.974 | 2625706.7497 | 1208161.6417 | 2625711.4408 | 1208156.2367 | 2625722.3092 | 1208151.6253 | 2625732.4156 | 1208152.7027 | 2625818.9124 | 1208186.7612 | 2625867.0718 | 1208216.8862 | 2625922.7485 | 1208266.4883 | 2625922.097 | 1208288.7424 | 2625918.5837 | 1208346.8597 | 2625918.9014 | 1208368.2619 | 2625920.5072 | 1208378.3746 | 2625922.4679 | 1208390.7789 | 2625930.5001 | 1208419.5409 | 2625943.7541 | 1208467.7143 | 2625946.1085 | 1208487.5022 | 2625941.5317 | 1208508.6164 | 2625936.1251 | 1208533.5292 | 2625929.5005 | 1208557.0803 | 2625916.7284 | 1208587.1084 | 2625911.3755 | 1208597.9246 | 2625910.8225 | 1208602.7471
133 | 2625691.7868 | 1208190.2823 | 2625690.8599 | 1208195.459 | 2625688.3729 | 1208227.3933
134 | 2625910.8225 | 1208602.7471 | 2625904.6827 | 1208603.9323 | 2625894.5853 | 1208611.4706 | 2625884.0653 | 1208628.8348 | 2625883.2984 | 1208630.8471
135 | 2625688.3729 | 1208227.3933 | 2625686.5707 | 1208250.5355
136 | 2625552.4529 | 1208136.7332 | 2625553.1957 | 1208131.9254
137 | 2625686.1126 | 1208256.4172 | 2625686.5707 | 1208250.5355
138 | 2625883.2984 | 1208630.8471 | 2625880.6052 | 1208637.9138 | 2625883.9538 | 1208654.582
139 | 2625938.0088 | 1208663.4879 | 2625945.7454 | 1208665.6894 | 2625955.5362 | 1208665.7319 | 2625970.2165 | 1208665.3954 | 2625977.0839 | 1208664.6804 | 2625986.5371 | 1208663.6987 | 2626006.9433 | 1208659.4517 | 2626044.9082 | 1208650.2674 | 2626068.976 | 1208648.3489 | 2626091.3846 | 1208652.1043 | 2626112.1547 | 1208658.5542 | 2626138.6134 | 1208669.6426 | 2626147.4351 | 1208673.9948
140 | 2625938.0088 | 1208663.4879 | 2625921.5004 | 1208668.1856 | 2625913.1248 | 1208668.4079
141 | 2626212.5787 | 1208726.6206 | 2626191.462 | 1208707.4173 | 2626153.2379 | 1208682.0469 | 2626147.4351 | 1208673.9948
142 | 2625913.1248 | 1208668.4079 | 2625894.3336 | 1208668.9067
143 | 2625074.0552 | 1207907.6608 | 2625070.3349 | 1207906.8804
144 | 2624292.8215 | 1207915.4277 | 2624288.1231 | 1207921.0228 | 2624283.9753 | 1207927.7208 | 2624284.913 | 1207934.5729 | 2624286.1203 | 1207936.8235

## bus_geodata
| x | y | coords
0 | 2624079.1415 | 1207964.6578
1 | 2624134.0083 | 1207859.4091
2 | 2624045.7098 | 1208142.0376
3 | 2624008.7824 | 1208586.789
4 | 2624054.8396 | 1208596.4133
5 | 2624019.7013 | 1208558.6369
6 | 2624090.4429 | 1208371.1524
7 | 2624034.9684 | 1208158.077
8 | 2624092.7768 | 1208409.3096
9 | 2624069.3412 | 1208601.1182
10 | 2624061.39 | 1208598.5373
11 | 2624091.9241 | 1208610.4987
12 | 2624049.0259 | 1208649.1967
13 | 2624038.8877 | 1208641.7882
14 | 2624060.9245 | 1208657.947
15 | 2624146.8364 | 1209027.2243
16 | 2624312.9671 | 1209240.8838
17 | 2624028.6239 | 1208539.2755
18 | 2624131.0661 | 1207827.7612
19 | 2624011.1259 | 1208528.1363
20 | 2624015.2524 | 1208525.8993
21 | 2624079.0887 | 1208174.0522
22 | 2624092.4519 | 1208414.04
23 | 2624021.4898 | 1208629.0748
24 | 2624077.2035 | 1208670.9575
25 | 2624098.2659 | 1208613.6294
26 | 2624173.2554 | 1208152.2198
27 | 2624287.6817 | 1208259.8435
28 | 2624279.4975 | 1207947.9543
29 | 2624150.48 | 1208670.4654
30 | 2624154.2201 | 1208665.3741
31 | 2624162.8433 | 1208653.6357
32 | 2624129.3857 | 1208631.3659
33 | 2624171.6289 | 1208659.7412
34 | 2624126.0583 | 1208629.2624
35 | 2624200.3785 | 1208683.8667
36 | 2624180.7311 | 1208647.738
37 | 2624282.9778 | 1208580.2268
38 | 2624295.5347 | 1208555.6932
39 | 2624257.6957 | 1208614.6311
40 | 2624308.478 | 1208516.7604
41 | 2624243.1808 | 1208597.6455
42 | 2624202.8239 | 1208646.989
43 | 2624339.4579 | 1208515.0443
44 | 2624233.3638 | 1208585.8852
45 | 2624185.2216 | 1208646.7629
46 | 2624276.0772 | 1208756.7852
47 | 2624300.8784 | 1208745.2394
48 | 2624253.6747 | 1208734.9821
49 | 2625376.4464 | 1208793.0845
50 | 2625520.1709 | 1208393.6947
51 | 2625339.8016 | 1208813.2315
52 | 2625457.7073 | 1208933.9199
53 | 2625605.114 | 1209042.9292
54 | 2625536.5847 | 1208888.7662
55 | 2625278.8627 | 1208013.6907
56 | 2625269.1534 | 1207990.5145
57 | 2625285.9529 | 1208012.7908
58 | 2625512.2833 | 1208442.7774
59 | 2625541.0892 | 1208769.1869
60 | 2624736.2045 | 1207914.1441
61 | 2625139.6629 | 1207910.124
62 | 2624691.2741 | 1207885.7524
63 | 2625573.8247 | 1208122.1039
64 | 2625220.504 | 1207915.0115
65 | 2625122.0328 | 1207920.6692
66 | 2624464.2033 | 1208536.9066
67 | 2624472.7569 | 1208534.4588
68 | 2624456.3713 | 1208540.0598
69 | 2624357.9406 | 1208536.0946
70 | 2624305.3322 | 1208742.6766
71 | 2624248.5769 | 1208730.0253
72 | 2625858.4005 | 1208678.3292
73 | 2625877.8053 | 1208670.0863
74 | 2625844.2316 | 1208663.4623
75 | 2625332.2092 | 1208819.1448
76 | 2625545.3165 | 1208835.9875
77 | 2625295.167 | 1208011.6212
78 | 2625538.6463 | 1208782.7358
79 | 2624327.2168 | 1207898.3468
80 | 2624322.737 | 1207901.8485
81 | 2624441.9741 | 1207739.5816
82 | 2624318.0834 | 1207894.0979
83 | 2624635.2571 | 1207833.5283
84 | 2624665.7748 | 1207854.9313
85 | 2624501.853 | 1208502.2238
86 | 2625559.1692 | 1208093.2599
87 | 2625109.0971 | 1207919.4616
88 | 2624239.9164 | 1208721.6189
89 | 2624244.1183 | 1208768.4955
90 | 2624213.4667 | 1208757.7875
91 | 2624222.6098 | 1208704.8201
92 | 2624195.9058 | 1208746.8437
93 | 2624215.5335 | 1208697.9513
94 | 2624191.6158 | 1208786.2408
95 | 2624169.9587 | 1208763.3459
96 | 2624220.767 | 1208816.9415
97 | 2624167.5303 | 1208760.6002
98 | 2624158.4842 | 1208750.3721
99 | 2624180.0972 | 1208731.1487
100 | 2624148.2148 | 1208740.6262
101 | 2624091.1811 | 1208429.6665
102 | 2624091.0115 | 1208431.7516
103 | 2624039.9784 | 1208517.2532
104 | 2624130.7979 | 1208420.301
105 | 2624041.3392 | 1208546.5412
106 | 2624112.409 | 1208650.1645
107 | 2624109.5652 | 1208654.5193
108 | 2624200.3515 | 1208712.1741
109 | 2624096.4893 | 1208687.379
110 | 2624113.8675 | 1208702.1763
111 | 2624129.6189 | 1208719.9485
112 | 2624057.1279 | 1208555.5631
113 | 2624074.0448 | 1208565.2297
114 | 2624080.5487 | 1208568.9461
115 | 2624088.9727 | 1208573.7597
116 | 2624287.9084 | 1207940.1993
117 | 2625380.7471 | 1208000.7585
118 | 2625378.5597 | 1208001.0362
119 | 2625395.1693 | 1207998.9279
120 | 2625367.7868 | 1208002.4036
121 | 2625463.4616 | 1207995.2969
122 | 2625359.6909 | 1208003.4312
123 | 2625334.884 | 1208006.5799
124 | 2625691.7869 | 1208190.2823
125 | 2625910.8225 | 1208602.7471
126 | 2625688.3729 | 1208227.3933
127 | 2625553.1957 | 1208131.9254
128 | 2625686.5707 | 1208250.5355
129 | 2625686.1126 | 1208256.4172
130 | 2625883.2984 | 1208630.8471
131 | 2625938.0088 | 1208663.4879
132 | 2626147.4351 | 1208673.9948
133 | 2625913.1248 | 1208668.4079
134 | 2625883.9538 | 1208654.582
135 | 2625552.4529 | 1208136.7332
136 | 2625894.3336 | 1208668.9067
137 | 2626212.5787 | 1208726.6206
138 | 2625533.4922 | 1208802.3693
139 | 2625311.061 | 1208009.6038
140 | 2625074.0552 | 1207907.6608
141 | 2625070.3349 | 1207906.8804
142 | 2624302.0061 | 1207927.1903
143 | 2624652.887 | 1207845.8204
144 | 2624286.1203 | 1207936.8235
145 | 2624292.8215 | 1207915.4277
146 | 2624171.6289 | 1208659.7412

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1