## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1051-10_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1051-10_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1051-10_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1051-10_0_5_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_1051-10_0_5_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1051-10_0_5_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1051-10_0_5_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1051-10_0_5_node_102 | 0.4 | n |  | TRUE
8 | bus_LV_1051-10_0_5_node_59 | 0.4 | n |  | TRUE
9 | bus_LV_1051-10_0_5_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1051-10_0_5_node_88 | 0.4 | n |  | TRUE
11 | bus_LV_1051-10_0_5_node_87 | 0.4 | n |  | TRUE
12 | bus_LV_1051-10_0_5_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1051-10_0_5_node_99 | 0.4 | n |  | TRUE
14 | bus_LV_1051-10_0_5_node_100 | 0.4 | n |  | TRUE
15 | bus_LV_1051-10_0_5_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1051-10_0_5_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_1051-10_0_5_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1051-10_0_5_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_1051-10_0_5_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_1051-10_0_5_node_52 | 0.4 | n |  | TRUE
21 | bus_LV_1051-10_0_5_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_1051-10_0_5_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1051-10_0_5_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_1051-10_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1051-10_0_5_node_78 | 0.4 | n |  | TRUE
26 | bus_LV_1051-10_0_5_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_1051-10_0_5_node_43 | 0.4 | n |  | TRUE
28 | bus_LV_1051-10_0_5_node_41 | 0.4 | n |  | TRUE
29 | bus_LV_1051-10_0_5_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1051-10_0_5_node_93 | 0.4 | n |  | TRUE
31 | bus_LV_1051-10_0_5_node_92 | 0.4 | n |  | TRUE
32 | bus_LV_1051-10_0_5_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_1051-10_0_5_node_104 | 0.4 | n |  | TRUE
34 | bus_LV_1051-10_0_5_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_1051-10_0_5_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_1051-10_0_5_node_69 | 0.4 | n |  | TRUE
37 | bus_LV_1051-10_0_5_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_1051-10_0_5_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1051-10_0_5_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1051-10_0_5_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_1051-10_0_5_node_19 | 0.4 | n |  | TRUE
42 | bus_LV_1051-10_0_5_node_51 | 0.4 | n |  | TRUE
43 | bus_LV_1051-10_0_5_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_1051-10_0_5_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_1051-10_0_5_node_58 | 0.4 | n |  | TRUE
46 | bus_LV_1051-10_0_5_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_1051-10_0_5_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1051-10_0_5_node_116 | 0.4 | n |  | TRUE
49 | bus_LV_1051-10_0_5_node_114 | 0.4 | n |  | TRUE
50 | bus_LV_1051-10_0_5_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_1051-10_0_5_node_101 | 0.4 | n |  | TRUE
52 | bus_LV_1051-10_0_5_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_1051-10_0_5_node_25 | 0.4 | n |  | TRUE
54 | bus_LV_1051-10_0_5_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_1051-10_0_5_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1051-10_0_5_node_79 | 0.4 | n |  | TRUE
57 | bus_LV_1051-10_0_5_node_118 | 0.4 | n |  | TRUE
58 | bus_LV_1051-10_0_5_node_119 | 0.4 | n |  | TRUE
59 | bus_LV_1051-10_0_5_node_60 | 0.4 | n |  | TRUE
60 | bus_LV_1051-10_0_5_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_1051-10_0_5_node_103 | 0.4 | n |  | TRUE
62 | bus_LV_1051-10_0_5_node_90 | 0.4 | n |  | TRUE
63 | bus_LV_1051-10_0_5_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_1051-10_0_5_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_1051-10_0_5_node_117 | 0.4 | n |  | TRUE
66 | bus_LV_1051-10_0_5_node_96 | 0.4 | n |  | TRUE
67 | bus_LV_1051-10_0_5_node_42 | 0.4 | n |  | TRUE
68 | bus_LV_1051-10_0_5_node_82 | 0.4 | n |  | TRUE
69 | bus_LV_1051-10_0_5_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_1051-10_0_5_node_124 | 0.4 | n |  | TRUE
71 | bus_LV_1051-10_0_5_node_122 | 0.4 | n |  | TRUE
72 | bus_LV_1051-10_0_5_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_1051-10_0_5_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_1051-10_0_5_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_1051-10_0_5_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_1051-10_0_5_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_1051-10_0_5_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_1051-10_0_5_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_1051-10_0_5_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_1051-10_0_5_node_115 | 0.4 | n |  | TRUE
81 | bus_LV_1051-10_0_5_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_1051-10_0_5_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_1051-10_0_5_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_1051-10_0_5_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_1051-10_0_5_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_1051-10_0_5_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1051-10_0_5_node_121 | 0.4 | n |  | TRUE
88 | bus_LV_1051-10_0_5_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_1051-10_0_5_node_48 | 0.4 | n |  | TRUE
90 | bus_LV_1051-10_0_5_node_39 | 0.4 | n |  | TRUE
91 | bus_LV_1051-10_0_5_node_34 | 0.4 | n |  | TRUE
92 | bus_LV_1051-10_0_5_node_36 | 0.4 | n |  | TRUE
93 | bus_LV_1051-10_0_5_node_38 | 0.4 | n |  | TRUE
94 | bus_LV_1051-10_0_5_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_1051-10_0_5_node_63 | 0.4 | n |  | TRUE
96 | bus_LV_1051-10_0_5_node_40 | 0.4 | n |  | TRUE
97 | bus_LV_1051-10_0_5_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_1051-10_0_5_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1051-10_0_5_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_1051-10_0_5_node_44 | 0.4 | n |  | TRUE
101 | bus_LV_1051-10_0_5_node_64 | 0.4 | n |  | TRUE
102 | bus_LV_1051-10_0_5_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_1051-10_0_5_node_65 | 0.4 | n |  | TRUE
104 | bus_LV_1051-10_0_5_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_1051-10_0_5_node_66 | 0.4 | n |  | TRUE
106 | bus_LV_1051-10_0_5_node_67 | 0.4 | n |  | TRUE
107 | bus_LV_1051-10_0_5_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_1051-10_0_5_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_1051-10_0_5_node_75 | 0.4 | n |  | TRUE
110 | bus_LV_1051-10_0_5_node_76 | 0.4 | n |  | TRUE
111 | bus_LV_1051-10_0_5_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_1051-10_0_5_node_81 | 0.4 | n |  | TRUE
113 | bus_LV_1051-10_0_5_node_123 | 0.4 | n |  | TRUE
114 | bus_LV_1051-10_0_5_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_1051-10_0_5_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_1051-10_0_5_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_1051-10_0_5_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_1051-10_0_5_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_1051-10_0_5_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_1051-10_0_5_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_1051-10_0_5_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_1051-10_0_5_node_125 | 0.4 | n |  | TRUE
123 | bus_MV_211_0_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1051-10_0_5_load_0 | 0 | 0.0065084 | 0.0016312 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1051-10_0_5_load_102 | 7 | 0.0099439 | 0.0024922 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1051-10_0_5_load_88 | 10 | 0.010685 | 0.002678 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1051-10_0_5_load_87 | 11 | 0.010745 | 0.002693 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1051-10_0_5_load_100 | 14 | 0.0094982 | 0.0023805 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1051-10_0_5_load_29 | 16 | 0.0052399 | 0.0013132 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1051-10_0_5_load_28 | 17 | 0.0053482 | 0.0013404 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1051-10_0_5_load_53 | 19 | 0.0010946 | 0.00027432 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1051-10_0_5_load_52 | 20 | 0.00072461 | 0.0001816 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1051-10_0_5_load_78 | 25 | 0.0047182 | 0.0011825 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1051-10_0_5_load_43 | 27 | 0.0031657 | 0.00079339 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1051-10_0_5_load_41 | 28 | 0.011927 | 0.0029892 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1051-10_0_5_load_92 | 31 | 0.0034711 | 0.00086994 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1051-10_0_5_load_104 | 33 | 0.0036878 | 0.00092424 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1051-10_0_5_load_37 | 35 | 0.0046752 | 0.0011717 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1051-10_0_5_load_49 | 38 | 0.0057738 | 0.001447 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1051-10_0_5_load_46 | 40 | 0.0032262 | 0.00080857 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1051-10_0_5_load_51 | 42 | 0.0028869 | 0.00072352 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1051-10_0_5_load_55 | 43 | 0.0028903 | 0.00072439 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1051-10_0_5_load_58 | 45 | 0.0065608 | 0.0016443 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1051-10_0_5_load_56 | 46 | 0.0073787 | 0.0018493 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1051-10_0_5_load_116 | 48 | 0.0034711 | 0.00086994 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1051-10_0_5_load_54 | 50 | 0.0020497 | 0.0005137 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1051-10_0_5_load_101 | 51 | 0.0072994 | 0.0018294 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1051-10_0_5_load_30 | 55 | 0.0082553 | 0.002069 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1051-10_0_5_load_119 | 58 | 0.0046893 | 0.0011752 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1051-10_0_5_load_60 | 59 | 0.0044174 | 0.0011071 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1051-10_0_5_load_103 | 61 | 0.0027375 | 0.00068607 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1051-10_0_5_load_89 | 64 | 0.020116 | 0.0050417 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1051-10_0_5_load_117 | 65 | 0.010537 | 0.0026407 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1051-10_0_5_load_96 | 66 | 0.0030116 | 0.00075477 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1051-10_0_5_load_82 | 68 | 0.0039806 | 0.00099763 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1051-10_0_5_load_83 | 69 | 0.0027963 | 0.00070082 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1051-10_0_5_load_124 | 70 | 0.0050204 | 0.0012582 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1051-10_0_5_load_35 | 72 | 0.005658 | 0.001418 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1051-10_0_5_load_68 | 73 | 0.00057176 | 0.0001433 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1051-10_0_5_load_50 | 74 | 0.0040127 | 0.0010057 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1051-10_0_5_load_71 | 76 | 0.0036621 | 0.00091781 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1051-10_0_5_load_74 | 77 | 0.0025257 | 0.00063301 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1051-10_0_5_load_73 | 78 | 0.0025264 | 0.00063316 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1051-10_0_5_load_57 | 79 | 0.0038699 | 0.00096988 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1051-10_0_5_load_115 | 80 | 0.0038349 | 0.00096112 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1051-10_0_5_load_62 | 82 | 0.0093447 | 0.002342 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1051-10_0_5_load_61 | 83 | 0.0096895 | 0.0024284 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1051-10_0_5_load_126 | 84 | 0.0050521 | 0.0012662 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1051-10_0_5_load_120 | 86 | 0.0023454 | 0.00058782 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1051-10_0_5_load_121 | 87 | 0.0023427 | 0.00058714 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1051-10_0_5_load_34 | 91 | 0.0017214 | 0.00043143 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1051-10_0_5_load_63 | 95 | 0.010742 | 0.0026922 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1051-10_0_5_load_84 | 97 | 0.0027981 | 0.00070126 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1051-10_0_5_load_86 | 98 | 0.00857 | 0.0021478 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1051-10_0_5_load_91 | 99 | 0.0042664 | 0.0010693 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1051-10_0_5_load_44 | 100 | 0.012374 | 0.0031011 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1051-10_0_5_load_64 | 101 | 0.0048943 | 0.0012266 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1051-10_0_5_load_97 | 102 | 0.0030022 | 0.00075241 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1051-10_0_5_load_105 | 104 | 0.01346 | 0.0033733 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1051-10_0_5_load_66 | 105 | 0.0031663 | 0.00079356 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1051-10_0_5_load_67 | 106 | 0.0030002 | 0.00075193 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1051-10_0_5_load_94 | 107 | 0.0030022 | 0.00075241 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1051-10_0_5_load_95 | 108 | 0.0061694 | 0.0015462 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1051-10_0_5_load_76 | 110 | 0.0050544 | 0.0012667 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1051-10_0_5_load_77 | 111 | 0.0025268 | 0.00063327 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1051-10_0_5_load_81 | 112 | 0.0025263 | 0.00063316 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1051-10_0_5_load_123 | 113 | 0.0038385 | 0.00096202 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1051-10_0_5_load_98 | 115 | 0.0093872 | 0.0023526 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1051-10_0_5_load_107 | 117 | 0.0038355 | 0.00096126 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1051-10_0_5_load_110 | 119 | 0.0034703 | 0.00086974 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1051-10_0_5_load_112 | 120 | 0.0076734 | 0.0019231 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1051-10_0_5_load_113 | 121 | 0.0034711 | 0.00086994 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1051-10_0_5_load_125 | 122 | 0.0069387 | 0.001739 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1051-10_0_5_line_0 |  | 0 | 1 | 0.018278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1051-10_0_5_line_1 |  | 1 | 2 | 0.04201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_1051-10_0_5_line_2 |  | 1 | 3 | 0.015309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_1051-10_0_5_line_3 |  | 2 | 7 | 0.021997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1051-10_0_5_line_4 |  | 2 | 8 | 0.050691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_1051-10_0_5_line_5 |  | 3 | 51 | 0.012242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1051-10_0_5_line_6 |  | 3 | 52 | 0.037412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1051-10_0_5_line_7 |  | 4 | 5 | 0.033759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1051-10_0_5_line_8 |  | 4 | 6 | 0.017774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1051-10_0_5_line_9 |  | 5 | 56 | 0.01891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1051-10_0_5_line_10 |  | 5 | 25 | 0.011572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1051-10_0_5_line_11 |  | 6 | 57 | 0.008496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1051-10_0_5_line_12 |  | 6 | 58 | 0.008213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1051-10_0_5_line_13 |  | 8 | 59 | 0.015572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1051-10_0_5_line_14 |  | 8 | 19 | 0.034054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1051-10_0_5_line_15 |  | 9 | 10 | 0.013149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1051-10_0_5_line_16 |  | 9 | 11 | 0.01612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_1051-10_0_5_line_17 |  | 10 | 21 | 0.017717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1051-10_0_5_line_18 |  | 11 | 60 | 0.014098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1051-10_0_5_line_19 |  | 12 | 13 | 0.015752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1051-10_0_5_line_20 |  | 12 | 14 | 0.000859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1051-10_0_5_line_21 |  | 13 | 61 | 0.024768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1051-10_0_5_line_22 |  | 13 | 62 | 0.019684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1051-10_0_5_line_23 |  | 15 | 16 | 0.030059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1051-10_0_5_line_24 |  | 15 | 17 | 0.022822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1051-10_0_5_line_25 |  | 16 | 63 | 0.035997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1051-10_0_5_line_26 |  | 16 | 64 | 0.018394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1051-10_0_5_line_27 |  | 18 | 19 | 0.022054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1051-10_0_5_line_28 |  | 18 | 20 | 0.01437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1051-10_0_5_line_29 |  | 20 | 39 | 0.0090998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1051-10_0_5_line_30 |  | 21 | 22 | 0.040937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1051-10_0_5_line_31 |  | 21 | 23 | 0.0060371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1051-10_0_5_line_32 |  | 22 | 65 | 0.03939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1051-10_0_5_line_33 |  | 23 | 24 | 0.0098836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1051-10_0_5_line_34 |  | 23 | 25 | 0.018972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1051-10_0_5_line_35 |  | 24 | 31 | 0.011828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1051-10_0_5_line_36 |  | 26 | 27 | 0.042954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1051-10_0_5_line_37 |  | 26 | 28 | 0.044947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1051-10_0_5_line_38 |  | 27 | 66 | 0.0060859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1051-10_0_5_line_39 |  | 28 | 67 | 0.016595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1051-10_0_5_line_40 |  | 29 | 30 | 0.012465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1051-10_0_5_line_41 |  | 29 | 31 | 0.014929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1051-10_0_5_line_42 |  | 30 | 70 | 0.010259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1051-10_0_5_line_43 |  | 30 | 71 | 0.011169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1051-10_0_5_line_44 |  | 32 | 33 | 0.008977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1051-10_0_5_line_45 |  | 32 | 34 | 0.047859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1051-10_0_5_line_46 |  | 34 | 35 | 0.040821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1051-10_0_5_line_47 |  | 34 | 36 | 0.041566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1051-10_0_5_line_48 |  | 35 | 72 | 0.023574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1051-10_0_5_line_49 |  | 36 | 73 | 0.042474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1051-10_0_5_line_50 |  | 37 | 38 | 0.029828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1051-10_0_5_line_51 |  | 37 | 39 | 0.025887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_1051-10_0_5_line_52 |  | 37 | 40 | 0.004222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_1051-10_0_5_line_53 |  | 38 | 74 | 0.046197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1051-10_0_5_line_54 |  | 39 | 50 | 0.015082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1051-10_0_5_line_55 |  | 39 | 44 | 0.020381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1051-10_0_5_line_56 |  | 40 | 63 | 0.011562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1051-10_0_5_line_57 |  | 41 | 42 | 0.040077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1051-10_0_5_line_58 |  | 41 | 43 | 0.050088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1051-10_0_5_line_59 |  | 42 | 74 | 0.087746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1051-10_0_5_line_60 |  | 44 | 45 | 0.01514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1051-10_0_5_line_61 |  | 44 | 46 | 0.026667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1051-10_0_5_line_62 |  | 45 | 75 | 0.013545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1051-10_0_5_line_63 |  | 46 | 79 | 0.015826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1051-10_0_5_line_64 |  | 47 | 48 | 0.022296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1051-10_0_5_line_65 |  | 47 | 49 | 0.008519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1051-10_0_5_line_66 |  | 49 | 80 | 0.008886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1051-10_0_5_line_67 |  | 49 | 81 | 0.003075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1051-10_0_5_line_68 |  | 52 | 55 | 0.015423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_1051-10_0_5_line_69 |  | 53 | 54 | 0.041616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_1051-10_0_5_line_70 |  | 53 | 55 | 0.0305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_1051-10_0_5_line_71 |  | 54 | 82 | 0.045163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1051-10_0_5_line_72 |  | 54 | 83 | 0.0092865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_1051-10_0_5_line_73 |  | 56 | 84 | 0.008898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1051-10_0_5_line_74 |  | 56 | 85 | 0.010381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1051-10_0_5_line_75 |  | 57 | 86 | 0.013919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_1051-10_0_5_line_76 |  | 57 | 87 | 0.007368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1051-10_0_5_line_77 |  | 60 | 95 | 0.012692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_1051-10_0_5_line_78 |  | 62 | 104 | 0.025018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1051-10_0_5_line_79 |  | 62 | 89 | 0.015948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1051-10_0_5_line_80 |  | 63 | 88 | 0.050808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_1051-10_0_5_line_81 |  | 64 | 89 | 0.027297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1051-10_0_5_line_82 |  | 66 | 102 | 0.00029354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1051-10_0_5_line_83 |  | 67 | 100 | 0.016781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1051-10_0_5_line_84 |  | 67 | 88 | 0.032887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_1051-10_0_5_line_85 |  | 68 | 69 | 0.018617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1051-10_0_5_line_86 |  | 69 | 97 | 0.0071107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1051-10_0_5_line_87 |  | 71 | 113 | 0.007235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1051-10_0_5_line_88 |  | 71 | 114 | 0.00563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1051-10_0_5_line_89 |  | 72 | 91 | 0.024625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1051-10_0_5_line_90 |  | 73 | 93 | 0.0019245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1051-10_0_5_line_91 |  | 75 | 76 | 0.011825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1051-10_0_5_line_92 |  | 77 | 78 | 0.011374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1051-10_0_5_line_93 |  | 78 | 109 | 0.0042775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1051-10_0_5_line_94 |  | 81 | 121 | 0.012954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1051-10_0_5_line_95 |  | 81 | 116 | 0.013913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1051-10_0_5_line_96 |  | 83 | 90 | 0.032436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_1051-10_0_5_line_97 |  | 85 | 112 | 0.009814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1051-10_0_5_line_98 |  | 85 | 111 | 0.0049306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1051-10_0_5_line_99 |  | 88 | 101 | 0.02918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1051-10_0_5_line_100 |  | 90 | 95 | 0.020493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_1051-10_0_5_line_101 |  | 90 | 96 | 0.031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1051-10_0_5_line_102 |  | 90 | 92 | 0.034772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1051-10_0_5_line_103 |  | 91 | 92 | 0.019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1051-10_0_5_line_104 |  | 93 | 94 | 0.007672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1051-10_0_5_line_105 |  | 94 | 99 | 0.013302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1051-10_0_5_line_106 |  | 96 | 97 | 0.025649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1051-10_0_5_line_107 |  | 96 | 98 | 0.024956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1051-10_0_5_line_108 |  | 101 | 103 | 0.0055327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1051-10_0_5_line_109 |  | 102 | 115 | 0.0075474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1051-10_0_5_line_110 |  | 103 | 105 | 0.011535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1051-10_0_5_line_111 |  | 103 | 106 | 0.0081398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1051-10_0_5_line_112 |  | 105 | 107 | 0.012055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1051-10_0_5_line_113 |  | 106 | 108 | 0.0032647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1051-10_0_5_line_114 |  | 109 | 110 | 0.012041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1051-10_0_5_line_115 |  | 109 | 111 | 0.0044213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1051-10_0_5_line_116 |  | 114 | 122 | 0.013361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1051-10_0_5_line_117 |  | 114 | 118 | 0.002043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1051-10_0_5_line_118 |  | 116 | 117 | 0.008465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1051-10_0_5_line_119 |  | 116 | 118 | 0.011313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1051-10_0_5_line_120 |  | 118 | 119 | 0.009694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1051-10_0_5_line_121 |  | 118 | 120 | 0.010627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1051-10_0_5_trafo_120 | 0.63 MVA 20/0.4 kV | 123 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2670403.2219 | 1213566.852 | 2670401.305 | 1213558.7131 | 2670398.1526 | 1213549.3116
1 | 2670401.61 | 1213608.1478 | 2670404.7357 | 1213598.1895 | 2670405.4298 | 1213593.4503 | 2670405.3095 | 1213579.1955 | 2670403.6849 | 1213568.8142 | 2670403.2219 | 1213566.852
2 | 2670403.2219 | 1213566.852 | 2670404.1144 | 1213566.5401 | 2670407.2187 | 1213565.4761 | 2670409.8425 | 1213564.5731 | 2670410.773 | 1213564.2506 | 2670409.1253 | 1213557.1155
3 | 2670401.61 | 1213608.1478 | 2670398.833 | 1213607.2256 | 2670385.1753 | 1213602.6838 | 2670384.1691 | 1213601.6935 | 2670385.1408 | 1213598.5252
4 | 2670401.61 | 1213608.1478 | 2670400.0967 | 1213612.1436 | 2670396.0705 | 1213618.589 | 2670389.8355 | 1213624.886 | 2670380.6413 | 1213631.5484 | 2670375.0909 | 1213633.9177 | 2670367.2848 | 1213636.2493 | 2670362.7912 | 1213636.6077
5 | 2670409.1253 | 1213557.1155 | 2670414.0657 | 1213555.5951 | 2670413.4535 | 1213553.4087 | 2670418.2393 | 1213552.7537
6 | 2670397.0475 | 1213521.7063 | 2670407.0702 | 1213550.387 | 2670409.1253 | 1213557.1155
7 | 2670369.8257 | 1213460.2575 | 2670374.7182 | 1213478.8825 | 2670379.1663 | 1213492.6881
8 | 2670379.1663 | 1213492.6881 | 2670370.9976 | 1213495.4713 | 2670367.7896 | 1213496.3117 | 2670367.0724 | 1213496.5812 | 2670366.9624 | 1213498.1698 | 2670366.7091 | 1213500.9686 | 2670366.6478 | 1213501.6572
9 | 2670369.8257 | 1213460.2575 | 2670366.7292 | 1213461.2994 | 2670363.8147 | 1213464.9451 | 2670362.7439 | 1213466.8448 | 2670358.8275 | 1213464.6305 | 2670356.6488 | 1213468.3627
10 | 2670369.8257 | 1213460.2575 | 2670367.5495 | 1213448.9119
11 | 2670366.6478 | 1213501.6572 | 2670365.5107 | 1213501.4547 | 2670361.9253 | 1213500.8009 | 2670361.0396 | 1213504.4039
12 | 2670366.6478 | 1213501.6572 | 2670367.9416 | 1213504.0295 | 2670369.421 | 1213509.3392
13 | 2670362.7912 | 1213636.6077 | 2670355.5635 | 1213628.5507 | 2670358.8404 | 1213625.0872
14 | 2670362.7912 | 1213636.6077 | 2670360.244 | 1213636.8111 | 2670350.8446 | 1213635.7662 | 2670342.9169 | 1213633.5936 | 2670336.6113 | 1213631.0843 | 2670335.8463 | 1213632.176 | 2670330.6264 | 1213629.8809
15 | 2670400.8219 | 1213422.0882 | 2670388.0828 | 1213425.344
16 | 2670400.8219 | 1213422.0882 | 2670401.5638 | 1213424.8764 | 2670406.975 | 1213431.0998 | 2670411.414 | 1213433.3738
17 | 2670370.735 | 1213428.9152 | 2670384.3561 | 1213426.2965 | 2670388.0828 | 1213425.344
18 | 2670423.406 | 1213440.7665 | 2670413.884 | 1213434.6391 | 2670411.414 | 1213433.3738
19 | 2670217.5897 | 1213651.9952 | 2670209.9453 | 1213650.9267 | 2670207.9177 | 1213643.1313
20 | 2670217.9861 | 1213651.2327 | 2670217.5897 | 1213651.9952
21 | 2670192.4464 | 1213629.3961 | 2670191.4574 | 1213630.8076 | 2670193.6319 | 1213637.7376 | 2670198.6885 | 1213641.8219 | 2670207.9177 | 1213643.1313
22 | 2670207.9177 | 1213643.1313 | 2670220.1248 | 1213627.6653
23 | 2670247.7255 | 1213666.6926 | 2670253.6149 | 1213659.4018 | 2670268.5739 | 1213645.0579
24 | 2670247.7255 | 1213666.6926 | 2670262.8899 | 1213671.0072 | 2670269.5481 | 1213673.3436
25 | 2670293.7152 | 1213619.4825 | 2670288.4747 | 1213623.2675 | 2670279.5376 | 1213634.5471 | 2670268.5739 | 1213645.0579
26 | 2670268.5739 | 1213645.0579 | 2670253.9625 | 1213633.8839
27 | 2670314.0123 | 1213616.9201 | 2670316.3916 | 1213621.9291 | 2670319.6062 | 1213625.0356 | 2670330.6264 | 1213629.8809
28 | 2670314.0123 | 1213616.9201 | 2670317.9983 | 1213603.1143
29 | 2670320.5224 | 1213594.3715 | 2670317.9983 | 1213603.1143
30 | 2670378.7546 | 1213469.0017 | 2670373.5874 | 1213448.5501 | 2670370.735 | 1213428.9152
31 | 2670364.8255 | 1213430.1463 | 2670365.5869 | 1213429.9996 | 2670368.0767 | 1213429.5176 | 2670370.735 | 1213428.9152
32 | 2670404.533 | 1213482.2142 | 2670400.8987 | 1213482.4826 | 2670395.3682 | 1213480.5717 | 2670392.7089 | 1213476.7601 | 2670391.599 | 1213465.8957 | 2670383.4078 | 1213466.7218 | 2670383.0754 | 1213468.4968 | 2670378.7546 | 1213469.0017
33 | 2670357.4971 | 1213428.67 | 2670364.4181 | 1213427.3397 | 2670364.8255 | 1213430.1463
34 | 2670364.8255 | 1213430.1463 | 2670366.5613 | 1213443.9866 | 2670367.5495 | 1213448.9119
35 | 2670357.4971 | 1213428.67 | 2670356.8151 | 1213425.3154 | 2670356.5134 | 1213423.8443 | 2670355.1449 | 1213417.0787
36 | 2670199.1973 | 1213539.2745 | 2670206.0406 | 1213538.0654 | 2670211.3682 | 1213537.2053 | 2670215.9526 | 1213536.2476 | 2670219.8969 | 1213532.2248 | 2670224.9158 | 1213527.9034 | 2670229.6835 | 1213526.214 | 2670236.1019 | 1213526.9011 | 2670238.2452 | 1213527.1263
37 | 2670199.1973 | 1213539.2745 | 2670220.9046 | 1213555.0177 | 2670229.7938 | 1213560.6926 | 2670234.0634 | 1213560.0091 | 2670237.2863 | 1213559.5051
38 | 2670238.2452 | 1213527.1263 | 2670241.1094 | 1213527.4271 | 2670244.3002 | 1213527.739
39 | 2670249.8387 | 1213567.2994 | 2670248.5236 | 1213564.8046 | 2670245.4213 | 1213560.5431 | 2670241.2705 | 1213558.8821 | 2670237.2863 | 1213559.5051
40 | 2670339.9494 | 1213404.8259 | 2670341.7848 | 1213404.4361 | 2670350.3271 | 1213402.8248 | 2670352.1852 | 1213402.4464
41 | 2670352.1852 | 1213402.4464 | 2670355.1449 | 1213417.0787
42 | 2670339.9494 | 1213404.8259 | 2670339.303 | 1213394.5896
43 | 2670332.883 | 1213401.7406 | 2670334.1929 | 1213401.467 | 2670334.7099 | 1213405.9314 | 2670339.9494 | 1213404.8259
44 | 2670486.4503 | 1213610.9515 | 2670486.8494 | 1213605.4639 | 2670485.7413 | 1213602.1709
45 | 2670500.9831 | 1213589.6654 | 2670502.032 | 1213597.9608 | 2670501.9465 | 1213606.4763 | 2670500.1845 | 1213620.5754 | 2670492.1891 | 1213615.1442 | 2670486.4503 | 1213610.9515
46 | 2670500.9831 | 1213589.6654 | 2670495.3609 | 1213574.3227 | 2670483.9164 | 1213552.6819
47 | 2670501.1023 | 1213548.1074 | 2670500.9831 | 1213589.6654
48 | 2670473.9281 | 1213531.3288 | 2670483.8292 | 1213552.5171 | 2670483.9164 | 1213552.6819
49 | 2670501.1023 | 1213548.1074 | 2670498.7325 | 1213524.3199 | 2670499.8996 | 1213512.3484 | 2670504.9263 | 1213508.1643
50 | 2670307.0392 | 1213611.1009 | 2670309.6901 | 1213601.4594 | 2670313.8717 | 1213586.3325 | 2670315.0094 | 1213582.358
51 | 2670307.0392 | 1213611.1009 | 2670312.7836 | 1213606.4546 | 2670316.5 | 1213592.7787 | 2670320.5224 | 1213594.3715
52 | 2670307.0392 | 1213611.1009 | 2670303.6323 | 1213613.5946
53 | 2670325.6274 | 1213537.4624 | 2670325.2064 | 1213539.8925 | 2670323.421 | 1213551.501 | 2670319.7901 | 1213565.656 | 2670315.0094 | 1213582.358
54 | 2670334.5391 | 1213600.0404 | 2670320.5224 | 1213594.3715
55 | 2670320.5224 | 1213594.3715 | 2670326.1848 | 1213574.7926
56 | 2670293.7152 | 1213619.4825 | 2670300.3422 | 1213616.0028 | 2670303.6323 | 1213613.5946
57 | 2670276.6363 | 1213422.5129 | 2670279.0803 | 1213428.4899 | 2670285.1788 | 1213442.793 | 2670295.2376 | 1213457.8057
58 | 2670276.6363 | 1213422.5129 | 2670273.3654 | 1213422.2409 | 2670270.4757 | 1213423.7856 | 2670269.329 | 1213426.9741 | 2670271.1349 | 1213432.3098 | 2670273.0339 | 1213434.9005 | 2670270.0655 | 1213436.6778 | 2670266.6712 | 1213437.8496 | 2670265.3455 | 1213437.5338 | 2670263.3362 | 1213436.5762 | 2670259.1555 | 1213434.2144 | 2670258.302 | 1213433.8041 | 2670257.5686 | 1213434.1512 | 2670257.8537 | 1213435.0996 | 2670258.5708 | 1213436.7758 | 2670260.1382 | 1213440.4299 | 2670260.8994 | 1213444.1634 | 2670259.2073 | 1213447.2232
59 | 2670325.6274 | 1213537.4624 | 2670326.3231 | 1213533.4461 | 2670326.6634 | 1213524.5667 | 2670324.551 | 1213512.3786 | 2670322.9418 | 1213505.1884 | 2670319.9311 | 1213497.6815 | 2670312.2024 | 1213483.1257 | 2670295.2376 | 1213457.8057
60 | 2670326.1848 | 1213574.7926 | 2670330.3866 | 1213560.2473
61 | 2670326.1848 | 1213574.7926 | 2670344.0942 | 1213584.043 | 2670350.4029 | 1213582.4386
62 | 2670333.5535 | 1213547.0843 | 2670331.5782 | 1213556.1223 | 2670330.3866 | 1213560.2473
63 | 2670359.956 | 1213569.8211 | 2670350.4029 | 1213582.4386
64 | 2670299.4996 | 1213405.316 | 2670302.7945 | 1213423.5218 | 2670305.9216 | 1213425.6823
65 | 2670299.4996 | 1213405.316 | 2670307.8756 | 1213403.6359
66 | 2670307.8756 | 1213403.6359 | 2670307.8208 | 1213394.7519
67 | 2670307.8756 | 1213403.6359 | 2670310.8986 | 1213403.0267
68 | 2670397.0475 | 1213521.7063 | 2670412.2198 | 1213518.9391
69 | 2670423.528 | 1213491.5332 | 2670432.5767 | 1213519.0685 | 2670434.2214 | 1213531.5958
70 | 2670434.2214 | 1213531.5958 | 2670429.6312 | 1213533.0536 | 2670428.546 | 1213529.7387 | 2670423.3478 | 1213529.933 | 2670417.765 | 1213528.5996 | 2670415.0451 | 1213525.421 | 2670412.2198 | 1213518.9391
71 | 2670410.1661 | 1213450.3495 | 2670419.6188 | 1213460.4119 | 2670421.277 | 1213475.6633 | 2670423.528 | 1213491.5332
72 | 2670423.528 | 1213491.5332 | 2670427.733 | 1213489.2481 | 2670429.1605 | 1213484.9798
73 | 2670356.6488 | 1213468.3627 | 2670358.8107 | 1213476.9937
74 | 2670356.6488 | 1213468.3627 | 2670351.8427 | 1213464.9372 | 2670350.3645 | 1213469.178
75 | 2670361.0396 | 1213504.4039 | 2670356.7184 | 1213503.6635 | 2670355.665 | 1213507.309 | 2670356.951 | 1213512.9165
76 | 2670361.0396 | 1213504.4039 | 2670363.2813 | 1213511.4236
77 | 2670423.406 | 1213440.7665 | 2670424.3786 | 1213441.3895 | 2670433.7304 | 1213448.1459
78 | 2670220.1248 | 1213627.6653 | 2670218.1852 | 1213602.7268
79 | 2670220.1248 | 1213627.6653 | 2670232.2794 | 1213617.3019
80 | 2670278.9099 | 1213575.6805 | 2670279.2116 | 1213580.3759 | 2670279.348 | 1213587.4931 | 2670275.7544 | 1213597.2013 | 2670277.2614 | 1213598.8867 | 2670284.9411 | 1213607.9162 | 2670293.7152 | 1213619.4825
81 | 2670232.2794 | 1213617.3019 | 2670253.9625 | 1213633.8839
82 | 2670244.5923 | 1213527.7675 | 2670244.3002 | 1213527.739
83 | 2670249.8387 | 1213567.2994 | 2670265.2416 | 1213568.804 | 2670265.523 | 1213567.4843
84 | 2670278.9099 | 1213575.6805 | 2670277.3163 | 1213574.2497 | 2670275.042 | 1213573.2222 | 2670269.5346 | 1213573.224 | 2670263.066 | 1213574.2151 | 2670254.41 | 1213573.2459 | 2670251.1539 | 1213569.7943 | 2670249.8387 | 1213567.2994
85 | 2670420.5508 | 1213398.1795 | 2670435.2696 | 1213409.5797
86 | 2670440.8912 | 1213413.9338 | 2670435.2696 | 1213409.5797
87 | 2670332.883 | 1213401.7406 | 2670333.2873 | 1213394.5186
88 | 2670332.883 | 1213401.7406 | 2670327.3616 | 1213402.9207
89 | 2670473.9281 | 1213531.3288 | 2670463.503 | 1213509.0194
90 | 2670506.4054 | 1213506.933 | 2670504.9263 | 1213508.1643
91 | 2670333.5535 | 1213547.0843 | 2670340.2728 | 1213550.5991 | 2670342.4445 | 1213546.9549
92 | 2670339.4278 | 1213467.0588 | 2670336.7993 | 1213471.5751 | 2670331.867 | 1213467.9035
93 | 2670342.908 | 1213469.5459 | 2670339.4278 | 1213467.0588
94 | 2670310.8986 | 1213403.0267 | 2670313.4761 | 1213415.7206
95 | 2670316.9203 | 1213401.2966 | 2670317.9826 | 1213405.2671 | 2670314.0474 | 1213405.9212 | 2670313.2058 | 1213402.5647 | 2670310.8986 | 1213403.0267
96 | 2670448.5936 | 1213459.6202 | 2670445.1189 | 1213466.3056 | 2670435.958 | 1213474.6249 | 2670430.1663 | 1213481.9722 | 2670429.1605 | 1213484.9798
97 | 2670350.3645 | 1213469.178 | 2670352.6067 | 1213478.7327
98 | 2670350.3645 | 1213469.178 | 2670346.1792 | 1213466.5715
99 | 2670278.9099 | 1213575.6805 | 2670286.1442 | 1213561.29 | 2670292.1736 | 1213549.6899
100 | 2670448.5936 | 1213459.6202 | 2670433.3115 | 1213449.8002 | 2670434.3287 | 1213448.5781 | 2670433.7304 | 1213448.1459
101 | 2670448.5936 | 1213459.6202 | 2670449.4019 | 1213458.0732 | 2670460.6842 | 1213430.3112
102 | 2670448.5936 | 1213459.6202 | 2670449.4019 | 1213458.0732 | 2670451.1443 | 1213462.9747 | 2670455.5551 | 1213475.4235 | 2670457.1212 | 1213479.8225 | 2670459.2396 | 1213489.5425
103 | 2670459.2396 | 1213489.5425 | 2670463.4546 | 1213508.9156 | 2670463.503 | 1213509.0194
104 | 2670506.4054 | 1213506.933 | 2670508.3311 | 1213505.3326 | 2670513.1324 | 1213503.377
105 | 2670513.1324 | 1213503.377 | 2670518.1626 | 1213501.3351 | 2670525.739 | 1213499.1936
106 | 2670460.6842 | 1213430.3112 | 2670443.9851 | 1213416.3274 | 2670440.8912 | 1213413.9338
107 | 2670460.6842 | 1213430.3112 | 2670470.1874 | 1213407.2354
108 | 2670294.7252 | 1213544.7807 | 2670292.1736 | 1213549.6899
109 | 2670252.1039 | 1213528.5017 | 2670244.5923 | 1213527.7675
110 | 2670294.7252 | 1213544.7807 | 2670283.2553 | 1213543.555
111 | 2670294.7252 | 1213544.7807 | 2670295.6968 | 1213542.9132 | 2670296.9937 | 1213537.0195
112 | 2670271.7734 | 1213540.541 | 2670276.3651 | 1213542.8187 | 2670283.2553 | 1213543.555
113 | 2670297.6954 | 1213533.8311 | 2670296.9937 | 1213537.0195
114 | 2670342.908 | 1213469.5459 | 2670345.0066 | 1213473.8845 | 2670346.6023 | 1213480.9299
115 | 2670342.908 | 1213469.5459 | 2670346.1792 | 1213466.5715
116 | 2670332.5069 | 1213411.0865 | 2670331.7527 | 1213406.1189 | 2670327.9787 | 1213407.2751 | 2670327.3616 | 1213402.9207
117 | 2670325.3586 | 1213403.3529 | 2670327.3616 | 1213402.9207
118 | 2670316.9203 | 1213401.2966 | 2670314.7809 | 1213400.4152 | 2670314.139 | 1213394.2927
119 | 2670316.9203 | 1213401.2966 | 2670319.777 | 1213401.2636 | 2670320.2104 | 1213404.4484 | 2670325.3586 | 1213403.3529
120 | 2670325.3586 | 1213403.3529 | 2670326.027 | 1213413.0224
121 | 2670320.656 | 1213394.3696 | 2670322.4159 | 1213401.0167 | 2670325.3586 | 1213403.3529

## bus_geodata
| x | y | coords
0 | 2670398.1526 | 1213549.3116
1 | 2670403.2219 | 1213566.852
2 | 2670401.61 | 1213608.1478
3 | 2670409.1253 | 1213557.1155
4 | 2670379.1663 | 1213492.6881
5 | 2670369.8257 | 1213460.2575
6 | 2670366.6478 | 1213501.6572
7 | 2670385.1408 | 1213598.5252
8 | 2670362.7912 | 1213636.6077
9 | 2670400.8219 | 1213422.0882
10 | 2670388.0828 | 1213425.344
11 | 2670411.414 | 1213433.3738
12 | 2670217.5897 | 1213651.9952
13 | 2670207.9177 | 1213643.1313
14 | 2670217.9861 | 1213651.2327
15 | 2670247.7255 | 1213666.6926
16 | 2670268.5739 | 1213645.0579
17 | 2670269.5481 | 1213673.3436
18 | 2670314.0123 | 1213616.9201
19 | 2670330.6264 | 1213629.8809
20 | 2670317.9983 | 1213603.1143
21 | 2670370.735 | 1213428.9152
22 | 2670378.7546 | 1213469.0017
23 | 2670364.8255 | 1213430.1463
24 | 2670357.4971 | 1213428.67
25 | 2670367.5495 | 1213448.9119
26 | 2670199.1973 | 1213539.2745
27 | 2670238.2452 | 1213527.1263
28 | 2670237.2863 | 1213559.5051
29 | 2670352.1852 | 1213402.4464
30 | 2670339.9494 | 1213404.8259
31 | 2670355.1449 | 1213417.0787
32 | 2670486.4503 | 1213610.9515
33 | 2670485.7413 | 1213602.1709
34 | 2670500.9831 | 1213589.6654
35 | 2670483.9164 | 1213552.6819
36 | 2670501.1023 | 1213548.1074
37 | 2670307.0392 | 1213611.1009
38 | 2670315.0094 | 1213582.3581
39 | 2670320.5224 | 1213594.3715
40 | 2670303.6323 | 1213613.5946
41 | 2670276.6363 | 1213422.5129
42 | 2670295.2376 | 1213457.8057
43 | 2670259.2073 | 1213447.2232
44 | 2670326.1848 | 1213574.7926
45 | 2670330.3866 | 1213560.2473
46 | 2670350.4029 | 1213582.4386
47 | 2670299.4996 | 1213405.316
48 | 2670305.9216 | 1213425.6823
49 | 2670307.8756 | 1213403.6359
50 | 2670334.5391 | 1213600.0404
51 | 2670418.2393 | 1213552.7537
52 | 2670397.0475 | 1213521.7063
53 | 2670434.2214 | 1213531.5958
54 | 2670423.528 | 1213491.5332
55 | 2670412.2198 | 1213518.9391
56 | 2670356.6488 | 1213468.3627
57 | 2670361.0396 | 1213504.4039
58 | 2670369.421 | 1213509.3392
59 | 2670358.8404 | 1213625.0872
60 | 2670423.406 | 1213440.7665
61 | 2670192.4464 | 1213629.3961
62 | 2670220.1248 | 1213627.6653
63 | 2670293.7152 | 1213619.4825
64 | 2670253.9625 | 1213633.8839
65 | 2670404.533 | 1213482.2142
66 | 2670244.3002 | 1213527.739
67 | 2670249.8387 | 1213567.2994
68 | 2670420.5508 | 1213398.1795
69 | 2670435.2696 | 1213409.5797
70 | 2670339.303 | 1213394.5896
71 | 2670332.883 | 1213401.7406
72 | 2670473.9281 | 1213531.3288
73 | 2670504.9263 | 1213508.1643
74 | 2670325.6274 | 1213537.4624
75 | 2670333.5535 | 1213547.0843
76 | 2670342.4445 | 1213546.9549
77 | 2670331.867 | 1213467.9035
78 | 2670339.4278 | 1213467.0588
79 | 2670359.956 | 1213569.8211
80 | 2670307.8208 | 1213394.7519
81 | 2670310.8986 | 1213403.0267
82 | 2670410.1661 | 1213450.3495
83 | 2670429.1605 | 1213484.9798
84 | 2670358.8107 | 1213476.9937
85 | 2670350.3645 | 1213469.178
86 | 2670356.951 | 1213512.9165
87 | 2670363.2813 | 1213511.4236
88 | 2670278.9099 | 1213575.6805
89 | 2670232.2794 | 1213617.3019
90 | 2670448.5936 | 1213459.6202
91 | 2670463.503 | 1213509.0194
92 | 2670459.2396 | 1213489.5425
93 | 2670506.4054 | 1213506.933
94 | 2670513.1324 | 1213503.377
95 | 2670433.7304 | 1213448.1459
96 | 2670460.6842 | 1213430.3112
97 | 2670440.8912 | 1213413.9338
98 | 2670470.1874 | 1213407.2354
99 | 2670525.739 | 1213499.1936
100 | 2670265.523 | 1213567.4843
101 | 2670292.1736 | 1213549.6899
102 | 2670244.5923 | 1213527.7675
103 | 2670294.7252 | 1213544.7807
104 | 2670218.1852 | 1213602.7268
105 | 2670283.2553 | 1213543.555
106 | 2670296.9937 | 1213537.0195
107 | 2670271.7734 | 1213540.541
108 | 2670297.6954 | 1213533.8311
109 | 2670342.908 | 1213469.5459
110 | 2670346.6023 | 1213480.9299
111 | 2670346.1792 | 1213466.5715
112 | 2670352.6067 | 1213478.7327
113 | 2670333.2873 | 1213394.5186
114 | 2670327.3616 | 1213402.9207
115 | 2670252.1039 | 1213528.5017
116 | 2670316.9203 | 1213401.2966
117 | 2670314.139 | 1213394.2927
118 | 2670325.3586 | 1213403.3529
119 | 2670326.027 | 1213413.0224
120 | 2670320.656 | 1213394.3696
121 | 2670313.4761 | 1213415.7206
122 | 2670332.5069 | 1213411.0865
123 | 2670361.0396 | 1213504.4039

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98093 | -0.36541 | 0.0065084 | 0.0016312
1 | 0.98104 | -0.36325 | 0 | 0
2 | 0.97964 | -0.39038 | 0 | 0
3 | 0.98156 | -0.35302 | 0 | 0
4 | 0.99722 | -0.052552 | 0 | 0
5 | 0.99491 | -0.096515 | 0 | 0
6 | 0.99844 | -0.029487 | 0 | 0
7 | 0.97944 | -0.39436 | 0.0099439 | 0.0024922
8 | 0.97806 | -0.42139 | 0 | 0
9 | 0.99097 | -0.17162 | 0 | 0
10 | 0.99165 | -0.15859 | 0.010685 | 0.002678
11 | 0.99014 | -0.18763 | 0.010745 | 0.002693
12 | 0.97245 | -0.5317 | 0 | 0
13 | 0.97259 | -0.52894 | 0 | 0
14 | 0.97244 | -0.53185 | 0.0094982 | 0.0023805
15 | 0.97409 | -0.49927 | 0 | 0
16 | 0.97424 | -0.49632 | 0.0052399 | 0.0013132
17 | 0.97398 | -0.50151 | 0.0053482 | 0.0013404
18 | 0.97635 | -0.45483 | 0 | 0
19 | 0.97702 | -0.44172 | 0.0010946 | 0.00027432
20 | 0.97592 | -0.46338 | 0.00072461 | 0.0001816
21 | 0.99261 | -0.14039 | 0 | 0
22 | 0.99221 | -0.14802 | 0 | 0
23 | 0.99294 | -0.13397 | 0 | 0
24 | 0.99254 | -0.14184 | 0 | 0
25 | 0.99416 | -0.11081 | 0.0047182 | 0.0011825
26 | 0.97328 | -0.51536 | 0 | 0
27 | 0.97254 | -0.53005 | 0.0031657 | 0.00079339
28 | 0.97367 | -0.50768 | 0.011927 | 0.0029892
29 | 0.99148 | -0.16226 | 0 | 0
30 | 0.99101 | -0.17145 | 0 | 0
31 | 0.99205 | -0.15127 | 0.0034711 | 0.00086994
32 | 0.98559 | -0.27558 | 0 | 0
33 | 0.98556 | -0.27617 | 0.0036878 | 0.00092424
34 | 0.98575 | -0.27241 | 0 | 0
35 | 0.98607 | -0.26616 | 0.0046752 | 0.0011717
36 | 0.98557 | -0.27602 | 0 | 0
37 | 0.97498 | -0.48189 | 0 | 0
38 | 0.97454 | -0.49041 | 0.0057738 | 0.001447
39 | 0.97564 | -0.46877 | 0 | 0
40 | 0.97488 | -0.48379 | 0.0032262 | 0.00080857
41 | 0.97354 | -0.51018 | 0 | 0
42 | 0.97365 | -0.50804 | 0.0028869 | 0.00072352
43 | 0.97341 | -0.51284 | 0.0028903 | 0.00072439
44 | 0.97524 | -0.47679 | 0 | 0
45 | 0.97509 | -0.47962 | 0.0065608 | 0.0016443
46 | 0.97496 | -0.48229 | 0.0073787 | 0.0018493
47 | 0.99008 | -0.18943 | 0 | 0
48 | 0.99001 | -0.19081 | 0.0034711 | 0.00086994
49 | 0.99011 | -0.1889 | 0 | 0
50 | 0.97561 | -0.46934 | 0.0020497 | 0.0005137
51 | 0.98148 | -0.35464 | 0.0072994 | 0.0018294
52 | 0.9829 | -0.32708 | 0 | 0
53 | 0.98459 | -0.29443 | 0 | 0
54 | 0.98614 | -0.26453 | 0 | 0
55 | 0.98345 | -0.31641 | 0.0082553 | 0.002069
56 | 0.99456 | -0.10325 | 0 | 0
57 | 0.99903 | -0.018343 | 0 | 0
58 | 0.9984 | -0.030161 | 0.0046893 | 0.0011752
59 | 0.97799 | -0.42264 | 0.0044174 | 0.0011071
60 | 0.98943 | -0.20111 | 0 | 0
61 | 0.97253 | -0.53019 | 0.0027375 | 0.00068607
62 | 0.97282 | -0.52451 | 0 | 0
63 | 0.97462 | -0.48886 | 0 | 0
64 | 0.97385 | -0.50406 | 0.020116 | 0.0050417
65 | 0.99183 | -0.15537 | 0.010537 | 0.0026407
66 | 0.97245 | -0.53177 | 0.0030116 | 0.00075477
67 | 0.97376 | -0.50582 | 0 | 0
68 | 0.98695 | -0.24899 | 0.0039806 | 0.00099763
69 | 0.98702 | -0.24766 | 0.0027963 | 0.00070082
70 | 0.99096 | -0.17236 | 0.0050204 | 0.0012582
71 | 0.99063 | -0.1787 | 0 | 0
72 | 0.98636 | -0.26058 | 0.005658 | 0.001418
73 | 0.98538 | -0.27971 | 0.00057176 | 0.0001433
74 | 0.97412 | -0.49872 | 0.0040127 | 0.0010057
75 | 0.97505 | -0.48053 | 0 | 0
76 | 0.97501 | -0.48133 | 0.0036621 | 0.00091781
77 | 0.99427 | -0.1088 | 0.0025257 | 0.00063301
78 | 0.9943 | -0.10829 | 0.0025264 | 0.00063316
79 | 0.9749 | -0.48341 | 0.0038699 | 0.00096988
80 | 0.99008 | -0.18951 | 0.0038349 | 0.00096112
81 | 0.99013 | -0.1885 | 0 | 0
82 | 0.98575 | -0.2721 | 0.0093447 | 0.002342
83 | 0.9865 | -0.25756 | 0.0096895 | 0.0024284
84 | 0.99452 | -0.10404 | 0.0050521 | 0.0012662
85 | 0.99441 | -0.10602 | 0 | 0
86 | 1 | 0 | -0.3855 | -0.098602
87 | 0.99901 | -0.018645 | 0.0023427 | 0.00058714
88 | 0.97402 | -0.50064 | 0 | 0
89 | 0.9732 | -0.51696 | 0 | 0
90 | 0.98782 | -0.23212 | 0 | 0
91 | 0.98678 | -0.25227 | 0.0017214 | 0.00043143
92 | 0.98716 | -0.24492 | 0 | 0
93 | 0.98537 | -0.27986 | 0 | 0
94 | 0.98534 | -0.28044 | 0 | 0
95 | 0.9888 | -0.21326 | 0.010742 | 0.0026922
96 | 0.98729 | -0.24241 | 0 | 0
97 | 0.98707 | -0.2468 | 0.0027981 | 0.00070126
98 | 0.98709 | -0.24623 | 0.00857 | 0.0021478
99 | 0.98529 | -0.28146 | 0.0042664 | 0.0010693
100 | 0.97357 | -0.50964 | 0.012374 | 0.0031011
101 | 0.97347 | -0.51149 | 0.0048943 | 0.0012266
102 | 0.97244 | -0.53184 | 0.0030022 | 0.00075241
103 | 0.9734 | -0.51305 | 0 | 0
104 | 0.9725 | -0.53071 | 0.01346 | 0.0033733
105 | 0.97333 | -0.51436 | 0.0031663 | 0.00079356
106 | 0.97333 | -0.51443 | 0.0030002 | 0.00075193
107 | 0.9733 | -0.51503 | 0.0030022 | 0.00075241
108 | 0.97331 | -0.5148 | 0.0061694 | 0.0015462
109 | 0.99432 | -0.10791 | 0 | 0
110 | 0.99426 | -0.10898 | 0.0050544 | 0.0012667
111 | 0.99436 | -0.10712 | 0.0025268 | 0.00063327
112 | 0.99439 | -0.10646 | 0.0025263 | 0.00063316
113 | 0.99061 | -0.17919 | 0.0038385 | 0.00096202
114 | 0.99046 | -0.18197 | 0 | 0
115 | 0.97238 | -0.53315 | 0.0093872 | 0.0023526
116 | 0.99026 | -0.18584 | 0 | 0
117 | 0.99023 | -0.18642 | 0.0038355 | 0.00096126
118 | 0.99042 | -0.1829 | 0 | 0
119 | 0.99038 | -0.1835 | 0.0034703 | 0.00086974
120 | 0.99034 | -0.18435 | 0.0076734 | 0.0019231
121 | 0.99009 | -0.1893 | 0.0034711 | 0.00086994
122 | 0.99038 | -0.18361 | 0.0069387 | 0.001739
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0065084 | -0.0016312 | 0.0065091 | 0.0016314 | 6.681e-07 | 1.9683e-07 | 0.009873 | 0.0098729 | 0.009873 | 0.98093 | -0.36541 | 0.98104 | -0.36325 | 2.7124
1 | 0.17916 | 0.045322 | -0.17892 | -0.045176 | 0.00023292 | 0.00014642 | 0.27189 | 0.27189 | 0.27189 | 0.98104 | -0.36325 | 0.97964 | -0.39038 | 14.9392
2 | -0.18567 | -0.046954 | 0.18576 | 0.047011 | 9.1159e-05 | 5.7375e-05 | 0.28177 | 0.28177 | 0.28177 | 0.98104 | -0.36325 | 0.98156 | -0.35302 | 15.4816
3 | 0.0099458 | 0.0024931 | -0.0099439 | -0.0024922 | 1.8826e-06 | 9.2798e-07 | 0.015107 | 0.015107 | 0.015107 | 0.97964 | -0.39038 | 0.97944 | -0.39436 | 4.1503
4 | 0.16898 | 0.042683 | -0.16873 | -0.042526 | 0.00025069 | 0.00015726 | 0.25679 | 0.25679 | 0.25679 | 0.97964 | -0.39038 | 0.97806 | -0.42139 | 14.1092
5 | 0.0073 | 0.0018296 | -0.0072994 | -0.0018294 | 5.6223e-07 | 2.051e-07 | 0.011067 | 0.011067 | 0.011067 | 0.98156 | -0.35302 | 0.98148 | -0.35464 | 3.0403
6 | -0.19306 | -0.048841 | 0.1933 | 0.048992 | 0.00024061 | 0.00015162 | 0.29283 | 0.29283 | 0.29283 | 0.98156 | -0.35302 | 0.9829 | -0.32708 | 16.0897
7 | 0.37585 | 0.096223 | -0.37505 | -0.095714 | 0.00079841 | 0.00050879 | 0.56155 | 0.56155 | 0.56155 | 0.99722 | -0.052552 | 0.99491 | -0.096515 | 30.8544
8 | -0.37585 | -0.096223 | 0.37627 | 0.096491 | 0.00042036 | 0.00026787 | 0.56155 | 0.56155 | 0.56155 | 0.99722 | -0.052552 | 0.99844 | -0.029487 | 30.8544
9 | 0.020222 | 0.0050709 | -0.020215 | -0.005067 | 6.487e-06 | 3.9062e-06 | 0.030246 | 0.030246 | 0.030246 | 0.99491 | -0.096515 | 0.99456 | -0.10325 | 8.3092
10 | 0.35483 | 0.090643 | -0.35458 | -0.090487 | 0.00024499 | 0.00015604 | 0.53131 | 0.53131 | 0.53131 | 0.99491 | -0.096515 | 0.99416 | -0.11081 | 29.1926
11 | -0.38096 | -0.097666 | 0.38117 | 0.097797 | 0.00020597 | 0.00013126 | 0.56854 | 0.56854 | 0.56854 | 0.99844 | -0.029487 | 0.99903 | -0.018343 | 31.2384
12 | 0.0046894 | 0.0011752 | -0.0046893 | -0.0011752 | 1.5043e-07 | -1.113e-08 | 0.0069889 | 0.0069889 | 0.0069889 | 0.99844 | -0.029487 | 0.9984 | -0.030161 | 1.92
13 | 0.0044176 | 0.0011071 | -0.0044174 | -0.0011071 | 2.6378e-07 | -2.6595e-08 | 0.0067209 | 0.006721 | 0.006721 | 0.97806 | -0.42139 | 0.97799 | -0.42264 | 1.8464
14 | 0.16431 | 0.041419 | -0.16415 | -0.041319 | 0.00015972 | 0.00010008 | 0.25007 | 0.25007 | 0.25007 | 0.97806 | -0.42139 | 0.97702 | -0.44172 | 13.74
15 | -0.28259 | -0.072049 | 0.28277 | 0.072162 | 0.00017792 | 0.00011302 | 0.42477 | 0.42476 | 0.42477 | 0.99097 | -0.17162 | 0.99165 | -0.15859 | 23.3387
16 | 0.28259 | 0.072049 | -0.28237 | -0.071911 | 0.00021813 | 0.00013857 | 0.42477 | 0.42477 | 0.42477 | 0.99097 | -0.17162 | 0.99014 | -0.18763 | 23.3388
17 | -0.29345 | -0.07484 | 0.29371 | 0.075004 | 0.00025819 | 0.0001641 | 0.4408 | 0.4408 | 0.4408 | 0.99165 | -0.15859 | 0.99261 | -0.14039 | 24.2197
18 | 0.27163 | 0.069218 | -0.27145 | -0.069105 | 0.00017655 | 0.00011209 | 0.40862 | 0.40862 | 0.40862 | 0.99014 | -0.18763 | 0.98943 | -0.20111 | 22.4515
19 | -0.0094982 | -0.0023805 | 0.0094995 | 0.0023811 | 1.2478e-06 | 6.0311e-07 | 0.014534 | 0.014534 | 0.014534 | 0.97245 | -0.5317 | 0.97259 | -0.52894 | 3.9928
20 | 0.0094982 | 0.0023805 | -0.0094982 | -0.0023805 | 6.8044e-08 | 3.2891e-08 | 0.014534 | 0.014534 | 0.014534 | 0.97245 | -0.5317 | 0.97244 | -0.53185 | 3.9928
21 | 0.0027376 | 0.00068587 | -0.0027375 | -0.00068607 | 1.6294e-07 | -2.0307e-07 | 0.0041883 | 0.0041885 | 0.0041885 | 0.97259 | -0.52894 | 0.97253 | -0.53019 | 1.1507
22 | -0.012237 | -0.003067 | 0.01224 | 0.0030684 | 2.5874e-06 | 1.4116e-06 | 0.018722 | 0.018722 | 0.018722 | 0.97259 | -0.52894 | 0.97282 | -0.52451 | 5.1435
23 | -0.0053488 | -0.0013405 | 0.0053496 | 0.0013406 | 7.5253e-07 | 1.0738e-07 | 0.0081708 | 0.0081706 | 0.0081708 | 0.97409 | -0.49927 | 0.97424 | -0.49632 | 2.2447
24 | 0.0053488 | 0.0013405 | -0.0053482 | -0.0013404 | 5.7138e-07 | 8.1614e-08 | 0.0081708 | 0.0081709 | 0.0081709 | 0.97409 | -0.49927 | 0.97398 | -0.50151 | 2.2447
25 | -0.056451 | -0.014165 | 0.056471 | 0.014176 | 2.0073e-05 | 1.0605e-05 | 0.086227 | 0.086227 | 0.086227 | 0.97424 | -0.49632 | 0.97462 | -0.48886 | 4.7378
26 | 0.045862 | 0.011511 | -0.045845 | -0.011501 | 1.6926e-05 | 1.0374e-05 | 0.070054 | 0.070054 | 0.070054 | 0.97424 | -0.49632 | 0.97385 | -0.50406 | 9.6228
27 | -0.16295 | -0.04098 | 0.16306 | 0.041044 | 0.00010206 | 6.3939e-05 | 0.2484 | 0.2484 | 0.2484 | 0.97635 | -0.45483 | 0.97702 | -0.44172 | 13.6484
28 | 0.16295 | 0.04098 | -0.16289 | -0.040939 | 6.6499e-05 | 4.1661e-05 | 0.2484 | 0.2484 | 0.2484 | 0.97635 | -0.45483 | 0.97592 | -0.46338 | 13.6484
29 | 0.16216 | 0.040757 | -0.16212 | -0.040731 | 4.1738e-05 | 2.6144e-05 | 0.2473 | 0.2473 | 0.2473 | 0.97592 | -0.46338 | 0.97564 | -0.46877 | 13.5878
30 | 0.010544 | 0.0026445 | -0.01054 | -0.0026426 | 3.8359e-06 | 1.9261e-06 | 0.015807 | 0.015808 | 0.015808 | 0.99261 | -0.14039 | 0.99221 | -0.14802 | 4.3427
31 | -0.30425 | -0.077649 | 0.30435 | 0.077709 | 9.4399e-05 | 6.0025e-05 | 0.45661 | 0.45661 | 0.45661 | 0.99261 | -0.14039 | 0.99294 | -0.13397 | 25.0882
32 | 0.01054 | 0.0026426 | -0.010537 | -0.0026407 | 3.6911e-06 | 1.8537e-06 | 0.015808 | 0.015808 | 0.015808 | 0.99221 | -0.14802 | 0.99183 | -0.15537 | 4.3428
33 | 0.045127 | 0.011347 | -0.04511 | -0.011336 | 1.6957e-05 | 1.0725e-05 | 0.06764 | 0.06764 | 0.06764 | 0.99294 | -0.13397 | 0.99254 | -0.14184 | 18.5824
34 | -0.34948 | -0.089056 | 0.34987 | 0.089305 | 0.00039106 | 0.00024905 | 0.52424 | 0.52424 | 0.52424 | 0.99294 | -0.13397 | 0.99416 | -0.11081 | 28.8046
35 | 0.04511 | 0.011336 | -0.04509 | -0.011323 | 2.0292e-05 | 1.2834e-05 | 0.06764 | 0.06764 | 0.06764 | 0.99254 | -0.14184 | 0.99205 | -0.15127 | 18.5824
36 | 0.018581 | 0.004662 | -0.018568 | -0.0046543 | 1.3002e-05 | 7.7877e-06 | 0.02841 | 0.028411 | 0.028411 | 0.97328 | -0.51536 | 0.97254 | -0.53005 | 7.8051
37 | -0.018581 | -0.004662 | 0.018588 | 0.0046653 | 6.8023e-06 | 3.2359e-06 | 0.02841 | 0.02841 | 0.02841 | 0.97328 | -0.51536 | 0.97367 | -0.50768 | 3.9025
38 | 0.015403 | 0.0038609 | -0.015402 | -0.0038601 | 1.2676e-06 | 7.3572e-07 | 0.023567 | 0.023567 | 0.023567 | 0.97254 | -0.53005 | 0.97245 | -0.53177 | 6.4745
39 | -0.030515 | -0.0076545 | 0.030518 | 0.0076552 | 2.7071e-06 | 7.0046e-07 | 0.046638 | 0.046637 | 0.046638 | 0.97367 | -0.50768 | 0.97376 | -0.50582 | 2.5625
40 | 0.041597 | 0.01044 | -0.041578 | -0.010428 | 1.8221e-05 | 1.1501e-05 | 0.062434 | 0.062434 | 0.062434 | 0.99148 | -0.16226 | 0.99101 | -0.17145 | 17.1521
41 | -0.041597 | -0.01044 | 0.041618 | 0.010453 | 2.1822e-05 | 1.3773e-05 | 0.062434 | 0.062433 | 0.062434 | 0.99148 | -0.16226 | 0.99205 | -0.15127 | 17.1521
42 | 0.0050206 | 0.0012582 | -0.0050204 | -0.0012582 | 2.1863e-07 | 7.7495e-09 | 0.0075385 | 0.0075386 | 0.0075386 | 0.99101 | -0.17145 | 0.99096 | -0.17236 | 2.071
43 | 0.036558 | 0.0091698 | -0.036545 | -0.0091619 | 1.2622e-05 | 7.9339e-06 | 0.054895 | 0.054895 | 0.054895 | 0.99101 | -0.17145 | 0.99063 | -0.1787 | 15.0811
44 | 0.0036879 | 0.0009242 | -0.0036878 | -0.00092424 | 1.0436e-07 | -4.7607e-08 | 0.0055678 | 0.0055679 | 0.0055679 | 0.98559 | -0.27558 | 0.98556 | -0.27617 | 1.5296
45 | -0.0036879 | -0.0009242 | 0.0036884 | 0.00092394 | 5.5635e-07 | -2.5394e-07 | 0.0055678 | 0.0055676 | 0.0055678 | 0.98559 | -0.27558 | 0.98575 | -0.27241 | 1.5296
46 | -0.0085286 | -0.0021364 | 0.0085311 | 0.0021375 | 2.537e-06 | 1.1031e-06 | 0.012874 | 0.012874 | 0.012874 | 0.98575 | -0.27241 | 0.98607 | -0.26616 | 3.5368
47 | 0.0048402 | 0.0012125 | -0.0048393 | -0.0012125 | 8.3207e-07 | 2.7374e-09 | 0.0073062 | 0.0073064 | 0.0073064 | 0.98575 | -0.27241 | 0.98557 | -0.27602 | 2.0072
48 | -0.013206 | -0.0033093 | 0.01321 | 0.0033112 | 3.5109e-06 | 1.9462e-06 | 0.019929 | 0.019929 | 0.019929 | 0.98607 | -0.26616 | 0.98636 | -0.26058 | 5.4749
49 | 0.0048393 | 0.0012125 | -0.0048385 | -0.0012125 | 8.5028e-07 | 3.031e-09 | 0.0073064 | 0.0073065 | 0.0073065 | 0.98557 | -0.27602 | 0.98538 | -0.27971 | 2.0073
50 | 0.015577 | 0.0039061 | -0.015571 | -0.0039024 | 6.3224e-06 | 3.6745e-06 | 0.023775 | 0.023775 | 0.023775 | 0.97498 | -0.48189 | 0.97454 | -0.49041 | 6.5315
51 | -0.1385 | -0.034775 | 0.13859 | 0.034829 | 8.6767e-05 | 5.3916e-05 | 0.2114 | 0.2114 | 0.2114 | 0.97498 | -0.48189 | 0.97564 | -0.46877 | 11.6155
52 | 0.12292 | 0.030869 | -0.12291 | -0.030862 | 1.1148e-05 | 6.8712e-06 | 0.18763 | 0.18763 | 0.18763 | 0.97498 | -0.48189 | 0.97488 | -0.48379 | 10.3092
53 | 0.009797 | 0.0024553 | -0.0097931 | -0.0024534 | 3.8766e-06 | 1.9057e-06 | 0.014959 | 0.014959 | 0.014959 | 0.97454 | -0.49041 | 0.97412 | -0.49872 | 4.1096
54 | 0.0020498 | 0.00051355 | -0.0020497 | -0.0005137 | 5.5274e-08 | -1.5296e-07 | 0.0031261 | 0.0031262 | 0.0031262 | 0.97564 | -0.46877 | 0.97561 | -0.46934 | 0.85885
55 | 0.021484 | 0.0053883 | -0.021476 | -0.0053833 | 8.2069e-06 | 4.998e-06 | 0.032769 | 0.032769 | 0.032769 | 0.97564 | -0.46877 | 0.97524 | -0.47679 | 9.0024
56 | 0.11969 | 0.030054 | -0.11966 | -0.030036 | 2.8947e-05 | 1.7805e-05 | 0.1827 | 0.1827 | 0.1827 | 0.97488 | -0.48379 | 0.97462 | -0.48886 | 10.0387
57 | -0.0028907 | -0.000724 | 0.002891 | 0.00072369 | 2.9335e-07 | -3.1064e-07 | 0.0044182 | 0.004418 | 0.0044182 | 0.97354 | -0.51018 | 0.97365 | -0.50804 | 1.2138
58 | 0.0028907 | 0.000724 | -0.0028903 | -0.00072439 | 3.6667e-07 | -3.8806e-07 | 0.0044182 | 0.0044184 | 0.0044184 | 0.97354 | -0.51018 | 0.97341 | -0.51284 | 1.2138
59 | -0.0057779 | -0.0014472 | 0.0057805 | 0.0014478 | 2.5654e-06 | 5.5003e-07 | 0.00883 | 0.0088296 | 0.00883 | 0.97365 | -0.50804 | 0.97412 | -0.49872 | 2.4258
60 | 0.010225 | 0.0025627 | -0.010223 | -0.002562 | 1.3818e-06 | 6.9548e-07 | 0.015601 | 0.015601 | 0.015601 | 0.97524 | -0.47679 | 0.97509 | -0.47962 | 4.2859
61 | 0.011252 | 0.0028206 | -0.011249 | -0.0028191 | 2.9475e-06 | 1.5537e-06 | 0.017168 | 0.017168 | 0.017168 | 0.97524 | -0.47679 | 0.97496 | -0.48229 | 4.7165
62 | 0.0036624 | 0.00091768 | -0.0036622 | -0.00091775 | 1.5866e-07 | -6.7411e-08 | 0.0055888 | 0.0055889 | 0.0055889 | 0.97509 | -0.47962 | 0.97505 | -0.48053 | 1.5354
63 | 0.0038701 | 0.00096981 | -0.0038699 | -0.00096988 | 2.0705e-07 | -6.4832e-08 | 0.0059066 | 0.0059067 | 0.0059067 | 0.97496 | -0.48229 | 0.9749 | -0.48341 | 1.6227
64 | 0.0034713 | 0.0008698 | -0.0034711 | -0.00086994 | 2.2757e-07 | -1.4107e-07 | 0.0052171 | 0.0052172 | 0.0052172 | 0.99008 | -0.18943 | 0.99001 | -0.19081 | 1.4333
65 | -0.0034713 | -0.0008698 | 0.0034714 | 0.00086974 | 8.695e-08 | -5.3912e-08 | 0.0052171 | 0.005217 | 0.0052171 | 0.99008 | -0.18943 | 0.99011 | -0.1889 | 1.4333
66 | 0.003835 | 0.00096107 | -0.0038349 | -0.00096112 | 1.1069e-07 | -4.3435e-08 | 0.0057636 | 0.0057636 | 0.0057636 | 0.99011 | -0.1889 | 0.99008 | -0.18951 | 1.5834
67 | -0.0073064 | -0.0018308 | 0.0073066 | 0.0018309 | 1.3904e-07 | 4.9435e-08 | 0.010981 | 0.010981 | 0.010981 | 0.99011 | -0.1889 | 0.99013 | -0.1885 | 3.0166
68 | -0.1933 | -0.048992 | 0.1934 | 0.049055 | 9.9187e-05 | 6.2502e-05 | 0.29283 | 0.29283 | 0.29283 | 0.9829 | -0.32708 | 0.98345 | -0.31641 | 16.0896
69 | -0.20187 | -0.051258 | 0.20216 | 0.051442 | 0.00029096 | 0.00018356 | 0.30532 | 0.30532 | 0.30532 | 0.98459 | -0.29443 | 0.98614 | -0.26453 | 16.7759
70 | 0.20187 | 0.051258 | -0.20165 | -0.051124 | 0.00021324 | 0.00013454 | 0.30532 | 0.30532 | 0.30532 | 0.98459 | -0.29443 | 0.98345 | -0.31641 | 16.7759
71 | 0.009348 | 0.0023436 | -0.0093447 | -0.002342 | 3.3699e-06 | 1.5808e-06 | 0.014106 | 0.014106 | 0.014106 | 0.98614 | -0.26453 | 0.98575 | -0.2721 | 3.8753
72 | -0.2115 | -0.053786 | 0.21158 | 0.05383 | 7.1064e-05 | 4.4889e-05 | 0.31943 | 0.31943 | 0.31943 | 0.98614 | -0.26453 | 0.9865 | -0.25756 | 17.5509
73 | 0.0050523 | 0.0012662 | -0.0050521 | -0.0012662 | 1.9066e-07 | 6.5563e-09 | 0.007559 | 0.007559 | 0.007559 | 0.99456 | -0.10325 | 0.99452 | -0.10404 | 2.0766
74 | 0.015163 | 0.0038009 | -0.015161 | -0.0037997 | 2.0036e-06 | 1.1476e-06 | 0.022687 | 0.022687 | 0.022687 | 0.99456 | -0.10325 | 0.99441 | -0.10602 | 6.2326
75 | -0.38351 | -0.098384 | 0.38385 | 0.098602 | 0.00034159 | 0.0002177 | 0.57203 | 0.57203 | 0.57203 | 0.99903 | -0.018343 | 1 | 0 | 31.4301
76 | 0.0023427 | 0.00058706 | -0.0023427 | -0.00058714 | 3.3643e-08 | -7.4942e-08 | 0.0034894 | 0.0034894 | 0.0034894 | 0.99903 | -0.018343 | 0.99901 | -0.018645 | 0.95864
77 | 0.27145 | 0.069105 | -0.27129 | -0.069005 | 0.00015894 | 0.00010091 | 0.40862 | 0.40862 | 0.40862 | 0.98943 | -0.20111 | 0.9888 | -0.21326 | 22.4515
78 | 0.013464 | 0.0033756 | -0.01346 | -0.0033733 | 3.9791e-06 | 2.2361e-06 | 0.020594 | 0.020595 | 0.020595 | 0.97282 | -0.52451 | 0.9725 | -0.53071 | 5.6579
79 | -0.025703 | -0.0064439 | 0.025713 | 0.0064497 | 9.2446e-06 | 5.7185e-06 | 0.039317 | 0.039317 | 0.039317 | 0.97282 | -0.52451 | 0.9732 | -0.51696 | 10.8013
80 | 0.063185 | 0.01586 | -0.06315 | -0.01584 | 3.5469e-05 | 1.9536e-05 | 0.096478 | 0.096479 | 0.096479 | 0.97462 | -0.48886 | 0.97402 | -0.50064 | 5.301
81 | 0.025728 | 0.0064594 | -0.025713 | -0.0064497 | 1.5823e-05 | 9.7874e-06 | 0.039316 | 0.039317 | 0.039317 | 0.97385 | -0.50406 | 0.9732 | -0.51696 | 10.8012
82 | 0.01239 | 0.0031054 | -0.01239 | -0.0031053 | 3.9565e-08 | 2.168e-08 | 0.018959 | 0.018959 | 0.018959 | 0.97245 | -0.53177 | 0.97244 | -0.53184 | 5.2085
83 | 0.012376 | 0.0031023 | -0.012374 | -0.0031011 | 2.2507e-06 | 1.2318e-06 | 0.018912 | 0.018912 | 0.018912 | 0.97376 | -0.50582 | 0.97357 | -0.50964 | 5.1956
84 | -0.042894 | -0.010758 | 0.042905 | 0.010762 | 1.0598e-05 | 4.7365e-06 | 0.065549 | 0.065549 | 0.065549 | 0.97376 | -0.50582 | 0.97402 | -0.50064 | 3.6016
85 | -0.0039806 | -0.00099763 | 0.0039808 | 0.00099755 | 2.5145e-07 | -7.7e-08 | 0.0060015 | 0.0060014 | 0.0060015 | 0.98695 | -0.24899 | 0.98702 | -0.24766 | 1.6488
86 | -0.0067772 | -0.0016984 | 0.0067774 | 0.0016985 | 2.7835e-07 | 8.726e-08 | 0.010217 | 0.010217 | 0.010217 | 0.98702 | -0.24766 | 0.98707 | -0.2468 | 2.8069
87 | 0.0038386 | 0.00096198 | -0.0038385 | -0.00096202 | 9.0199e-08 | -3.5418e-08 | 0.0057659 | 0.0057659 | 0.0057659 | 0.99063 | -0.1787 | 0.99061 | -0.17919 | 1.584
88 | 0.032707 | 0.0081999 | -0.032702 | -0.0081967 | 5.0959e-06 | 3.1889e-06 | 0.049129 | 0.049129 | 0.049129 | 0.99063 | -0.1787 | 0.99046 | -0.18197 | 13.497
89 | -0.018868 | -0.0047292 | 0.018875 | 0.0047337 | 7.4818e-06 | 4.4739e-06 | 0.028464 | 0.028464 | 0.028464 | 0.98636 | -0.26058 | 0.98678 | -0.25227 | 7.8198
90 | 0.0042667 | 0.0010692 | -0.0042667 | -0.0010692 | 2.9961e-08 | -5.3404e-09 | 0.0064431 | 0.0064431 | 0.0064431 | 0.98538 | -0.27971 | 0.98537 | -0.27986 | 1.7701
91 | 0.0036622 | 0.00091775 | -0.0036621 | -0.00091781 | 1.3852e-07 | -5.8837e-08 | 0.0055889 | 0.0055889 | 0.0055889 | 0.97505 | -0.48053 | 0.97501 | -0.48133 | 1.5354
92 | -0.0025257 | -0.00063301 | 0.0025258 | 0.0006329 | 6.0944e-08 | -1.0852e-07 | 0.00378 | 0.0037799 | 0.00378 | 0.99427 | -0.1088 | 0.9943 | -0.10829 | 1.0385
93 | -0.0050522 | -0.0012661 | 0.0050522 | 0.0012661 | 9.1697e-08 | 3.2049e-09 | 0.0075608 | 0.0075607 | 0.0075608 | 0.9943 | -0.10829 | 0.99432 | -0.10791 | 2.0771
94 | 0.0034712 | 0.00086986 | -0.0034711 | -0.00086994 | 1.322e-07 | -8.1993e-08 | 0.0052167 | 0.0052168 | 0.0052168 | 0.99013 | -0.1885 | 0.99009 | -0.1893 | 1.4332
95 | -0.010778 | -0.0027007 | 0.010779 | 0.0027014 | 1.3688e-06 | 6.9704e-07 | 0.016197 | 0.016197 | 0.016197 | 0.99013 | -0.1885 | 0.99026 | -0.18584 | 4.4498
96 | -0.22127 | -0.056259 | 0.22154 | 0.056431 | 0.00027145 | 0.00017165 | 0.33404 | 0.33404 | 0.33404 | 0.9865 | -0.25756 | 0.98782 | -0.23212 | 18.3539
97 | 0.0025264 | 0.00063307 | -0.0025263 | -0.00063316 | 5.2597e-08 | -9.3654e-08 | 0.0037804 | 0.0037804 | 0.0037804 | 0.99441 | -0.10602 | 0.99439 | -0.10646 | 1.0386
98 | 0.012635 | 0.0031666 | -0.012634 | -0.0031663 | 6.6091e-07 | 3.5902e-07 | 0.018906 | 0.018906 | 0.018906 | 0.99441 | -0.10602 | 0.99436 | -0.10712 | 5.194
99 | 0.020245 | 0.0050781 | -0.020235 | -0.0050717 | 1.0468e-05 | 6.3368e-06 | 0.03093 | 0.03093 | 0.03093 | 0.97402 | -0.50064 | 0.97347 | -0.51149 | 8.4973
100 | -0.26031 | -0.066162 | 0.26055 | 0.066312 | 0.00023673 | 0.00015019 | 0.39245 | 0.39245 | 0.39245 | 0.98782 | -0.23212 | 0.9888 | -0.21326 | 21.5634
101 | 0.018158 | 0.0045545 | -0.018149 | -0.0045492 | 8.8981e-06 | 5.289e-06 | 0.027354 | 0.027354 | 0.027354 | 0.98782 | -0.23212 | 0.98729 | -0.24241 | 7.5148
102 | 0.020617 | 0.0051771 | -0.020604 | -0.0051695 | 1.2579e-05 | 7.6059e-06 | 0.03106 | 0.03106 | 0.03106 | 0.98782 | -0.23212 | 0.98716 | -0.24492 | 8.5329
103 | -0.020597 | -0.0051651 | 0.020604 | 0.0051695 | 7.214e-06 | 4.3621e-06 | 0.03106 | 0.03106 | 0.03106 | 0.98678 | -0.25227 | 0.98716 | -0.24492 | 8.5329
104 | 0.0042667 | 0.0010692 | -0.0042666 | -0.0010692 | 1.1944e-07 | -2.1285e-08 | 0.0064431 | 0.0064432 | 0.0064432 | 0.98537 | -0.27986 | 0.98534 | -0.28044 | 1.7701
105 | 0.0042666 | 0.0010692 | -0.0042664 | -0.0010693 | 2.0709e-07 | -3.6889e-08 | 0.0064432 | 0.0064432 | 0.0064432 | 0.98534 | -0.28044 | 0.98529 | -0.28146 | 1.7701
106 | 0.0095775 | 0.0024007 | -0.0095755 | -0.0023997 | 2.0042e-06 | 9.5477e-07 | 0.014435 | 0.014435 | 0.014435 | 0.98729 | -0.24241 | 0.98707 | -0.2468 | 3.9657
107 | 0.0085716 | 0.0021485 | -0.00857 | -0.0021478 | 1.5619e-06 | 6.8056e-07 | 0.012919 | 0.012919 | 0.012919 | 0.98729 | -0.24241 | 0.98709 | -0.24623 | 3.5492
108 | 0.01534 | 0.0038451 | -0.015339 | -0.0038444 | 1.1408e-06 | 6.6135e-07 | 0.023449 | 0.023449 | 0.023449 | 0.97347 | -0.51149 | 0.9734 | -0.51305 | 6.442
109 | 0.0093877 | 0.0023529 | -0.0093872 | -0.0023526 | 5.8403e-07 | 2.8015e-07 | 0.014365 | 0.014365 | 0.014365 | 0.97244 | -0.53184 | 0.97238 | -0.53315 | 3.9464
110 | 0.006169 | 0.001546 | -0.0061686 | -0.0015459 | 3.847e-07 | 1.0283e-07 | 0.0094304 | 0.0094304 | 0.0094304 | 0.9734 | -0.51305 | 0.97333 | -0.51436 | 2.5908
111 | 0.0091704 | 0.0022984 | -0.0091698 | -0.0022982 | 5.9987e-07 | 2.8274e-07 | 0.014019 | 0.014019 | 0.014019 | 0.9734 | -0.51305 | 0.97333 | -0.51443 | 3.8513
112 | 0.0030023 | 0.00075232 | -0.0030022 | -0.00075241 | 9.5234e-08 | -8.8876e-08 | 0.0045898 | 0.0045898 | 0.0045898 | 0.97333 | -0.51436 | 0.9733 | -0.51503 | 1.2609
113 | 0.0061695 | 0.0015462 | -0.0061694 | -0.0015462 | 1.0891e-07 | 2.9129e-08 | 0.0094319 | 0.0094319 | 0.0094319 | 0.97333 | -0.51443 | 0.97331 | -0.5148 | 2.5912
114 | 0.0050546 | 0.0012668 | -0.0050544 | -0.0012667 | 2.5837e-07 | 9.1866e-09 | 0.0075644 | 0.0075644 | 0.0075644 | 0.99432 | -0.10791 | 0.99426 | -0.10898 | 2.0781
115 | -0.010107 | -0.0025328 | 0.010107 | 0.002533 | 3.7929e-07 | 1.854e-07 | 0.015125 | 0.015125 | 0.015125 | 0.99432 | -0.10791 | 0.99436 | -0.10712 | 4.1552
116 | 0.0069393 | 0.0017392 | -0.0069387 | -0.001739 | 5.4456e-07 | 1.7657e-07 | 0.010425 | 0.010425 | 0.010425 | 0.99046 | -0.18197 | 0.99038 | -0.18361 | 2.8641
117 | 0.025762 | 0.0064575 | -0.025761 | -0.0064568 | 1.1477e-06 | 7.0821e-07 | 0.038704 | 0.038704 | 0.038704 | 0.99046 | -0.18197 | 0.99042 | -0.1829 | 10.633
118 | 0.0038356 | 0.00096122 | -0.0038355 | -0.00096126 | 1.0545e-07 | -4.1414e-08 | 0.0057635 | 0.0057635 | 0.0057635 | 0.99026 | -0.18584 | 0.99023 | -0.18642 | 1.5834
119 | -0.014615 | -0.0036626 | 0.014617 | 0.0036638 | 2.046e-06 | 1.1639e-06 | 0.021961 | 0.021961 | 0.021961 | 0.99026 | -0.18584 | 0.99042 | -0.1829 | 6.0332
120 | 0.0034704 | 0.00086967 | -0.0034703 | -0.00086974 | 9.8826e-08 | -6.15e-08 | 0.0052139 | 0.005214 | 0.005214 | 0.99042 | -0.1829 | 0.99038 | -0.1835 | 1.4324
121 | 0.0076739 | 0.0019233 | -0.0076734 | -0.0019231 | 5.2974e-07 | 2.0228e-07 | 0.011529 | 0.011529 | 0.011529 | 0.99042 | -0.1829 | 0.99034 | -0.18435 | 3.1674

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38785 | 0.09919

## res_load
| p_mw | q_mvar
0 | 0.0065084 | 0.0016312
1 | 0.0099439 | 0.0024922
2 | 0.010685 | 0.002678
3 | 0.010745 | 0.002693
4 | 0.0094982 | 0.0023805
5 | 0.0052399 | 0.0013132
6 | 0.0053482 | 0.0013404
7 | 0.0010946 | 0.00027432
8 | 0.00072461 | 0.0001816
9 | 0.0047182 | 0.0011825
10 | 0.0031657 | 0.00079339
11 | 0.011927 | 0.0029892
12 | 0.0034711 | 0.00086994
13 | 0.0036878 | 0.00092424
14 | 0.0046752 | 0.0011717
15 | 0.0057738 | 0.001447
16 | 0.0032262 | 0.00080857
17 | 0.0028869 | 0.00072352
18 | 0.0028903 | 0.00072439
19 | 0.0065608 | 0.0016443
20 | 0.0073787 | 0.0018493
21 | 0.0034711 | 0.00086994
22 | 0.0020497 | 0.0005137
23 | 0.0072994 | 0.0018294
24 | 0.0082553 | 0.002069
25 | 0.0046893 | 0.0011752
26 | 0.0044174 | 0.0011071
27 | 0.0027375 | 0.00068607
28 | 0.020116 | 0.0050417
29 | 0.010537 | 0.0026407
30 | 0.0030116 | 0.00075477
31 | 0.0039806 | 0.00099763
32 | 0.0027963 | 0.00070082
33 | 0.0050204 | 0.0012582
34 | 0.005658 | 0.001418
35 | 0.00057176 | 0.0001433
36 | 0.0040127 | 0.0010057
37 | 0.0036621 | 0.00091781
38 | 0.0025257 | 0.00063301
39 | 0.0025264 | 0.00063316
40 | 0.0038699 | 0.00096988
41 | 0.0038349 | 0.00096112
42 | 0.0093447 | 0.002342
43 | 0.0096895 | 0.0024284
44 | 0.0050521 | 0.0012662
45 | 0.0023454 | 0.00058782
46 | 0.0023427 | 0.00058714
47 | 0.0017214 | 0.00043143
48 | 0.010742 | 0.0026922
49 | 0.0027981 | 0.00070126
50 | 0.00857 | 0.0021478
51 | 0.0042664 | 0.0010693
52 | 0.012374 | 0.0031011
53 | 0.0048943 | 0.0012266
54 | 0.0030022 | 0.00075241
55 | 0.01346 | 0.0033733
56 | 0.0031663 | 0.00079356
57 | 0.0030002 | 0.00075193
58 | 0.0030022 | 0.00075241
59 | 0.0061694 | 0.0015462
60 | 0.0050544 | 0.0012667
61 | 0.0025268 | 0.00063327
62 | 0.0025263 | 0.00063316
63 | 0.0038385 | 0.00096202
64 | 0.0093872 | 0.0023526
65 | 0.0038355 | 0.00096126
66 | 0.0034703 | 0.00086974
67 | 0.0076734 | 0.0019231
68 | 0.0034711 | 0.00086994
69 | 0.0069387 | 0.001739

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1