## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1051-16_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_1051-16_1_2_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_1051-16_1_2_node_93 | 0.4 | n |  | TRUE
3 | bus_LV_1051-16_1_2_node_47 | 0.4 | n |  | TRUE
4 | bus_LV_1051-16_1_2_node_45 | 0.4 | n |  | TRUE
5 | bus_LV_1051-16_1_2_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1051-16_1_2_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1051-16_1_2_node_66 | 0.4 | n |  | TRUE
8 | bus_LV_1051-16_1_2_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1051-16_1_2_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1051-16_1_2_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_1051-16_1_2_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_1051-16_1_2_node_49 | 0.4 | n |  | TRUE
13 | bus_LV_1051-16_1_2_node_67 | 0.4 | n |  | TRUE
14 | bus_LV_1051-16_1_2_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1051-16_1_2_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1051-16_1_2_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_1051-16_1_2_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_1051-16_1_2_node_84 | 0.4 | n |  | TRUE
19 | bus_LV_1051-16_1_2_node_85 | 0.4 | n |  | TRUE
20 | bus_LV_1051-16_1_2_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1051-16_1_2_node_52 | 0.4 | n |  | TRUE
22 | bus_LV_1051-16_1_2_node_72 | 0.4 | n |  | TRUE
23 | bus_LV_1051-16_1_2_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_1051-16_1_2_node_79 | 0.4 | n |  | TRUE
25 | bus_LV_1051-16_1_2_node_74 | 0.4 | n |  | TRUE
26 | bus_LV_1051-16_1_2_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_1051-16_1_2_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_1051-16_1_2_node_77 | 0.4 | n |  | TRUE
29 | bus_LV_1051-16_1_2_node_54 | 0.4 | n |  | TRUE
30 | bus_LV_1051-16_1_2_node_68 | 0.4 | n |  | TRUE
31 | bus_LV_1051-16_1_2_node_69 | 0.4 | n |  | TRUE
32 | bus_LV_1051-16_1_2_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_1051-16_1_2_node_73 | 0.4 | n |  | TRUE
34 | bus_LV_1051-16_1_2_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_1051-16_1_2_node_94 | 0.4 | n |  | TRUE
36 | bus_LV_1051-16_1_2_node_95 | 0.4 | n |  | TRUE
37 | bus_LV_1051-16_1_2_node_78 | 0.4 | n |  | TRUE
38 | bus_LV_1051-16_1_2_node_81 | 0.4 | n |  | TRUE
39 | bus_LV_1051-16_1_2_node_82 | 0.4 | n |  | TRUE
40 | bus_LV_1051-16_1_2_node_80 | 0.4 | n |  | TRUE
41 | bus_LV_1051-16_1_2_node_83 | 0.4 | n |  | TRUE
42 | bus_LV_1051-16_1_2_node_86 | 0.4 | n |  | TRUE
43 | bus_LV_1051-16_1_2_node_87 | 0.4 | n |  | TRUE
44 | bus_LV_1051-16_1_2_node_88 | 0.4 | n |  | TRUE
45 | bus_LV_1051-16_1_2_node_91 | 0.4 | n |  | TRUE
46 | bus_MV_211_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1051-16_1_2_load_93 | 2 | 0.0039943 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1051-16_1_2_load_45 | 4 | 0.014911 | 0.003737 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1051-16_1_2_load_66 | 7 | 0.015542 | 0.0038951 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1051-16_1_2_load_28 | 8 | 0.0033222 | 0.00083261 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1051-16_1_2_load_37 | 10 | 0.0037472 | 0.00093914 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1051-16_1_2_load_48 | 11 | 0.010283 | 0.0025773 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1051-16_1_2_load_49 | 12 | 0.002206 | 0.00055286 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1051-16_1_2_load_67 | 13 | 0.017421 | 0.0043662 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1051-16_1_2_load_26 | 14 | 0.00587 | 0.0014712 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1051-16_1_2_load_27 | 15 | 0.0042481 | 0.0010647 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1051-16_1_2_load_29 | 16 | 0.0038979 | 0.00097692 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1051-16_1_2_load_30 | 17 | 0.0092354 | 0.0023146 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1051-16_1_2_load_84 | 18 | 0.0026308 | 0.00065933 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1051-16_1_2_load_85 | 19 | 0.0028947 | 0.00072548 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1051-16_1_2_load_53 | 20 | 0.0022605 | 0.00056653 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1051-16_1_2_load_52 | 21 | 0.0021712 | 0.00054415 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1051-16_1_2_load_79 | 24 | 0.0021306 | 0.00053398 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1051-16_1_2_load_74 | 25 | 0.0045291 | 0.0011351 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1051-16_1_2_load_76 | 26 | 0.0017549 | 0.00043982 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1051-16_1_2_load_70 | 27 | 0.0032558 | 0.00081598 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1051-16_1_2_load_77 | 28 | 0.0017549 | 0.00043982 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1051-16_1_2_load_54 | 29 | 0.0060801 | 0.0015238 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1051-16_1_2_load_68 | 30 | 0.015538 | 0.0038943 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1051-16_1_2_load_69 | 31 | 0.0043632 | 0.0010935 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1051-16_1_2_load_71 | 32 | 0.0021054 | 0.00052765 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1051-16_1_2_load_73 | 33 | 0.0022764 | 0.00057052 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1051-16_1_2_load_75 | 34 | 0.0021011 | 0.00052658 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1051-16_1_2_load_94 | 35 | 0.0021173 | 0.00053064 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1051-16_1_2_load_95 | 36 | 0.0021319 | 0.0005343 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1051-16_1_2_load_81 | 38 | 0.0018736 | 0.00046957 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1051-16_1_2_load_82 | 39 | 0.0018724 | 0.00046928 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1051-16_1_2_load_80 | 40 | 0.007125 | 0.0017857 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1051-16_1_2_load_83 | 41 | 0.0022086 | 0.00055352 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1051-16_1_2_load_86 | 42 | 0.0066299 | 0.0016616 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1051-16_1_2_load_87 | 43 | 0.0031536 | 0.00079035 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1051-16_1_2_load_88 | 44 | 0.0023089 | 0.00057867 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1051-16_1_2_load_91 | 45 | 0.0021023 | 0.00052688 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1051-16_1_2_line_0 |  | 0 | 1 | 0.01965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1051-16_1_2_line_1 |  | 0 | 2 | 0.033608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1051-16_1_2_line_2 |  | 1 | 3 | 0.028239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1051-16_1_2_line_3 |  | 1 | 4 | 0.028926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1051-16_1_2_line_4 |  | 3 | 12 | 0.011179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1051-16_1_2_line_5 |  | 5 | 6 | 0.38185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1051-16_1_2_line_6 |  | 5 | 7 | 0.016685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1051-16_1_2_line_7 |  | 6 | 8 | 0.017389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1051-16_1_2_line_8 |  | 7 | 13 | 0.013665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1051-16_1_2_line_9 |  | 8 | 14 | 0.020223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1051-16_1_2_line_10 |  | 9 | 10 | 0.0088104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1051-16_1_2_line_11 |  | 9 | 11 | 0.02064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1051-16_1_2_line_12 |  | 10 | 20 | 0.032885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1051-16_1_2_line_13 |  | 12 | 22 | 0.014843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1051-16_1_2_line_14 |  | 13 | 30 | 0.024373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1051-16_1_2_line_15 |  | 14 | 15 | 0.0027794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1051-16_1_2_line_16 |  | 15 | 16 | 0.020967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1051-16_1_2_line_17 |  | 16 | 17 | 0.010933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1051-16_1_2_line_18 |  | 17 | 18 | 0.0070277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1051-16_1_2_line_19 |  | 18 | 19 | 0.0094928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1051-16_1_2_line_20 |  | 19 | 42 | 0.038055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1051-16_1_2_line_21 |  | 19 | 21 | 0.042954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1051-16_1_2_line_22 |  | 20 | 21 | 0.0018378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1051-16_1_2_line_23 |  | 21 | 29 | 0.0049806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1051-16_1_2_line_24 |  | 22 | 25 | 0.0080621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1051-16_1_2_line_25 |  | 22 | 27 | 0.017557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1051-16_1_2_line_26 |  | 23 | 24 | 0.011716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1051-16_1_2_line_27 |  | 23 | 25 | 0.058676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1051-16_1_2_line_28 |  | 23 | 26 | 0.02211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1051-16_1_2_line_29 |  | 26 | 28 | 0.019828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1051-16_1_2_line_30 |  | 27 | 32 | 0.015455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1051-16_1_2_line_31 |  | 28 | 37 | 0.016252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1051-16_1_2_line_32 |  | 30 | 31 | 0.0078482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1051-16_1_2_line_33 |  | 32 | 33 | 0.0065123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1051-16_1_2_line_34 |  | 33 | 34 | 0.006239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1051-16_1_2_line_35 |  | 34 | 35 | 0.0065344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1051-16_1_2_line_36 |  | 35 | 36 | 0.017337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1051-16_1_2_line_37 |  | 36 | 45 | 0.0056115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1051-16_1_2_line_38 |  | 37 | 38 | 0.013307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1051-16_1_2_line_39 |  | 37 | 39 | 0.0087057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1051-16_1_2_line_40 |  | 38 | 41 | 0.00064873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1051-16_1_2_line_41 |  | 40 | 41 | 0.005751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1051-16_1_2_line_42 |  | 42 | 43 | 0.026157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1051-16_1_2_line_43 |  | 43 | 44 | 0.0041354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1051-16_1_2_line_44 |  | 44 | 45 | 0.007448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1051-16_1_2_trafo_86 | 0.63 MVA 20/0.4 kV | 46 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35
0 | 2670170.5599 | 1213115.1712 | 2670162.2666 | 1213120.1212 | 2670158.1323 | 1213115.0916 | 2670160.2313 | 1213112.3146
1 | 2670170.5599 | 1213115.1712 | 2670184.7582 | 1213121.6534 | 2670199.6885 | 1213131.7067
2 | 2670160.2313 | 1213112.3146 | 2670169.5778 | 1213085.6633
3 | 2670160.2313 | 1213112.3146 | 2670162.6743 | 1213113.2328 | 2670169.0762 | 1213111.4959 | 2670178.0633 | 1213108.2773 | 2670183.6351 | 1213107.3534 | 2670188.1211 | 1213107.5153
4 | 2670169.5778 | 1213085.6633 | 2670174.1303 | 1213075.4534
5 | 2670367.8008 | 1213201.8935 | 2670389.429 | 1213216.6913 | 2670407.593 | 1213230.8368 | 2670414.0318 | 1213239.4737 | 2670418.4357 | 1213249.9545 | 2670418.3551 | 1213259.9932 | 2670416.9376 | 1213270.0161 | 2670415.6534 | 1213275.1931 | 2670412.9476 | 1213283.0328 | 2670409.0863 | 1213291.5703 | 2670411.8228 | 1213292.7145 | 2670412.9038 | 1213293.1719 | 2670411.922 | 1213295.2506 | 2670411.8013 | 1213299.0404 | 2670413.1275 | 1213301.2463 | 2670414.3938 | 1213302.084 | 2670421.3082 | 1213301.9656 | 2670432.7357 | 1213301.1444 | 2670439.2804 | 1213300.1655 | 2670447.6018 | 1213297.9846 | 2670454.6751 | 1213294.0657 | 2670459.6601 | 1213289.4328 | 2670462.5182 | 1213285.4307 | 2670464.7569 | 1213280.4874 | 2670465.481 | 1213276.4267 | 2670465.6273 | 1213265.3326 | 2670462.2712 | 1213251.6955 | 2670456.0224 | 1213227.6288 | 2670449.3129 | 1213209.7605 | 2670440.3755 | 1213192.055 | 2670433.557 | 1213180.8341 | 2670417.8987 | 1213161.6371 | 2670409.1841 | 1213152.7176 | 2670396.7259 | 1213142.364 | 2670378.5353 | 1213129.8082 | 2670369.1123 | 1213121.6808
6 | 2670369.1123 | 1213121.6808 | 2670354.7133 | 1213113.2512
7 | 2670367.8008 | 1213201.8935 | 2670353.4509 | 1213192.0726
8 | 2670354.7133 | 1213113.2512 | 2670342.9209 | 1213106.3476
9 | 2670336.7624 | 1213180.6512 | 2670353.4509 | 1213192.0726
10 | 2670219.7813 | 1213144.7578 | 2670227.2108 | 1213149.4934
11 | 2670232.0785 | 1213128.1811 | 2670219.7813 | 1213144.7578
12 | 2670227.2108 | 1213149.4934 | 2670239.4539 | 1213157.2973 | 2670254.0036 | 1213168.5053
13 | 2670179.6069 | 1213061.6885 | 2670178.3561 | 1213065.9764 | 2670174.1303 | 1213075.4534
14 | 2670342.9209 | 1213106.3476 | 2670321.8869 | 1213094.0337
15 | 2670336.7624 | 1213180.6512 | 2670334.4687 | 1213179.0814
16 | 2670334.4687 | 1213179.0814 | 2670317.1657 | 1213167.2395
17 | 2670317.1657 | 1213167.2395 | 2670308.1434 | 1213161.0648
18 | 2670302.3439 | 1213157.0957 | 2670308.1434 | 1213161.0648
19 | 2670302.3439 | 1213157.0957 | 2670294.51 | 1213151.7343
20 | 2670294.51 | 1213151.7343 | 2670270.1566 | 1213135.0672 | 2670269.7798 | 1213126.5309
21 | 2670294.51 | 1213151.7343 | 2670255.4595 | 1213169.6269
22 | 2670255.4595 | 1213169.6269 | 2670255.4595 | 1213169.6269 | 2670254.0036 | 1213168.5053
23 | 2670254.0056 | 1213174.3905 | 2670255.4595 | 1213169.6269
24 | 2670179.6069 | 1213061.6885 | 2670181.5069 | 1213053.8534
25 | 2670179.6069 | 1213061.6885 | 2670186.6397 | 1213065.7293 | 2670194.7721 | 1213070.5346
26 | 2670199.9387 | 1212998.9105 | 2670206.616 | 1212989.2831
27 | 2670199.9387 | 1212998.9105 | 2670196.8182 | 1213001.9757 | 2670193.278 | 1213008.427 | 2670189.6755 | 1213020.1698 | 2670181.5069 | 1213053.8534
28 | 2670199.9387 | 1212998.9105 | 2670203.2138 | 1213007.8769 | 2670204.6517 | 1213020.3582
29 | 2670204.6517 | 1213020.3582 | 2670205.0197 | 1213023.5524 | 2670211.4653 | 1213032.9453 | 2670215.9312 | 1213035.6498
30 | 2670194.7721 | 1213070.5346 | 2670208.0779 | 1213078.3966
31 | 2670229.833 | 1213044.0685 | 2670215.9312 | 1213035.6498
32 | 2670315.114 | 1213090.0686 | 2670321.8869 | 1213094.0337
33 | 2670213.6846 | 1213081.7095 | 2670208.0779 | 1213078.3966
34 | 2670219.056 | 1213084.8833 | 2670213.6846 | 1213081.7095
35 | 2670219.056 | 1213084.8833 | 2670224.6817 | 1213088.2074
36 | 2670224.6817 | 1213088.2074 | 2670239.6079 | 1213097.027
37 | 2670244.439 | 1213099.8816 | 2670239.6079 | 1213097.027
38 | 2670229.833 | 1213044.0685 | 2670237.6277 | 1213040.1912 | 2670241.6088 | 1213042.4988
39 | 2670229.833 | 1213044.0685 | 2670237.6277 | 1213040.1912
40 | 2670242.1701 | 1213042.8241 | 2670242.1701 | 1213042.8241 | 2670241.6088 | 1213042.4988
41 | 2670242.1701 | 1213042.8241 | 2670241.9049 | 1213048.569
42 | 2670269.7798 | 1213126.5309 | 2670269.7009 | 1213124.7442 | 2670265.2072 | 1213117.987 | 2670254.2219 | 1213106.0083
43 | 2670250.8513 | 1213103.6705 | 2670253.5288 | 1213105.2526 | 2670254.2219 | 1213106.0083
44 | 2670250.8513 | 1213103.6705 | 2670244.439 | 1213099.8816

## bus_geodata
| x | y | coords
0 | 2670170.5599 | 1213115.1712
1 | 2670160.2313 | 1213112.3146
2 | 2670199.6885 | 1213131.7067
3 | 2670169.5778 | 1213085.6633
4 | 2670188.1211 | 1213107.5153
5 | 2670369.1123 | 1213121.6808
6 | 2670367.8008 | 1213201.8935
7 | 2670354.7133 | 1213113.2512
8 | 2670353.4509 | 1213192.0726
9 | 2670219.7813 | 1213144.7578
10 | 2670227.2108 | 1213149.4934
11 | 2670232.0785 | 1213128.1811
12 | 2670174.1303 | 1213075.4534
13 | 2670342.9209 | 1213106.3476
14 | 2670336.7624 | 1213180.6512
15 | 2670334.4687 | 1213179.0814
16 | 2670317.1657 | 1213167.2395
17 | 2670308.1434 | 1213161.0648
18 | 2670302.3439 | 1213157.0957
19 | 2670294.51 | 1213151.7343
20 | 2670254.0036 | 1213168.5053
21 | 2670255.4595 | 1213169.6269
22 | 2670179.6069 | 1213061.6885
23 | 2670199.9387 | 1212998.9105
24 | 2670206.616 | 1212989.2831
25 | 2670181.5069 | 1213053.8534
26 | 2670204.6517 | 1213020.3582
27 | 2670194.7721 | 1213070.5346
28 | 2670215.9312 | 1213035.6498
29 | 2670254.0056 | 1213174.3905
30 | 2670321.8869 | 1213094.0337
31 | 2670315.114 | 1213090.0686
32 | 2670208.0779 | 1213078.3966
33 | 2670213.6846 | 1213081.7095
34 | 2670219.056 | 1213084.8833
35 | 2670224.6817 | 1213088.2074
36 | 2670239.6079 | 1213097.027
37 | 2670229.833 | 1213044.0685
38 | 2670241.6088 | 1213042.4988
39 | 2670237.6277 | 1213040.1912
40 | 2670241.9049 | 1213048.569
41 | 2670242.1701 | 1213042.8241
42 | 2670269.7798 | 1213126.5309
43 | 2670254.2219 | 1213106.0083
44 | 2670250.8513 | 1213103.6705
45 | 2670244.439 | 1213099.8816
46 | 2670179.6069 | 1213061.6885

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99326 | -0.12969 | 0 | 0
1 | 0.99333 | -0.12831 | 0 | 0
2 | 0.99313 | -0.13207 | 0.0039943 | 0.0010011
3 | 0.99381 | -0.11888 | 0 | 0
4 | 0.99293 | -0.13593 | 0.014911 | 0.003737
5 | 0.97194 | -0.53942 | 0 | 0
6 | 0.99081 | -0.17402 | 0 | 0
7 | 0.97111 | -0.55571 | 0.015542 | 0.0038951
8 | 0.99168 | -0.1577 | 0.0033222 | 0.00083261
9 | 0.99466 | -0.10171 | 0 | 0
10 | 0.99474 | -0.10012 | 0.0037472 | 0.00093914
11 | 0.99446 | -0.10545 | 0.010283 | 0.0025773
12 | 0.99401 | -0.11515 | 0.002206 | 0.00055286
13 | 0.97064 | -0.56514 | 0.017421 | 0.0043662
14 | 0.99274 | -0.13758 | 0.00587 | 0.0014712
15 | 0.9929 | -0.13453 | 0.0042481 | 0.0010647
16 | 0.99419 | -0.10998 | 0.0038979 | 0.00097692
17 | 0.99491 | -0.096452 | 0.0092354 | 0.0023146
18 | 0.99543 | -0.086625 | 0.0026308 | 0.00065933
19 | 0.99615 | -0.072928 | 0.0028947 | 0.00072548
20 | 0.99516 | -0.091992 | 0.0022605 | 0.00056653
21 | 0.99519 | -0.091465 | 0.0021712 | 0.00054415
22 | 0.99429 | -0.10962 | 0 | 0
23 | 0.99312 | -0.13232 | 0 | 0
24 | 0.9931 | -0.13277 | 0.0021306 | 0.00053398
25 | 0.99412 | -0.11293 | 0.0045291 | 0.0011351
26 | 0.99278 | -0.13881 | 0.0017549 | 0.00043982
27 | 0.995 | -0.095899 | 0.0032558 | 0.00081598
28 | 0.99251 | -0.14401 | 0.0017549 | 0.00043982
29 | 0.99516 | -0.091998 | 0.0060801 | 0.0015238
30 | 0.97018 | -0.57412 | 0.015538 | 0.0038943
31 | 0.97015 | -0.57475 | 0.0043632 | 0.0010935
32 | 0.99568 | -0.082949 | 0.0021054 | 0.00052765
33 | 0.99597 | -0.077257 | 0.0022764 | 0.00057052
34 | 0.99627 | -0.071557 | 0.0021011 | 0.00052658
35 | 0.99659 | -0.06535 | 0.0021173 | 0.00053064
36 | 0.99748 | -0.048258 | 0.0021319 | 0.0005343
37 | 0.99232 | -0.14778 | 0 | 0
38 | 0.99218 | -0.15042 | 0.0018736 | 0.00046957
39 | 0.99231 | -0.14806 | 0.0018724 | 0.00046928
40 | 0.99214 | -0.15125 | 0.007125 | 0.0017857
41 | 0.99218 | -0.15052 | 0.0022086 | 0.00055352
42 | 1 | 0 | -0.17918 | -0.045303
43 | 0.99843 | -0.030103 | 0.0031536 | 0.00079035
44 | 0.99819 | -0.034642 | 0.0023089 | 0.00057867
45 | 0.99778 | -0.042523 | 0.0021023 | 0.00052688
46 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0039947 | -0.0010009 | 0.003995 | 0.0010008 | 2.639e-07 | -8.5451e-08 | 0.0059845 | 0.0059844 | 0.0059845 | 0.99326 | -0.12969 | 0.99333 | -0.12831 | 1.6441
1 | 0.0039947 | 0.0010009 | -0.0039943 | -0.0010011 | 4.5137e-07 | -1.4605e-07 | 0.0059845 | 0.0059846 | 0.0059846 | 0.99326 | -0.12969 | 0.99313 | -0.13207 | 1.6441
2 | -0.018911 | -0.0047409 | 0.01892 | 0.004746 | 8.4988e-06 | 5.0735e-06 | 0.02833 | 0.028329 | 0.02833 | 0.99333 | -0.12831 | 0.99381 | -0.11888 | 7.7829
3 | 0.014916 | 0.0037401 | -0.014911 | -0.003737 | 5.4162e-06 | 3.0921e-06 | 0.022345 | 0.022345 | 0.022345 | 0.99333 | -0.12831 | 0.99293 | -0.13593 | 6.1388
4 | -0.01892 | -0.004746 | 0.018923 | 0.004748 | 3.3644e-06 | 2.0083e-06 | 0.028329 | 0.028329 | 0.028329 | 0.99381 | -0.11888 | 0.99401 | -0.11515 | 7.7828
5 | -0.052931 | -0.013291 | 0.053871 | 0.013888 | 0.00094051 | 0.0005971 | 0.081045 | 0.081043 | 0.081045 | 0.97194 | -0.53942 | 0.99081 | -0.17402 | 22.2651
6 | 0.052931 | 0.013291 | -0.05289 | -0.013265 | 4.1097e-05 | 2.6095e-05 | 0.081045 | 0.081045 | 0.081045 | 0.97194 | -0.53942 | 0.97111 | -0.55571 | 22.2651
7 | -0.053871 | -0.013888 | 0.053914 | 0.013915 | 4.2829e-05 | 2.7186e-05 | 0.081043 | 0.081043 | 0.081043 | 0.99081 | -0.17402 | 0.99168 | -0.1577 | 22.2646
8 | 0.037348 | 0.0093697 | -0.037331 | -0.0093591 | 1.6784e-05 | 1.0573e-05 | 0.057231 | 0.057231 | 0.057231 | 0.97111 | -0.55571 | 0.97064 | -0.56514 | 15.7229
9 | -0.057236 | -0.014748 | 0.057292 | 0.014783 | 5.6124e-05 | 3.5658e-05 | 0.086028 | 0.086028 | 0.086028 | 0.99168 | -0.1577 | 0.99274 | -0.13758 | 23.6341
10 | -0.010285 | -0.0025782 | 0.010286 | 0.0025786 | 7.8223e-07 | 3.8626e-07 | 0.015387 | 0.015387 | 0.015387 | 0.99466 | -0.10171 | 0.99474 | -0.10012 | 4.2272
11 | 0.010285 | 0.0025782 | -0.010283 | -0.0025773 | 1.8325e-06 | 9.0498e-07 | 0.015387 | 0.015387 | 0.015387 | 0.99466 | -0.10171 | 0.99446 | -0.10545 | 4.2272
12 | -0.014033 | -0.0035177 | 0.014039 | 0.0035208 | 5.4343e-06 | 3.0509e-06 | 0.020992 | 0.020992 | 0.020992 | 0.99474 | -0.10012 | 0.99516 | -0.091992 | 5.7671
13 | -0.021129 | -0.0053009 | 0.021135 | 0.0053042 | 5.5693e-06 | 3.3719e-06 | 0.031632 | 0.031632 | 0.031632 | 0.99401 | -0.11515 | 0.99429 | -0.10962 | 8.69
14 | 0.01991 | 0.0049929 | -0.019902 | -0.0049878 | 8.5159e-06 | 5.149e-06 | 0.030524 | 0.030524 | 0.030524 | 0.97064 | -0.56514 | 0.97018 | -0.57412 | 8.3857
15 | -0.063162 | -0.016255 | 0.063172 | 0.016261 | 9.3722e-06 | 5.9623e-06 | 0.094826 | 0.094826 | 0.094826 | 0.99274 | -0.13758 | 0.9929 | -0.13453 | 26.0512
16 | -0.06742 | -0.017325 | 0.0675 | 0.017376 | 8.0514e-05 | 5.1257e-05 | 0.10119 | 0.10119 | 0.10119 | 0.9929 | -0.13453 | 0.99419 | -0.10998 | 27.8002
17 | -0.071398 | -0.018353 | 0.071445 | 0.018383 | 4.6962e-05 | 2.9914e-05 | 0.10703 | 0.10703 | 0.10703 | 0.99419 | -0.10998 | 0.99491 | -0.096452 | 29.4029
18 | -0.080681 | -0.020698 | 0.080719 | 0.020722 | 3.8482e-05 | 2.4537e-05 | 0.12084 | 0.12084 | 0.12084 | 0.99491 | -0.096452 | 0.99543 | -0.086625 | 33.1975
19 | -0.08335 | -0.021382 | 0.083405 | 0.021417 | 5.5419e-05 | 3.5344e-05 | 0.12477 | 0.12477 | 0.12477 | 0.99543 | -0.086625 | 0.99615 | -0.072928 | 34.2778
20 | -0.11087 | -0.028311 | 0.11127 | 0.028562 | 0.00039232 | 0.00025059 | 0.1658 | 0.1658 | 0.1658 | 0.99615 | -0.072928 | 1 | 0 | 45.5507
21 | 0.024573 | 0.0061689 | -0.024551 | -0.0061555 | 2.1707e-05 | 1.3334e-05 | 0.03671 | 0.03671 | 0.03671 | 0.99615 | -0.072928 | 0.99519 | -0.091465 | 10.0851
22 | -0.016299 | -0.0040873 | 0.0163 | 0.0040875 | 4.0938e-07 | 2.3812e-07 | 0.024372 | 0.024372 | 0.024372 | 0.99516 | -0.091992 | 0.99519 | -0.091465 | 6.6957
23 | 0.0060803 | 0.0015239 | -0.0060801 | -0.0015238 | 1.5437e-07 | 3.4085e-08 | 0.0090913 | 0.0090913 | 0.0090913 | 0.99519 | -0.091465 | 0.99516 | -0.091998 | 2.4976
24 | 0.023283 | 0.0058464 | -0.023279 | -0.0058441 | 3.6715e-06 | 2.2452e-06 | 0.034848 | 0.034848 | 0.034848 | 0.99429 | -0.10962 | 0.99412 | -0.11293 | 9.5737
25 | -0.044418 | -0.011151 | 0.044447 | 0.011169 | 2.9098e-05 | 1.8395e-05 | 0.06648 | 0.06648 | 0.06648 | 0.99429 | -0.10962 | 0.995 | -0.095899 | 18.2638
26 | 0.0021307 | 0.00053386 | -0.0021306 | -0.00053398 | 4.4777e-08 | -1.2294e-07 | 0.0031924 | 0.0031924 | 0.0031924 | 0.99312 | -0.13232 | 0.9931 | -0.13277 | 0.87704
27 | -0.018733 | -0.0046987 | 0.01875 | 0.004709 | 1.7336e-05 | 1.0335e-05 | 0.028069 | 0.028069 | 0.028069 | 0.99312 | -0.13232 | 0.99412 | -0.11293 | 7.7114
28 | 0.016602 | 0.0041648 | -0.016597 | -0.0041618 | 5.1311e-06 | 2.9979e-06 | 0.024877 | 0.024877 | 0.024877 | 0.99312 | -0.13232 | 0.99278 | -0.13881 | 6.8344
29 | 0.014842 | 0.003722 | -0.014839 | -0.0037199 | 3.68e-06 | 2.0989e-06 | 0.022247 | 0.022247 | 0.022247 | 0.99278 | -0.13881 | 0.99251 | -0.14401 | 6.1118
30 | -0.047703 | -0.011985 | 0.047732 | 0.012004 | 2.9504e-05 | 1.8681e-05 | 0.071349 | 0.071349 | 0.071349 | 0.995 | -0.095899 | 0.99568 | -0.082949 | 19.6014
31 | 0.013084 | 0.0032801 | -0.013081 | -0.0032788 | 2.3451e-06 | 1.2909e-06 | 0.019616 | 0.019616 | 0.019616 | 0.99251 | -0.14401 | 0.99232 | -0.14778 | 5.389
32 | 0.0043633 | 0.0010935 | -0.0043632 | -0.0010935 | 1.3181e-07 | -1.2555e-08 | 0.0066922 | 0.0066922 | 0.0066922 | 0.97018 | -0.57412 | 0.97015 | -0.57475 | 1.8385
33 | -0.049837 | -0.012531 | 0.049851 | 0.01254 | 1.3553e-05 | 8.589e-06 | 0.074495 | 0.074495 | 0.074495 | 0.99568 | -0.082949 | 0.99597 | -0.077257 | 20.4657
34 | -0.052127 | -0.01311 | 0.052142 | 0.013119 | 1.4196e-05 | 9.0045e-06 | 0.077896 | 0.077896 | 0.077896 | 0.99597 | -0.077257 | 0.99627 | -0.071557 | 21.4001
35 | -0.054243 | -0.013646 | 0.054259 | 0.013656 | 1.6091e-05 | 1.0213e-05 | 0.081034 | 0.081034 | 0.081034 | 0.99627 | -0.071557 | 0.99659 | -0.06535 | 22.2622
36 | -0.056376 | -0.014187 | 0.056422 | 0.014216 | 4.6088e-05 | 2.927e-05 | 0.084196 | 0.084196 | 0.084196 | 0.99659 | -0.06535 | 0.99748 | -0.048258 | 23.1307
37 | -0.058554 | -0.01475 | 0.05857 | 0.014761 | 1.6065e-05 | 1.0209e-05 | 0.087376 | 0.087376 | 0.087376 | 0.99748 | -0.048258 | 0.99778 | -0.042523 | 24.0044
38 | 0.011209 | 0.0028096 | -0.011207 | -0.0028089 | 1.4098e-06 | 7.304e-07 | 0.016808 | 0.016808 | 0.016808 | 0.99232 | -0.14778 | 0.99218 | -0.15042 | 4.6177
39 | 0.0018725 | 0.00046918 | -0.0018724 | -0.00046928 | 2.5738e-08 | -9.5992e-08 | 0.0028078 | 0.0028078 | 0.0028078 | 0.99232 | -0.14778 | 0.99231 | -0.14806 | 0.77138
40 | 0.0093339 | 0.0023393 | -0.0093338 | -0.0023393 | 4.7671e-08 | 2.2131e-08 | 0.013998 | 0.013998 | 0.013998 | 0.99218 | -0.15042 | 0.99218 | -0.15052 | 3.8457
41 | -0.007125 | -0.0017857 | 0.0071252 | 0.0017858 | 2.4627e-07 | 8.3343e-08 | 0.010686 | 0.010686 | 0.010686 | 0.99214 | -0.15125 | 0.99218 | -0.15052 | 2.9357
42 | 0.066267 | 0.016741 | -0.066171 | -0.01668 | 9.5462e-05 | 6.0753e-05 | 0.098653 | 0.098653 | 0.098653 | 1 | 0 | 0.99843 | -0.030103 | 27.1024
43 | 0.063018 | 0.015889 | -0.063004 | -0.015881 | 1.3689e-05 | 8.7069e-06 | 0.093953 | 0.093953 | 0.093953 | 0.99843 | -0.030103 | 0.99819 | -0.034642 | 25.8113
44 | 0.060695 | 0.015302 | -0.060672 | -0.015288 | 2.2881e-05 | 1.4547e-05 | 0.090511 | 0.090511 | 0.090511 | 0.99819 | -0.034642 | 0.99778 | -0.042523 | 24.8657

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18581 | 0.046964

## res_load
| p_mw | q_mvar
0 | 0.0039943 | 0.0010011
1 | 0.014911 | 0.003737
2 | 0.015542 | 0.0038951
3 | 0.0033222 | 0.00083261
4 | 0.0037472 | 0.00093914
5 | 0.010283 | 0.0025773
6 | 0.002206 | 0.00055286
7 | 0.017421 | 0.0043662
8 | 0.00587 | 0.0014712
9 | 0.0042481 | 0.0010647
10 | 0.0038979 | 0.00097692
11 | 0.0092354 | 0.0023146
12 | 0.0026308 | 0.00065933
13 | 0.0028947 | 0.00072548
14 | 0.0022605 | 0.00056653
15 | 0.0021712 | 0.00054415
16 | 0.0021306 | 0.00053398
17 | 0.0045291 | 0.0011351
18 | 0.0017549 | 0.00043982
19 | 0.0032558 | 0.00081598
20 | 0.0017549 | 0.00043982
21 | 0.0060801 | 0.0015238
22 | 0.015538 | 0.0038943
23 | 0.0043632 | 0.0010935
24 | 0.0021054 | 0.00052765
25 | 0.0022764 | 0.00057052
26 | 0.0021011 | 0.00052658
27 | 0.0021173 | 0.00053064
28 | 0.0021319 | 0.0005343
29 | 0.0018736 | 0.00046957
30 | 0.0018724 | 0.00046928
31 | 0.007125 | 0.0017857
32 | 0.0022086 | 0.00055352
33 | 0.0066299 | 0.0016616
34 | 0.0031536 | 0.00079035
35 | 0.0023089 | 0.00057867
36 | 0.0021023 | 0.00052688

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1