## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1051-3_1_5_node_115 | 0.4 | n |  | TRUE
1 | bus_LV_1051-3_1_5_node_116 | 0.4 | n |  | TRUE
2 | bus_LV_1051-3_1_5_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_1051-3_1_5_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_1051-3_1_5_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1051-3_1_5_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1051-3_1_5_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1051-3_1_5_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1051-3_1_5_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1051-3_1_5_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1051-3_1_5_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1051-3_1_5_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1051-3_1_5_node_19 | 0.4 | n |  | TRUE
13 | bus_LV_1051-3_1_5_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_1051-3_1_5_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1051-3_1_5_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1051-3_1_5_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_1051-3_1_5_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1051-3_1_5_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_1051-3_1_5_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1051-3_1_5_node_52 | 0.4 | n |  | TRUE
21 | bus_LV_1051-3_1_5_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1051-3_1_5_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1051-3_1_5_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1051-3_1_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1051-3_1_5_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1051-3_1_5_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_1051-3_1_5_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1051-3_1_5_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1051-3_1_5_node_68 | 0.4 | n |  | TRUE
30 | bus_LV_1051-3_1_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1051-3_1_5_node_47 | 0.4 | n |  | TRUE
32 | bus_LV_1051-3_1_5_node_53 | 0.4 | n |  | TRUE
33 | bus_LV_1051-3_1_5_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1051-3_1_5_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_1051-3_1_5_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_1051-3_1_5_node_59 | 0.4 | n |  | TRUE
37 | bus_LV_1051-3_1_5_node_144 | 0.4 | n |  | TRUE
38 | bus_LV_1051-3_1_5_node_55 | 0.4 | n |  | TRUE
39 | bus_LV_1051-3_1_5_node_148 | 0.4 | n |  | TRUE
40 | bus_LV_1051-3_1_5_node_147 | 0.4 | n |  | TRUE
41 | bus_LV_1051-3_1_5_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_1051-3_1_5_node_50 | 0.4 | n |  | TRUE
43 | bus_LV_1051-3_1_5_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1051-3_1_5_node_46 | 0.4 | n |  | TRUE
45 | bus_LV_1051-3_1_5_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1051-3_1_5_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_1051-3_1_5_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_1051-3_1_5_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_1051-3_1_5_node_94 | 0.4 | n |  | TRUE
50 | bus_LV_1051-3_1_5_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_1051-3_1_5_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_1051-3_1_5_node_132 | 0.4 | n |  | TRUE
53 | bus_LV_1051-3_1_5_node_88 | 0.4 | n |  | TRUE
54 | bus_LV_1051-3_1_5_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1051-3_1_5_node_131 | 0.4 | n |  | TRUE
56 | bus_LV_1051-3_1_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_1051-3_1_5_node_130 | 0.4 | n |  | TRUE
58 | bus_LV_1051-3_1_5_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_1051-3_1_5_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_1051-3_1_5_node_120 | 0.4 | n |  | TRUE
61 | bus_LV_1051-3_1_5_node_122 | 0.4 | n |  | TRUE
62 | bus_LV_1051-3_1_5_node_127 | 0.4 | n |  | TRUE
63 | bus_LV_1051-3_1_5_node_128 | 0.4 | n |  | TRUE
64 | bus_LV_1051-3_1_5_node_87 | 0.4 | n |  | TRUE
65 | bus_LV_1051-3_1_5_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_1051-3_1_5_node_105 | 0.4 | n |  | TRUE
67 | bus_LV_1051-3_1_5_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_1051-3_1_5_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_1051-3_1_5_node_118 | 0.4 | n |  | TRUE
70 | bus_LV_1051-3_1_5_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_1051-3_1_5_node_152 | 0.4 | n |  | TRUE
72 | bus_LV_1051-3_1_5_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_1051-3_1_5_node_133 | 0.4 | n |  | TRUE
74 | bus_LV_1051-3_1_5_node_142 | 0.4 | n |  | TRUE
75 | bus_LV_1051-3_1_5_node_139 | 0.4 | n |  | TRUE
76 | bus_LV_1051-3_1_5_node_97 | 0.4 | n |  | TRUE
77 | bus_LV_1051-3_1_5_node_95 | 0.4 | n |  | TRUE
78 | bus_LV_1051-3_1_5_node_150 | 0.4 | n |  | TRUE
79 | bus_LV_1051-3_1_5_node_149 | 0.4 | n |  | TRUE
80 | bus_LV_1051-3_1_5_node_154 | 0.4 | n |  | TRUE
81 | bus_LV_1051-3_1_5_node_134 | 0.4 | n |  | TRUE
82 | bus_LV_1051-3_1_5_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_1051-3_1_5_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_1051-3_1_5_node_63 | 0.4 | n |  | TRUE
85 | bus_LV_1051-3_1_5_node_64 | 0.4 | n |  | TRUE
86 | bus_LV_1051-3_1_5_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_1051-3_1_5_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_1051-3_1_5_node_66 | 0.4 | n |  | TRUE
89 | bus_LV_1051-3_1_5_node_129 | 0.4 | n |  | TRUE
90 | bus_LV_1051-3_1_5_node_123 | 0.4 | n |  | TRUE
91 | bus_LV_1051-3_1_5_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_1051-3_1_5_node_71 | 0.4 | n |  | TRUE
93 | bus_LV_1051-3_1_5_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_1051-3_1_5_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_1051-3_1_5_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_1051-3_1_5_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_1051-3_1_5_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_1051-3_1_5_node_101 | 0.4 | n |  | TRUE
99 | bus_LV_1051-3_1_5_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_1051-3_1_5_node_108 | 0.4 | n |  | TRUE
101 | bus_LV_1051-3_1_5_node_106 | 0.4 | n |  | TRUE
102 | bus_LV_1051-3_1_5_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_1051-3_1_5_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_1051-3_1_5_node_77 | 0.4 | n |  | TRUE
105 | bus_LV_1051-3_1_5_node_78 | 0.4 | n |  | TRUE
106 | bus_LV_1051-3_1_5_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_1051-3_1_5_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_1051-3_1_5_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_1051-3_1_5_node_83 | 0.4 | n |  | TRUE
110 | bus_LV_1051-3_1_5_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1051-3_1_5_node_153 | 0.4 | n |  | TRUE
112 | bus_LV_1051-3_1_5_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_1051-3_1_5_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_1051-3_1_5_node_103 | 0.4 | n |  | TRUE
115 | bus_LV_1051-3_1_5_node_86 | 0.4 | n |  | TRUE
116 | bus_LV_1051-3_1_5_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_1051-3_1_5_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_1051-3_1_5_node_90 | 0.4 | n |  | TRUE
119 | bus_LV_1051-3_1_5_node_113 | 0.4 | n |  | TRUE
120 | bus_LV_1051-3_1_5_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_1051-3_1_5_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_1051-3_1_5_node_96 | 0.4 | n |  | TRUE
123 | bus_LV_1051-3_1_5_node_98 | 0.4 | n |  | TRUE
124 | bus_LV_1051-3_1_5_node_99 | 0.4 | n |  | TRUE
125 | bus_LV_1051-3_1_5_node_100 | 0.4 | n |  | TRUE
126 | bus_LV_1051-3_1_5_node_124 | 0.4 | n |  | TRUE
127 | bus_LV_1051-3_1_5_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_1051-3_1_5_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_1051-3_1_5_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_1051-3_1_5_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_1051-3_1_5_node_119 | 0.4 | n |  | TRUE
132 | bus_LV_1051-3_1_5_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_1051-3_1_5_node_145 | 0.4 | n |  | TRUE
134 | bus_LV_1051-3_1_5_node_146 | 0.4 | n |  | TRUE
135 | bus_LV_1051-3_1_5_node_135 | 0.4 | n |  | TRUE
136 | bus_LV_1051-3_1_5_node_136 | 0.4 | n |  | TRUE
137 | bus_LV_1051-3_1_5_node_143 | 0.4 | n |  | TRUE
138 | bus_LV_1051-3_1_5_node_141 | 0.4 | n |  | TRUE
139 | bus_LV_1051-3_1_5_node_137 | 0.4 | n |  | TRUE
140 | bus_LV_1051-3_1_5_node_138 | 0.4 | n |  | TRUE
141 | bus_LV_1051-3_1_5_node_140 | 0.4 | n |  | TRUE
142 | bus_LV_1051-3_1_5_node_151 | 0.4 | n |  | TRUE
143 | bus_MV_211_0_node_181 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1051-3_1_5_load_115 | 0 | 0.002218 | 0.00055587 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1051-3_1_5_load_116 | 1 | 0.011115 | 0.0027856 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1051-3_1_5_load_9 | 2 | 0.0027413 | 0.00068703 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1051-3_1_5_load_10 | 3 | 0.002703 | 0.00067744 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1051-3_1_5_load_14 | 6 | 0.0023872 | 0.00059828 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1051-3_1_5_load_15 | 7 | 0.0022288 | 0.00055859 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1051-3_1_5_load_16 | 8 | 0.0024934 | 0.00062491 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1051-3_1_5_load_18 | 11 | 0.0023835 | 0.00059736 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1051-3_1_5_load_19 | 12 | 0.001858 | 0.00046567 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1051-3_1_5_load_34 | 13 | 0.0027247 | 0.00068288 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1051-3_1_5_load_31 | 15 | 0.0024477 | 0.00061345 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1051-3_1_5_load_28 | 16 | 0.0025319 | 0.00063455 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1051-3_1_5_load_32 | 18 | 0.002391 | 0.00059923 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1051-3_1_5_load_52 | 20 | 0.0022459 | 0.00056288 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1051-3_1_5_load_20 | 21 | 0.0051077 | 0.0012801 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1051-3_1_5_load_21 | 22 | 0.0014326 | 0.00035906 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1051-3_1_5_load_24 | 25 | 0.000689 | 0.00017268 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1051-3_1_5_load_27 | 28 | 0.0098246 | 0.0024623 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1051-3_1_5_load_68 | 29 | 0.0026738 | 0.00067012 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1051-3_1_5_load_47 | 31 | 0.0034611 | 0.00086742 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1051-3_1_5_load_53 | 32 | 0.0017277 | 0.000433 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1051-3_1_5_load_48 | 34 | 0.0023385 | 0.00058609 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1051-3_1_5_load_144 | 37 | 0.0014998 | 0.00037589 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1051-3_1_5_load_147 | 40 | 0.013898 | 0.0034831 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1051-3_1_5_load_54 | 41 | 0.0049643 | 0.0012442 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1051-3_1_5_load_50 | 42 | 0.0010907 | 0.00027337 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1051-3_1_5_load_46 | 44 | 0.0043058 | 0.0010791 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1051-3_1_5_load_94 | 49 | 0.018021 | 0.0045166 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1051-3_1_5_load_132 | 52 | 0.0098319 | 0.0024641 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1051-3_1_5_load_131 | 55 | 0.010246 | 0.0025678 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1051-3_1_5_load_130 | 57 | 0.0043755 | 0.0010966 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1051-3_1_5_load_45 | 59 | 0.0019963 | 0.00050031 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1051-3_1_5_load_127 | 62 | 0.0015141 | 0.00037947 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1051-3_1_5_load_128 | 63 | 0.0043751 | 0.0010965 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1051-3_1_5_load_102 | 65 | 0.0025954 | 0.00065048 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1051-3_1_5_load_105 | 66 | 0.017688 | 0.004433 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1051-3_1_5_load_84 | 67 | 0.0022991 | 0.0005762 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1051-3_1_5_load_85 | 68 | 0.0023008 | 0.00057664 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1051-3_1_5_load_118 | 69 | 0.0019972 | 0.00050054 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1051-3_1_5_load_51 | 70 | 0.0011263 | 0.00028228 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1051-3_1_5_load_152 | 71 | 0.001183 | 0.00029648 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1051-3_1_5_load_60 | 72 | 0.0015096 | 0.00037835 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1051-3_1_5_load_133 | 73 | 0.0015137 | 0.00037938 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1051-3_1_5_load_142 | 74 | 0.0014991 | 0.00037572 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1051-3_1_5_load_97 | 76 | 0.002076 | 0.00052029 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1051-3_1_5_load_95 | 77 | 0.002076 | 0.00052029 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1051-3_1_5_load_154 | 80 | 0.027856 | 0.0069813 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1051-3_1_5_load_134 | 81 | 0.0014345 | 0.00035952 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1051-3_1_5_load_61 | 82 | 0.0026719 | 0.00066964 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1051-3_1_5_load_62 | 83 | 0.0019962 | 0.00050029 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1051-3_1_5_load_63 | 84 | 0.0019952 | 0.00050005 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1051-3_1_5_load_64 | 85 | 0.006342 | 0.0015894 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1051-3_1_5_load_65 | 86 | 0.0019745 | 0.00049485 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1051-3_1_5_load_67 | 87 | 0.0026734 | 0.00067001 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1051-3_1_5_load_66 | 88 | 0.0021269 | 0.00053306 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1051-3_1_5_load_129 | 89 | 0.0019962 | 0.00050029 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1051-3_1_5_load_123 | 90 | 0.0021269 | 0.00053306 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1051-3_1_5_load_70 | 91 | 0.0021224 | 0.00053193 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1051-3_1_5_load_71 | 92 | 0.0021238 | 0.00053229 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1051-3_1_5_load_72 | 93 | 0.0021253 | 0.00053264 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1051-3_1_5_load_73 | 94 | 0.0021252 | 0.00053264 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1051-3_1_5_load_74 | 95 | 0.0021238 | 0.00053229 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1051-3_1_5_load_76 | 97 | 0.0025413 | 0.0006369 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1051-3_1_5_load_101 | 98 | 0.0020623 | 0.00051687 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1051-3_1_5_load_108 | 100 | 0.0025937 | 0.00065004 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1051-3_1_5_load_106 | 101 | 0.0041219 | 0.001033 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1051-3_1_5_load_107 | 103 | 0.0025954 | 0.00065048 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1051-3_1_5_load_77 | 104 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1051-3_1_5_load_78 | 105 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1051-3_1_5_load_79 | 106 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1051-3_1_5_load_80 | 107 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1051-3_1_5_load_81 | 108 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1051-3_1_5_load_83 | 109 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1051-3_1_5_load_153 | 111 | 0.0028495 | 0.00071415 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1051-3_1_5_load_103 | 114 | 0.0025954 | 0.00065048 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1051-3_1_5_load_112 | 116 | 0.0053328 | 0.0013365 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1051-3_1_5_load_110 | 117 | 0.0037016 | 0.00092771 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1051-3_1_5_load_90 | 118 | 0.0042241 | 0.0010587 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1051-3_1_5_load_113 | 119 | 0.0020586 | 0.00051593 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1051-3_1_5_load_126 | 120 | 0.0059602 | 0.0014938 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1051-3_1_5_load_109 | 121 | 0.0030586 | 0.00076656 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1051-3_1_5_load_96 | 122 | 0.0020757 | 0.00052022 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1051-3_1_5_load_98 | 123 | 0.002074 | 0.0005198 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1051-3_1_5_load_99 | 124 | 0.0020784 | 0.0005209 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1051-3_1_5_load_100 | 125 | 0.002076 | 0.00052029 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1051-3_1_5_load_124 | 126 | 0.0020757 | 0.00052022 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1051-3_1_5_load_111 | 128 | 0.012756 | 0.003197 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1051-3_1_5_load_125 | 129 | 0.002074 | 0.0005198 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1051-3_1_5_load_117 | 130 | 0.0021269 | 0.00053306 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1051-3_1_5_load_119 | 131 | 0.0021285 | 0.00053344 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1051-3_1_5_load_121 | 132 | 0.0019972 | 0.00050055 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1051-3_1_5_load_145 | 133 | 0.0043784 | 0.0010973 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1051-3_1_5_load_146 | 134 | 0.013134 | 0.0032916 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1051-3_1_5_load_135 | 135 | 0.0015121 | 0.00037898 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1051-3_1_5_load_136 | 136 | 0.001433 | 0.00035915 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1051-3_1_5_load_143 | 137 | 0.0015093 | 0.00037826 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1051-3_1_5_load_141 | 138 | 0.001433 | 0.00035914 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1051-3_1_5_load_137 | 139 | 0.0015096 | 0.00037835 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1051-3_1_5_load_138 | 140 | 0.0019724 | 0.00049433 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1051-3_1_5_load_140 | 141 | 0.009494 | 0.0023794 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1051-3_1_5_load_151 | 142 | 0.007063 | 0.0017701 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1051-3_1_5_line_0 |  | 0 | 1 | 0.12612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1051-3_1_5_line_1 |  | 1 | 46 | 0.017759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1051-3_1_5_line_2 |  | 2 | 3 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1051-3_1_5_line_3 |  | 2 | 4 | 0.017179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1051-3_1_5_line_4 |  | 3 | 5 | 0.0022395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1051-3_1_5_line_5 |  | 4 | 6 | 0.0035599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1051-3_1_5_line_6 |  | 5 | 7 | 0.016489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1051-3_1_5_line_7 |  | 5 | 8 | 0.017135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1051-3_1_5_line_8 |  | 6 | 12 | 0.011701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1051-3_1_5_line_9 |  | 7 | 13 | 0.013329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1051-3_1_5_line_10 |  | 8 | 14 | 0.0098847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1051-3_1_5_line_11 |  | 9 | 10 | 0.001326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1051-3_1_5_line_12 |  | 9 | 11 | 0.0093141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1051-3_1_5_line_13 |  | 10 | 15 | 0.0090002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1051-3_1_5_line_14 |  | 11 | 16 | 0.012586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1051-3_1_5_line_15 |  | 13 | 17 | 0.022385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_1051-3_1_5_line_16 |  | 14 | 18 | 0.022435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_1051-3_1_5_line_17 |  | 14 | 19 | 0.000565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1051-3_1_5_line_18 |  | 15 | 20 | 0.012754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1051-3_1_5_line_19 |  | 16 | 19 | 0.0095278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1051-3_1_5_line_20 |  | 17 | 58 | 0.018954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1051-3_1_5_line_21 |  | 18 | 43 | 0.014066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_1051-3_1_5_line_22 |  | 21 | 22 | 0.041258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1051-3_1_5_line_23 |  | 22 | 23 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1051-3_1_5_line_24 |  | 23 | 27 | 0.09822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1051-3_1_5_line_25 |  | 24 | 25 | 0.10112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1051-3_1_5_line_26 |  | 24 | 26 | 0.12041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_1051-3_1_5_line_27 |  | 25 | 28 | 0.039605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1051-3_1_5_line_28 |  | 26 | 29 | 0.17757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1051-3_1_5_line_29 |  | 27 | 30 | 0.11687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1051-3_1_5_line_30 |  | 27 | 31 | 0.09961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1051-3_1_5_line_31 |  | 28 | 33 | 0.034511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1051-3_1_5_line_32 |  | 29 | 87 | 0.0013139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_1051-3_1_5_line_33 |  | 30 | 32 | 0.017555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1051-3_1_5_line_34 |  | 31 | 34 | 0.024658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1051-3_1_5_line_35 |  | 32 | 41 | 0.021873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1051-3_1_5_line_36 |  | 33 | 42 | 0.065307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1051-3_1_5_line_37 |  | 33 | 34 | 0.020309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1051-3_1_5_line_38 |  | 35 | 36 | 0.028579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1051-3_1_5_line_39 |  | 35 | 37 | 0.0036685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1051-3_1_5_line_40 |  | 35 | 38 | 0.003757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1051-3_1_5_line_41 |  | 36 | 39 | 0.014964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1051-3_1_5_line_42 |  | 36 | 40 | 0.0050464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1051-3_1_5_line_43 |  | 38 | 72 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1051-3_1_5_line_44 |  | 38 | 41 | 0.017595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1051-3_1_5_line_45 |  | 39 | 78 | 0.002696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1051-3_1_5_line_46 |  | 39 | 79 | 0.0073983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1051-3_1_5_line_47 |  | 42 | 70 | 0.030019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1051-3_1_5_line_48 |  | 43 | 44 | 0.005774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1051-3_1_5_line_49 |  | 43 | 45 | 0.011812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_1051-3_1_5_line_50 |  | 45 | 55 | 0.01504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1051-3_1_5_line_51 |  | 45 | 46 | 0.031852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1051-3_1_5_line_52 |  | 45 | 54 | 0.0383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_1051-3_1_5_line_53 |  | 47 | 48 | 0.021602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_1051-3_1_5_line_54 |  | 47 | 49 | 0.0038771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_1051-3_1_5_line_55 |  | 48 | 53 | 0.0062576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1051-3_1_5_line_56 |  | 49 | 50 | 0.012376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1051-3_1_5_line_57 |  | 50 | 51 | 0.020683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_1051-3_1_5_line_58 |  | 51 | 52 | 0.0037478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_1051-3_1_5_line_59 |  | 52 | 54 | 0.012333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_1051-3_1_5_line_60 |  | 53 | 66 | 0.011452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1051-3_1_5_line_61 |  | 56 | 57 | 0.07847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1051-3_1_5_line_62 |  | 56 | 58 | 0.004122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1051-3_1_5_line_63 |  | 58 | 59 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1051-3_1_5_line_64 |  | 59 | 60 | 0.023127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1051-3_1_5_line_65 |  | 60 | 69 | 0.013433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_1051-3_1_5_line_66 |  | 60 | 61 | 0.005151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1051-3_1_5_line_67 |  | 61 | 62 | 0.025293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1051-3_1_5_line_68 |  | 61 | 63 | 0.023484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1051-3_1_5_line_69 |  | 63 | 133 | 0.0053057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1051-3_1_5_line_70 |  | 64 | 65 | 0.039023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_1051-3_1_5_line_71 |  | 64 | 66 | 0.0041191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_1051-3_1_5_line_72 |  | 65 | 113 | 0.025172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1051-3_1_5_line_73 |  | 67 | 68 | 0.0053963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1051-3_1_5_line_74 |  | 68 | 115 | 0.015471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1051-3_1_5_line_75 |  | 69 | 130 | 0.0012203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_1051-3_1_5_line_76 |  | 70 | 71 | 0.028027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1051-3_1_5_line_77 |  | 72 | 73 | 0.0040062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1051-3_1_5_line_78 |  | 73 | 81 | 0.0087365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1051-3_1_5_line_79 |  | 74 | 75 | 0.008227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1051-3_1_5_line_80 |  | 75 | 138 | 0.0060449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1051-3_1_5_line_81 |  | 75 | 139 | 0.0095831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1051-3_1_5_line_82 |  | 76 | 77 | 0.0054368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1051-3_1_5_line_83 |  | 77 | 122 | 0.0054373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1051-3_1_5_line_84 |  | 78 | 142 | 0.00685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1051-3_1_5_line_85 |  | 79 | 80 | 0.00369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1051-3_1_5_line_86 |  | 81 | 135 | 0.018283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1051-3_1_5_line_87 |  | 82 | 83 | 8.2319e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_1051-3_1_5_line_88 |  | 82 | 84 | 0.0014631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_1051-3_1_5_line_89 |  | 83 | 85 | 0.0097002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_1051-3_1_5_line_90 |  | 84 | 86 | 0.0034074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_1051-3_1_5_line_91 |  | 85 | 87 | 0.046033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_1051-3_1_5_line_92 |  | 86 | 88 | 0.015142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_1051-3_1_5_line_93 |  | 88 | 89 | 0.011521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_1051-3_1_5_line_94 |  | 89 | 90 | 0.0013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_1051-3_1_5_line_95 |  | 90 | 132 | 5.6602e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_1051-3_1_5_line_96 |  | 91 | 92 | 0.0054243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1051-3_1_5_line_97 |  | 91 | 93 | 0.005426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1051-3_1_5_line_98 |  | 92 | 94 | 0.0046422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1051-3_1_5_line_99 |  | 93 | 95 | 0.027072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1051-3_1_5_line_100 |  | 94 | 96 | 0.021155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1051-3_1_5_line_101 |  | 95 | 97 | 6.1272e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1051-3_1_5_line_102 |  | 96 | 98 | 0.009209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1051-3_1_5_line_103 |  | 96 | 99 | 0.012922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1051-3_1_5_line_104 |  | 97 | 100 | 0.00021155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1051-3_1_5_line_105 |  | 99 | 101 | 0.004538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1051-3_1_5_line_106 |  | 99 | 102 | 0.012981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1051-3_1_5_line_107 |  | 100 | 103 | 0.0013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1051-3_1_5_line_108 |  | 102 | 111 | 0.028767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1051-3_1_5_line_109 |  | 102 | 112 | 0.092345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1051-3_1_5_line_110 |  | 103 | 114 | 0.0013855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1051-3_1_5_line_111 |  | 104 | 105 | 0.0054406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1051-3_1_5_line_112 |  | 104 | 106 | 0.0054388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1051-3_1_5_line_113 |  | 105 | 107 | 0.0054388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1051-3_1_5_line_114 |  | 106 | 108 | 0.0054406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1051-3_1_5_line_115 |  | 108 | 109 | 0.0054389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1051-3_1_5_line_116 |  | 109 | 110 | 0.011841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1051-3_1_5_line_117 |  | 110 | 119 | 0.005136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1051-3_1_5_line_118 |  | 110 | 118 | 0.0034012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1051-3_1_5_line_119 |  | 112 | 116 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1051-3_1_5_line_120 |  | 112 | 117 | 0.012928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1051-3_1_5_line_121 |  | 113 | 114 | 0.017545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1051-3_1_5_line_122 |  | 113 | 115 | 0.004147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1051-3_1_5_line_123 |  | 115 | 118 | 0.010924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1051-3_1_5_line_124 |  | 116 | 120 | 0.01257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1051-3_1_5_line_125 |  | 117 | 121 | 0.002339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1051-3_1_5_line_126 |  | 119 | 127 | 0.012018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1051-3_1_5_line_127 |  | 121 | 128 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1051-3_1_5_line_128 |  | 122 | 123 | 0.0054382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1051-3_1_5_line_129 |  | 123 | 124 | 0.0052477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1051-3_1_5_line_130 |  | 124 | 125 | 0.0054411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1051-3_1_5_line_131 |  | 125 | 126 | 0.0054375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1051-3_1_5_line_132 |  | 126 | 127 | 0.0026385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1051-3_1_5_line_133 |  | 127 | 129 | 0.002692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1051-3_1_5_line_134 |  | 130 | 131 | 0.01235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_1051-3_1_5_line_135 |  | 131 | 132 | 0.018523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_1051-3_1_5_line_136 |  | 133 | 134 | 0.0016949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1051-3_1_5_line_137 |  | 135 | 136 | 0.0058468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1051-3_1_5_line_138 |  | 136 | 137 | 0.0072262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1051-3_1_5_line_139 |  | 137 | 138 | 0.008441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1051-3_1_5_line_140 |  | 139 | 140 | 0.0006127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1051-3_1_5_line_141 |  | 140 | 141 | 0.0058634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1051-3_1_5_trafo_130 | 0.63 MVA 20/0.4 kV | 143 | 57 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32
0 | 2671169.796 | 1214023.2467 | 2671099.7193 | 1213950.0661 | 2671097.256 | 1213940.7087 | 2671103.9908 | 1213927.1748
1 | 2671111.9026 | 1213911.2758 | 2671103.9908 | 1213927.1748
2 | 2671116.9569 | 1213873.013 | 2671105.7453 | 1213867.5629
3 | 2671090.2954 | 1213860.0526 | 2671105.7453 | 1213867.5629
4 | 2671118.9711 | 1213873.9921 | 2671116.9569 | 1213873.013
5 | 2671090.2954 | 1213860.0526 | 2671087.0934 | 1213858.4967
6 | 2671118.9711 | 1213873.9921 | 2671133.8014 | 1213881.1997
7 | 2671118.9711 | 1213873.9921 | 2671111.5946 | 1213889.4581
8 | 2671076.569 | 1213853.3827 | 2671087.0934 | 1213858.4967
9 | 2671133.8014 | 1213881.1997 | 2671145.7893 | 1213887.026
10 | 2671107.3393 | 1213898.3799 | 2671111.5946 | 1213889.4581
11 | 2671077.1932 | 1213884.1783 | 2671078.3942 | 1213884.7485
12 | 2671078.3942 | 1213884.7485 | 2671086.8203 | 1213888.7174
13 | 2671077.1932 | 1213884.1783 | 2671069.0512 | 1213880.3427
14 | 2671098.2062 | 1213894.0804 | 2671086.8203 | 1213888.7174
15 | 2671165.9229 | 1213896.811 | 2671145.7893 | 1213887.026
16 | 2671107.3393 | 1213898.3799 | 2671125.6791 | 1213907.0263 | 2671127.6771 | 1213907.8459
17 | 2671106.8257 | 1213898.1403 | 2671107.3393 | 1213898.3799
18 | 2671057.5133 | 1213874.9074 | 2671069.0512 | 1213880.3427
19 | 2671106.8257 | 1213898.1403 | 2671098.2062 | 1213894.0804
20 | 2671165.9229 | 1213896.811 | 2671172.9376 | 1213881.8741 | 2671173.9896 | 1213879.6519
21 | 2671139.8682 | 1213914.6781 | 2671133.7748 | 1213910.3471 | 2671127.6771 | 1213907.8459
22 | 2671301.2913 | 1213731.623 | 2671281.6646 | 1213723.8506 | 2671262.5664 | 1213717.4312
23 | 2671315.7982 | 1213737.4894 | 2671314.8697 | 1213737.0002 | 2671301.2913 | 1213731.623
24 | 2671379.141 | 1213726.8404 | 2671380.7382 | 1213744.4372 | 2671379.9575 | 1213748.0969 | 2671374.0503 | 1213749.1491 | 2671372.311 | 1213752.308 | 2671370.3473 | 1213755.1641 | 2671367.3324 | 1213757.6407 | 2671364.0255 | 1213757.8568 | 2671360.9636 | 1213757.2754 | 2671318.5344 | 1213733.553 | 2671315.7982 | 1213737.4894
25 | 2671091.2747 | 1213657.5587 | 2671094.4917 | 1213651.5044 | 2671100.2369 | 1213645.5691 | 2671108.2178 | 1213646.4426 | 2671118.1072 | 1213652.8868 | 2671131.8915 | 1213662.6795 | 2671177.627 | 1213680.9888
26 | 2671091.2747 | 1213657.5587 | 2670972.2593 | 1213675.8307
27 | 2671214.3954 | 1213695.7083 | 2671177.627 | 1213680.9888
28 | 2670972.2593 | 1213675.8307 | 2670976.0797 | 1213714.7897 | 2670979.2856 | 1213737.0863 | 2670987.7556 | 1213745.359 | 2671035.4334 | 1213745.6268 | 2671044.7144 | 1213745.7485 | 2671060.5052 | 1213754.1641 | 2671079.3926 | 1213767.8978 | 2671077.054 | 1213773.2587
29 | 2671323.1083 | 1213803.9299 | 2671325.5041 | 1213803.0468 | 2671326.1374 | 1213802.8098 | 2671330.4664 | 1213801.6053 | 2671333.4949 | 1213799.896 | 2671334.2783 | 1213797.9041 | 2671336.5588 | 1213792.0499 | 2671337.8257 | 1213791.5536 | 2671340.4512 | 1213790.5177 | 2671341.5955 | 1213789.4752 | 2671342.7067 | 1213786.7534 | 2671344.4206 | 1213782.549 | 2671343.7392 | 1213779.8169 | 2671342.9705 | 1213776.7725 | 2671343.1822 | 1213775.5854 | 2671344.7511 | 1213772.7023 | 2671345.388 | 1213771.5314 | 2671352.2303 | 1213775.4935 | 2671353.3534 | 1213776.2185 | 2671353.7859 | 1213775.6233 | 2671356.4576 | 1213771.9975 | 2671357.8088 | 1213770.168 | 2671358.9672 | 1213768.5809 | 2671360.442 | 1213766.5862 | 2671363.5307 | 1213762.3871 | 2671364.2025 | 1213761.4724 | 2671367.3434 | 1213761.799 | 2671372.2991 | 1213760.2796 | 2671377.0333 | 1213756.3226 | 2671379.1771 | 1213751.7343 | 2671379.9575 | 1213748.0969 | 2671380.7382 | 1213744.4372 | 2671379.141 | 1213726.8404
30 | 2671379.141 | 1213726.8404 | 2671359.8571 | 1213728.5107 | 2671347.1152 | 1213726.2346 | 2671337.0303 | 1213721.5555 | 2671330.197 | 1213716.2037 | 2671321.4842 | 1213702.2351 | 2671314.1866 | 1213698.2231 | 2671307.036 | 1213698.4378 | 2671291.5996 | 1213700.4602
31 | 2671247.7813 | 1213694.3493 | 2671231.5181 | 1213698.769 | 2671226.8068 | 1213698.9128 | 2671220.9192 | 1213698.3199 | 2671214.3954 | 1213695.7083
32 | 2671076.5286 | 1213774.463 | 2671077.054 | 1213773.2587
33 | 2671323.1083 | 1213803.9299 | 2671317.274 | 1213794.4541 | 2671312.2875 | 1213790.3998
34 | 2671291.5996 | 1213700.4602 | 2671288.3733 | 1213700.8829 | 2671280.421 | 1213700.1652 | 2671267.7974 | 1213695.6115 | 2671267.7974 | 1213695.6115
35 | 2671292.5412 | 1213781.7763 | 2671295.9452 | 1213782.3026 | 2671308.0584 | 1213786.9614 | 2671312.2875 | 1213790.3998
36 | 2671247.7813 | 1213694.3493 | 2671250.7133 | 1213680.3755 | 2671246.739 | 1213671.6003 | 2671234.9914 | 1213665.5673 | 2671209.2665 | 1213654.041
37 | 2671247.7813 | 1213694.3493 | 2671257.0228 | 1213693.3369 | 2671267.7974 | 1213695.6115
38 | 2671273.446 | 1213787.9817 | 2671278.2851 | 1213789.8518 | 2671277.7829 | 1213791.1911 | 2671277.7946 | 1213793.3926 | 2671281.092 | 1213792.0645 | 2671282.7818 | 1213796.8544 | 2671283.0742 | 1213807.976
39 | 2671273.446 | 1213787.9817 | 2671274.4336 | 1213791.5147
40 | 2671275.6247 | 1213784.9169 | 2671273.446 | 1213787.9817
41 | 2671283.0742 | 1213807.976 | 2671283.4073 | 1213820.777 | 2671284.4762 | 1213820.9566 | 2671285.3962 | 1213821.5123
42 | 2671283.0742 | 1213807.976 | 2671287.8928 | 1213806.4771
43 | 2671275.6247 | 1213784.9169 | 2671269.0113 | 1213779.6012 | 2671266.6181 | 1213777.6438
44 | 2671275.6247 | 1213784.9169 | 2671287.6049 | 1213781.0132 | 2671292.5412 | 1213781.7763
45 | 2671286.2937 | 1213823.9579 | 2671286.2665 | 1213823.0571 | 2671285.9575 | 1213822.2195 | 2671285.3962 | 1213821.5123
46 | 2671280.8553 | 1213824.56 | 2671280.7849 | 1213822.8247 | 2671281.7594 | 1213821.3688 | 2671283.4073 | 1213820.777 | 2671284.4762 | 1213820.9566 | 2671285.3962 | 1213821.5123
47 | 2671209.2665 | 1213654.041 | 2671181.872 | 1213641.7665
48 | 2671139.8682 | 1213914.6781 | 2671142.0588 | 1213909.3342
49 | 2671135.3928 | 1213925.6094 | 2671137.1688 | 1213921.2834 | 2671138.4364 | 1213918.1743 | 2671139.8682 | 1213914.6781
50 | 2671135.3928 | 1213925.6094 | 2671129.6958 | 1213939.5288
51 | 2671111.9026 | 1213911.2758 | 2671119.8937 | 1213914.4397 | 2671137.1688 | 1213921.2834 | 2671135.3928 | 1213925.6094
52 | 2671135.3928 | 1213925.6094 | 2671137.1688 | 1213921.2834 | 2671148.5544 | 1213925.7887 | 2671158.6775 | 1213929.8009 | 2671165.3634 | 1213931.5818 | 2671164.5698 | 1213935.0634
53 | 2671206.6254 | 1213933.4087 | 2671225.4841 | 1213931.0213 | 2671225.2491 | 1213928.4391
54 | 2671206.6254 | 1213933.4087 | 2671206.9666 | 1213937.2708
55 | 2671225.8051 | 1213934.6719 | 2671225.4841 | 1213931.0213 | 2671225.2491 | 1213928.4391
56 | 2671194.596 | 1213937.6456 | 2671206.9666 | 1213937.2708
57 | 2671176.9883 | 1213933.8664 | 2671179.1409 | 1213934.2479 | 2671188.1354 | 1213934.8111 | 2671194.534 | 1213934.5651 | 2671194.596 | 1213937.6456
58 | 2671176.9883 | 1213933.8664 | 2671176.6399 | 1213937.5979
59 | 2671164.5698 | 1213935.0634 | 2671176.6399 | 1213937.5979
60 | 2671225.8051 | 1213934.6719 | 2671237.2045 | 1213933.574
61 | 2671177.8222 | 1213881.1987 | 2671180.2111 | 1213882.1611 | 2671184.0017 | 1213883.4183 | 2671197.6657 | 1213888.5957 | 2671199.742 | 1213889.0208 | 2671201.4292 | 1213888.9409 | 2671205.2187 | 1213887.1072 | 2671209.763 | 1213883.1367 | 2671213.2193 | 1213881.8549 | 2671226.0146 | 1213882.1746 | 2671233.1779 | 1213880.8815 | 2671251.803 | 1213874.5444
62 | 2671177.8222 | 1213881.1987 | 2671174.8438 | 1213879.9957 | 2671173.9896 | 1213879.6519
63 | 2671173.9896 | 1213879.6519 | 2671182.3044 | 1213862.0684
64 | 2671192.1557 | 1213841.1444 | 2671186.4112 | 1213853.3836 | 2671182.3044 | 1213862.0684
65 | 2671192.1557 | 1213841.1444 | 2671180.0316 | 1213835.3602
66 | 2671192.1557 | 1213841.1444 | 2671196.8159 | 1213843.3681
67 | 2671207.8212 | 1213820.5851 | 2671196.8159 | 1213843.3681
68 | 2671196.8159 | 1213843.3681 | 2671211.5182 | 1213850.0256 | 2671214.4811 | 1213849.3495 | 2671215.4134 | 1213848.2488 | 2671216.6545 | 1213845.6693
69 | 2671218.955 | 1213840.8882 | 2671216.6545 | 1213845.6693
70 | 2671238.3653 | 1213929.8744 | 2671250.308 | 1213929.0832 | 2671270.5795 | 1213930.5152 | 2671276.1469 | 1213931.827 | 2671277.1114 | 1213932.1327
71 | 2671238.3653 | 1213929.8744 | 2671238.3502 | 1213931.7754 | 2671238.0414 | 1213932.828 | 2671237.2045 | 1213933.574
72 | 2671301.0404 | 1213939.9408 | 2671289.2003 | 1213935.9634 | 2671277.1114 | 1213932.1327
73 | 2671282.5397 | 1213929.9437 | 2671287.6994 | 1213931.5242
74 | 2671302.4921 | 1213936.0557 | 2671287.6994 | 1213931.5242
75 | 2671178.9302 | 1213834.8347 | 2671180.0316 | 1213835.3602
76 | 2671181.872 | 1213641.7665 | 2671156.2954 | 1213630.3066
77 | 2671263.3827 | 1213775.3237 | 2671264.2796 | 1213775.7311 | 2671266.6181 | 1213777.6438
78 | 2671263.3827 | 1213775.3237 | 2671255.4284 | 1213771.7103
79 | 2671211.9579 | 1213762.9871 | 2671209.2211 | 1213755.2286
80 | 2671211.9579 | 1213762.9871 | 2671217.9314 | 1213762.0609
81 | 2671211.9579 | 1213762.9871 | 2671203.067 | 1213766.5631
82 | 2671342.9553 | 1213920.2914 | 2671348.0554 | 1213922.175
83 | 2671342.9553 | 1213920.2914 | 2671337.8547 | 1213918.4076
84 | 2671286.2937 | 1213823.9579 | 2671293.1621 | 1213823.8288
85 | 2671280.8553 | 1213824.56 | 2671277.3765 | 1213825.8192
86 | 2671255.4284 | 1213771.7103 | 2671248.1419 | 1213768.4004 | 2671238.7597 | 1213764.1989
87 | 2671121.1583 | 1213807.441 | 2671121.233 | 1213807.4755
88 | 2671121.233 | 1213807.4755 | 2671122.5609 | 1213808.0898
89 | 2671112.3543 | 1213803.3687 | 2671121.1583 | 1213807.441
90 | 2671125.6536 | 1213809.5203 | 2671122.5609 | 1213808.0898
91 | 2671112.3543 | 1213803.3687 | 2671076.5286 | 1213774.463
92 | 2671139.3598 | 1213815.9561 | 2671132.7587 | 1213812.8068 | 2671125.6536 | 1213809.5203
93 | 2671139.3598 | 1213815.9561 | 2671149.758 | 1213820.917
94 | 2671151.0146 | 1213821.5165 | 2671149.758 | 1213820.917
95 | 2671151.0146 | 1213821.5165 | 2671151.0657 | 1213821.5409
96 | 2671310.5371 | 1213977.0653 | 2671315.6788 | 1213978.793
97 | 2671310.5371 | 1213977.0653 | 2671305.3937 | 1213975.3371
98 | 2671315.6788 | 1213978.793 | 2671320.0793 | 1213980.2717
99 | 2671294.4296 | 1213959.4351 | 2671290.7102 | 1213970.4032 | 2671305.3937 | 1213975.3371
100 | 2671336.5679 | 1213982.3368 | 2671335.028 | 1213986.61 | 2671322.3286 | 1213982.7334 | 2671320.0793 | 1213980.2717
101 | 2671294.4296 | 1213959.4351 | 2671294.4493 | 1213959.3771
102 | 2671336.5679 | 1213982.3368 | 2671335.751 | 1213982.0491 | 2671338.3526 | 1213974.1196
103 | 2671336.5679 | 1213982.3368 | 2671348.8229 | 1213986.5416
104 | 2671294.4493 | 1213959.3771 | 2671294.5172 | 1213959.1767
105 | 2671352.6129 | 1213984.0298 | 2671348.8229 | 1213986.5416
106 | 2671345.4099 | 1213995.6287 | 2671345.2078 | 1213992.8468 | 2671349.4743 | 1213992.4087 | 2671349.2757 | 1213990.594 | 2671349.0081 | 1213988.2004 | 2671348.8229 | 1213986.5416
107 | 2671294.9608 | 1213957.8688 | 2671294.5172 | 1213959.1767
108 | 2671316.7458 | 1213992.8731 | 2671335.4456 | 1213995.5095 | 2671345.4099 | 1213995.6287
109 | 2671345.4099 | 1213995.6287 | 2671353.6901 | 1213994.9385 | 2671361.9065 | 1213993.2246 | 2671365.8825 | 1213998.0196 | 2671385.1556 | 1214021.2761 | 2671387.9094 | 1214030.4482 | 2671385.5118 | 1214039.7364 | 2671372.7708 | 1214055.2048
110 | 2671294.9608 | 1213957.8688 | 2671295.4057 | 1213956.5567
111 | 2671332.7875 | 1213937.3674 | 2671337.9332 | 1213939.1343
112 | 2671332.7875 | 1213937.3674 | 2671327.6435 | 1213935.601
113 | 2671337.9332 | 1213939.1343 | 2671343.0772 | 1213940.9007
114 | 2671322.4978 | 1213933.8341 | 2671327.6435 | 1213935.601
115 | 2671317.3538 | 1213932.0677 | 2671322.4978 | 1213933.8341
116 | 2671309.1682 | 1213926.5851 | 2671308.5539 | 1213929.0459 | 2671317.3538 | 1213932.0677
117 | 2671309.1682 | 1213926.5851 | 2671309.7555 | 1213924.4796 | 2671311.108 | 1213921.8577
118 | 2671309.1682 | 1213926.5851 | 2671308.3733 | 1213926.3643 | 2671306.4427 | 1213925.8298 | 2671305.8901 | 1213925.6786
119 | 2671372.7708 | 1214055.2048 | 2671383.6329 | 1214064.2434
120 | 2671372.7708 | 1214055.2048 | 2671362.507 | 1214047.344
121 | 2671301.0404 | 1213939.9408 | 2671295.4057 | 1213956.5567
122 | 2671301.0404 | 1213939.9408 | 2671301.417 | 1213938.9335 | 2671302.4921 | 1213936.0557
123 | 2671302.4921 | 1213936.0557 | 2671303.6768 | 1213932.9012 | 2671304.9573 | 1213928.725 | 2671305.8901 | 1213925.6786
124 | 2671393.295 | 1214072.2835 | 2671383.6329 | 1214064.2434
125 | 2671360.65 | 1214045.9217 | 2671362.507 | 1214047.344
126 | 2671314.9817 | 1213910.5 | 2671314.7766 | 1213911.1313 | 2671313.6885 | 1213914.4648 | 2671313.1525 | 1213916.0927 | 2671311.7618 | 1213920.5901 | 2671311.108 | 1213921.8577
127 | 2671347.7594 | 1214036.049 | 2671360.65 | 1214045.9217
128 | 2671337.8547 | 1213918.4076 | 2671332.7534 | 1213916.5235
129 | 2671327.7844 | 1213914.8361 | 2671332.6088 | 1213916.4701 | 2671332.7534 | 1213916.5235
130 | 2671322.6308 | 1213913.0907 | 2671327.7844 | 1213914.8361
131 | 2671317.4807 | 1213911.3464 | 2671322.6308 | 1213913.0907
132 | 2671314.9817 | 1213910.5 | 2671317.4807 | 1213911.3464
133 | 2671312.4246 | 1213909.6355 | 2671314.9817 | 1213910.5
134 | 2671178.9302 | 1213834.8347 | 2671167.7834 | 1213829.5167
135 | 2671167.7834 | 1213829.5167 | 2671151.0657 | 1213821.5409
136 | 2671219.6898 | 1213839.3609 | 2671218.955 | 1213840.8882
137 | 2671238.7597 | 1213764.1989 | 2671233.4235 | 1213761.8093 | 2671233.4235 | 1213761.8093
138 | 2671226.2728 | 1213760.7677 | 2671233.4235 | 1213761.8093
139 | 2671226.2728 | 1213760.7677 | 2671217.9314 | 1213762.0609
140 | 2671202.4986 | 1213766.7917 | 2671203.067 | 1213766.5631
141 | 2671197.0587 | 1213768.9797 | 2671202.4986 | 1213766.7917

## bus_geodata
| x | y | coords
0 | 2671169.796 | 1214023.2467
1 | 2671103.9908 | 1213927.1748
2 | 2671105.7453 | 1213867.5629
3 | 2671116.9569 | 1213873.013
4 | 2671090.2954 | 1213860.0526
5 | 2671118.9711 | 1213873.9921
6 | 2671087.0934 | 1213858.4967
7 | 2671133.8014 | 1213881.1997
8 | 2671111.5946 | 1213889.4581
9 | 2671078.3942 | 1213884.7485
10 | 2671077.1932 | 1213884.1783
11 | 2671086.8203 | 1213888.7174
12 | 2671076.569 | 1213853.3827
13 | 2671145.7893 | 1213887.026
14 | 2671107.3393 | 1213898.3799
15 | 2671069.0512 | 1213880.3427
16 | 2671098.2062 | 1213894.0804
17 | 2671165.9229 | 1213896.811
18 | 2671127.6771 | 1213907.8459
19 | 2671106.8257 | 1213898.1403
20 | 2671057.5133 | 1213874.9074
21 | 2671262.5664 | 1213717.4312
22 | 2671301.2913 | 1213731.623
23 | 2671315.7982 | 1213737.4894
24 | 2671091.2747 | 1213657.5587
25 | 2671177.627 | 1213680.9888
26 | 2670972.2593 | 1213675.8307
27 | 2671379.141 | 1213726.8404
28 | 2671214.3954 | 1213695.7083
29 | 2671077.054 | 1213773.2587
30 | 2671323.1083 | 1213803.9299
31 | 2671291.5996 | 1213700.4602
32 | 2671312.2875 | 1213790.3998
33 | 2671247.7813 | 1213694.3493
34 | 2671267.7974 | 1213695.6115
35 | 2671273.446 | 1213787.9817
36 | 2671283.0742 | 1213807.9761
37 | 2671274.4336 | 1213791.5147
38 | 2671275.6247 | 1213784.9169
39 | 2671285.3962 | 1213821.5123
40 | 2671287.8928 | 1213806.4771
41 | 2671292.5412 | 1213781.7763
42 | 2671209.2665 | 1213654.041
43 | 2671139.8682 | 1213914.6781
44 | 2671142.0588 | 1213909.3342
45 | 2671135.3929 | 1213925.6094
46 | 2671111.9026 | 1213911.2758
47 | 2671206.6254 | 1213933.4087
48 | 2671225.2491 | 1213928.4391
49 | 2671206.9666 | 1213937.2708
50 | 2671194.596 | 1213937.6456
51 | 2671176.9883 | 1213933.8664
52 | 2671176.6399 | 1213937.5979
53 | 2671225.8051 | 1213934.6719
54 | 2671164.5698 | 1213935.0634
55 | 2671129.6958 | 1213939.5288
56 | 2671177.8222 | 1213881.1987
57 | 2671251.803 | 1213874.5444
58 | 2671173.9896 | 1213879.6519
59 | 2671182.3044 | 1213862.0684
60 | 2671192.1557 | 1213841.1444
61 | 2671196.8159 | 1213843.3681
62 | 2671207.8212 | 1213820.5851
63 | 2671216.6545 | 1213845.6693
64 | 2671238.3653 | 1213929.8744
65 | 2671277.1114 | 1213932.1327
66 | 2671237.2045 | 1213933.574
67 | 2671282.5397 | 1213929.9437
68 | 2671287.6994 | 1213931.5242
69 | 2671180.0316 | 1213835.3602
70 | 2671181.872 | 1213641.7665
71 | 2671156.2954 | 1213630.3066
72 | 2671266.6181 | 1213777.6438
73 | 2671263.3827 | 1213775.3237
74 | 2671209.2211 | 1213755.2286
75 | 2671211.9579 | 1213762.9871
76 | 2671348.0554 | 1213922.175
77 | 2671342.9553 | 1213920.2914
78 | 2671286.2937 | 1213823.9579
79 | 2671280.8553 | 1213824.56
80 | 2671277.3765 | 1213825.8192
81 | 2671255.4284 | 1213771.7103
82 | 2671121.233 | 1213807.4755
83 | 2671121.1583 | 1213807.441
84 | 2671122.5609 | 1213808.0898
85 | 2671112.3543 | 1213803.3687
86 | 2671125.6536 | 1213809.5203
87 | 2671076.5286 | 1213774.463
88 | 2671139.3598 | 1213815.9561
89 | 2671149.758 | 1213820.917
90 | 2671151.0146 | 1213821.5165
91 | 2671310.5371 | 1213977.0653
92 | 2671315.6788 | 1213978.793
93 | 2671305.3937 | 1213975.3371
94 | 2671320.0793 | 1213980.2717
95 | 2671294.4296 | 1213959.4351
96 | 2671336.5679 | 1213982.3368
97 | 2671294.4493 | 1213959.3771
98 | 2671338.3526 | 1213974.1196
99 | 2671348.8229 | 1213986.5416
100 | 2671294.5172 | 1213959.1767
101 | 2671352.6129 | 1213984.0298
102 | 2671345.4099 | 1213995.6287
103 | 2671294.9608 | 1213957.8688
104 | 2671332.7875 | 1213937.3674
105 | 2671337.9332 | 1213939.1343
106 | 2671327.6435 | 1213935.601
107 | 2671343.0772 | 1213940.9007
108 | 2671322.4978 | 1213933.8341
109 | 2671317.3538 | 1213932.0677
110 | 2671309.1682 | 1213926.5851
111 | 2671316.7458 | 1213992.8731
112 | 2671372.7708 | 1214055.2048
113 | 2671301.0404 | 1213939.9408
114 | 2671295.4057 | 1213956.5567
115 | 2671302.4921 | 1213936.0557
116 | 2671383.6329 | 1214064.2434
117 | 2671362.507 | 1214047.344
118 | 2671305.8901 | 1213925.6786
119 | 2671311.108 | 1213921.8577
120 | 2671393.295 | 1214072.2835
121 | 2671360.65 | 1214045.9217
122 | 2671337.8547 | 1213918.4076
123 | 2671332.7534 | 1213916.5235
124 | 2671327.7844 | 1213914.8361
125 | 2671322.6308 | 1213913.0907
126 | 2671317.4807 | 1213911.3464
127 | 2671314.9817 | 1213910.5
128 | 2671347.7594 | 1214036.049
129 | 2671312.4246 | 1213909.6355
130 | 2671178.9302 | 1213834.8347
131 | 2671167.7834 | 1213829.5167
132 | 2671151.0657 | 1213821.5409
133 | 2671218.955 | 1213840.8882
134 | 2671219.6898 | 1213839.3609
135 | 2671238.7597 | 1213764.1989
136 | 2671233.4235 | 1213761.8093
137 | 2671226.2728 | 1213760.7677
138 | 2671217.9314 | 1213762.0609
139 | 2671203.067 | 1213766.5631
140 | 2671202.4986 | 1213766.7917
141 | 2671197.0587 | 1213768.9797
142 | 2671293.1621 | 1213823.8288
143 | 2671177.8222 | 1213881.1987

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98822 | -0.22519 | 0.002218 | 0.00055587
1 | 0.98847 | -0.22019 | 0.011115 | 0.0027856
2 | 0.99151 | -0.1617 | 0.0027413 | 0.00068703
3 | 0.99159 | -0.16015 | 0.002703 | 0.00067744
4 | 0.99144 | -0.16299 | 0 | 0
5 | 0.99161 | -0.15977 | 0 | 0
6 | 0.99143 | -0.16326 | 0.0023872 | 0.00059828
7 | 0.99222 | -0.14803 | 0.0022288 | 0.00055859
8 | 0.991 | -0.17139 | 0.0024934 | 0.00062491
9 | 0.99045 | -0.1821 | 0 | 0
10 | 0.99044 | -0.18221 | 0 | 0
11 | 0.99049 | -0.18132 | 0.0023835 | 0.00059736
12 | 0.99141 | -0.16364 | 0.001858 | 0.00046567
13 | 0.99272 | -0.13845 | 0.0027247 | 0.00068288
14 | 0.99066 | -0.17801 | 0 | 0
15 | 0.9904 | -0.18296 | 0.0024477 | 0.00061345
16 | 0.99057 | -0.17974 | 0.0025319 | 0.00063455
17 | 0.99357 | -0.12216 | 0 | 0
18 | 0.98991 | -0.1923 | 0.002391 | 0.00059923
19 | 0.99065 | -0.17811 | 0 | 0
20 | 0.99038 | -0.18347 | 0.0022459 | 0.00056288
21 | 0.97703 | -0.44155 | 0.0051077 | 0.0012801
22 | 0.97723 | -0.43771 | 0.0014326 | 0.00035906
23 | 0.97732 | -0.43584 | 0 | 0
24 | 0.98379 | -0.3098 | 0 | 0
25 | 0.98176 | -0.34928 | 0.000689 | 0.00017268
26 | 0.98621 | -0.263 | 0 | 0
27 | 0.97792 | -0.42412 | 0 | 0
28 | 0.98096 | -0.36468 | 0.0098246 | 0.0024623
29 | 0.98979 | -0.19439 | 0.0026738 | 0.00067012
30 | 0.97614 | -0.45905 | 0 | 0
31 | 0.97956 | -0.39207 | 0.0034611 | 0.00086742
32 | 0.97587 | -0.4643 | 0.0017277 | 0.000433
33 | 0.98034 | -0.3769 | 0 | 0
34 | 0.97998 | -0.38384 | 0.0023385 | 0.00058609
35 | 0.97462 | -0.48885 | 0 | 0
36 | 0.97332 | -0.51449 | 0 | 0
37 | 0.97462 | -0.48896 | 0.0014998 | 0.00037589
38 | 0.97471 | -0.48712 | 0 | 0
39 | 0.97283 | -0.52411 | 0 | 0
40 | 0.97325 | -0.51578 | 0.013898 | 0.0034831
41 | 0.97532 | -0.475 | 0.0049643 | 0.0012442
42 | 0.98013 | -0.38093 | 0.0010907 | 0.00027337
43 | 0.98946 | -0.20114 | 0 | 0
44 | 0.98943 | -0.20158 | 0.0043058 | 0.0010791
45 | 0.98908 | -0.20839 | 0 | 0
46 | 0.98869 | -0.21597 | 0 | 0
47 | 0.98665 | -0.25525 | 0 | 0
48 | 0.98617 | -0.26461 | 0 | 0
49 | 0.98674 | -0.25357 | 0.018021 | 0.0045166
50 | 0.98706 | -0.24742 | 0 | 0
51 | 0.98759 | -0.23714 | 0 | 0
52 | 0.98769 | -0.23528 | 0.0098319 | 0.0024641
53 | 0.98603 | -0.26732 | 0 | 0
54 | 0.98803 | -0.22872 | 0 | 0
55 | 0.98894 | -0.21114 | 0.010246 | 0.0025678
56 | 0.99457 | -0.10296 | 0 | 0
57 | 1 | 0 | -0.38196 | -0.097632
58 | 0.99429 | -0.1084 | 0 | 0
59 | 0.99368 | -0.11996 | 0.0019963 | 0.00050031
60 | 0.99297 | -0.13356 | 0 | 0
61 | 0.99286 | -0.13569 | 0 | 0
62 | 0.99282 | -0.13637 | 0.0015141 | 0.00037947
63 | 0.99239 | -0.14478 | 0.0043751 | 0.0010965
64 | 0.98569 | -0.27382 | 0 | 0
65 | 0.98382 | -0.31002 | 0.0025954 | 0.00065048
66 | 0.98577 | -0.27229 | 0.017688 | 0.004433
67 | 0.98125 | -0.36025 | 0.0022991 | 0.0005762
68 | 0.98126 | -0.36003 | 0.0023008 | 0.00057664
69 | 0.99261 | -0.14036 | 0.0019972 | 0.00050054
70 | 0.98007 | -0.38219 | 0.0011263 | 0.00028228
71 | 0.98004 | -0.38279 | 0.001183 | 0.00029648
72 | 0.97444 | -0.49239 | 0.0015096 | 0.00037835
73 | 0.97435 | -0.49411 | 0.0015137 | 0.00037938
74 | 0.97339 | -0.51309 | 0.0014991 | 0.00037572
75 | 0.9734 | -0.51286 | 0 | 0
76 | 0.98034 | -0.37794 | 0.002076 | 0.00052029
77 | 0.98035 | -0.37774 | 0.002076 | 0.00052029
78 | 0.97281 | -0.52446 | 0 | 0
79 | 0.97264 | -0.5279 | 0 | 0
80 | 0.97254 | -0.5298 | 0.027856 | 0.0069813
81 | 0.97418 | -0.4976 | 0.0014345 | 0.00035952
82 | 0.991 | -0.17112 | 0.0026719 | 0.00066964
83 | 0.991 | -0.17115 | 0.0019962 | 0.00050029
84 | 0.99104 | -0.17047 | 0.0019952 | 0.00050005
85 | 0.99079 | -0.17528 | 0.006342 | 0.0015894
86 | 0.99112 | -0.16894 | 0.0019745 | 0.00049485
87 | 0.98981 | -0.19387 | 0.0026734 | 0.00067001
88 | 0.99148 | -0.16203 | 0.0021269 | 0.00053306
89 | 0.99176 | -0.1567 | 0.0019962 | 0.00050029
90 | 0.99179 | -0.15604 | 0.0021269 | 0.00053306
91 | 0.97888 | -0.40651 | 0.0021224 | 0.00053193
92 | 0.97865 | -0.41086 | 0.0021238 | 0.00053229
93 | 0.97911 | -0.40195 | 0.0021253 | 0.00053264
94 | 0.97847 | -0.41441 | 0.0021252 | 0.00053264
95 | 0.98033 | -0.37818 | 0.0021238 | 0.00053229
96 | 0.97769 | -0.42977 | 0 | 0
97 | 0.98033 | -0.37813 | 0.0025413 | 0.0006369
98 | 0.97767 | -0.43012 | 0.0020623 | 0.00051687
99 | 0.97723 | -0.43868 | 0 | 0
100 | 0.98034 | -0.37792 | 0.0025937 | 0.00065004
101 | 0.97722 | -0.43902 | 0.0041219 | 0.001033
102 | 0.97683 | -0.44666 | 0 | 0
103 | 0.98041 | -0.37653 | 0.0025954 | 0.00065048
104 | 0.98061 | -0.37271 | 0.0020586 | 0.00051593
105 | 0.98059 | -0.37311 | 0.0020586 | 0.00051593
106 | 0.98064 | -0.3721 | 0.0020586 | 0.00051593
107 | 0.98058 | -0.37332 | 0.0020586 | 0.00051593
108 | 0.98068 | -0.37129 | 0.0020586 | 0.00051593
109 | 0.98073 | -0.37027 | 0.0020586 | 0.00051593
110 | 0.98087 | -0.36762 | 0 | 0
111 | 0.97675 | -0.44816 | 0.0028495 | 0.00071415
112 | 0.97418 | -0.49877 | 0 | 0
113 | 0.98148 | -0.35575 | 0 | 0
114 | 0.98049 | -0.37507 | 0.0025954 | 0.00065048
115 | 0.98132 | -0.35874 | 0 | 0
116 | 0.97403 | -0.50171 | 0.0053328 | 0.0013365
117 | 0.97394 | -0.50341 | 0.0037016 | 0.00092771
118 | 0.98097 | -0.36571 | 0.0042241 | 0.0010587
119 | 0.98078 | -0.36936 | 0.0020586 | 0.00051593
120 | 0.97396 | -0.50308 | 0.0059602 | 0.0014938
121 | 0.97391 | -0.50409 | 0.0030586 | 0.00076656
122 | 0.98037 | -0.37733 | 0.0020757 | 0.00052022
123 | 0.98041 | -0.37671 | 0.002074 | 0.0005198
124 | 0.98045 | -0.37592 | 0.0020784 | 0.0005209
125 | 0.9805 | -0.3749 | 0.002076 | 0.00052029
126 | 0.98056 | -0.37367 | 0.0020757 | 0.00052022
127 | 0.9806 | -0.37297 | 0 | 0
128 | 0.97372 | -0.5079 | 0.012756 | 0.003197
129 | 0.98059 | -0.37308 | 0.002074 | 0.0005198
130 | 0.99258 | -0.14097 | 0.0021269 | 0.00053306
131 | 0.99226 | -0.14704 | 0.0021285 | 0.00053344
132 | 0.99179 | -0.15602 | 0.0019972 | 0.00050055
133 | 0.9923 | -0.14643 | 0.0043784 | 0.0010973
134 | 0.99228 | -0.14682 | 0.013134 | 0.0032916
135 | 0.97383 | -0.50445 | 0.0015121 | 0.00037898
136 | 0.97373 | -0.50647 | 0.001433 | 0.00035915
137 | 0.97361 | -0.50879 | 0.0015093 | 0.00037826
138 | 0.97348 | -0.51126 | 0.001433 | 0.00035914
139 | 0.97329 | -0.51515 | 0.0015096 | 0.00037835
140 | 0.97328 | -0.51528 | 0.0019724 | 0.00049433
141 | 0.97323 | -0.51631 | 0.009494 | 0.0023794
142 | 0.97277 | -0.52535 | 0.007063 | 0.0017701
143 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.002218 | -0.00055587 | 0.0022185 | 0.0005546 | 5.2741e-07 | -1.2787e-06 | 0.0033397 | 0.0033392 | 0.0033397 | 0.98822 | -0.22519 | 0.98847 | -0.22019 | 0.91751
1 | -0.013333 | -0.0033402 | 0.013336 | 0.0033417 | 2.6828e-06 | 1.4893e-06 | 0.020071 | 0.020071 | 0.020071 | 0.98847 | -0.22019 | 0.98869 | -0.21597 | 5.514
2 | -0.0069868 | -0.0017508 | 0.0069873 | 0.001751 | 5.1397e-07 | 1.6815e-07 | 0.010485 | 0.010485 | 0.010485 | 0.99151 | -0.1617 | 0.99159 | -0.16015 | 2.8806
3 | 0.0042455 | 0.0010638 | -0.0042453 | -0.0010638 | 2.6152e-07 | -5.4172e-08 | 0.0063715 | 0.0063715 | 0.0063715 | 0.99151 | -0.1617 | 0.99144 | -0.16299 | 1.7504
4 | -0.0096904 | -0.0024284 | 0.0096906 | 0.0024285 | 1.7759e-07 | 8.4767e-08 | 0.014542 | 0.014542 | 0.014542 | 0.99159 | -0.16015 | 0.99161 | -0.15977 | 3.995
5 | 0.0042453 | 0.0010638 | -0.0042452 | -0.0010638 | 5.4195e-08 | -1.1222e-08 | 0.0063715 | 0.0063716 | 0.0063716 | 0.99144 | -0.16299 | 0.99143 | -0.16326 | 1.7504
6 | -0.20243 | -0.051331 | 0.20254 | 0.051403 | 0.00011427 | 7.2071e-05 | 0.30398 | 0.30398 | 0.30398 | 0.99161 | -0.15977 | 0.99222 | -0.14803 | 16.7022
7 | 0.19274 | 0.048903 | -0.19263 | -0.048835 | 0.00010766 | 6.7799e-05 | 0.28944 | 0.28944 | 0.28944 | 0.99161 | -0.15977 | 0.991 | -0.17139 | 15.9033
8 | 0.0018581 | 0.00046554 | -0.001858 | -0.00046567 | 3.4125e-08 | -1.2905e-07 | 0.0027887 | 0.0027888 | 0.0027888 | 0.99143 | -0.16326 | 0.99141 | -0.16364 | 0.76614
9 | -0.20477 | -0.051962 | 0.20487 | 0.052021 | 9.4415e-05 | 5.9564e-05 | 0.30732 | 0.30732 | 0.30732 | 0.99222 | -0.14803 | 0.99272 | -0.13845 | 16.8859
10 | 0.19014 | 0.04821 | -0.19008 | -0.048172 | 6.0511e-05 | 3.809e-05 | 0.2857 | 0.2857 | 0.2857 | 0.991 | -0.17139 | 0.99066 | -0.17801 | 15.6976
11 | 0.0046939 | 0.0011762 | -0.0046939 | -0.0011762 | 2.4728e-08 | -1.2396e-09 | 0.0070519 | 0.0070519 | 0.0070519 | 0.99045 | -0.1821 | 0.99044 | -0.18221 | 1.9373
12 | -0.0046939 | -0.0011762 | 0.004694 | 0.0011762 | 1.7369e-07 | -8.7135e-09 | 0.0070519 | 0.0070518 | 0.0070519 | 0.99045 | -0.1821 | 0.99049 | -0.18132 | 1.9373
13 | 0.0046939 | 0.0011762 | -0.0046937 | -0.0011762 | 1.6784e-07 | -8.4078e-09 | 0.0070519 | 0.0070519 | 0.0070519 | 0.99044 | -0.18221 | 0.9904 | -0.18296 | 1.9373
14 | -0.0070775 | -0.0017735 | 0.0070781 | 0.0017737 | 5.3355e-07 | 1.7947e-07 | 0.010633 | 0.010632 | 0.010633 | 0.99049 | -0.18132 | 0.99057 | -0.17974 | 2.921
15 | -0.20759 | -0.052704 | 0.20775 | 0.052807 | 0.00016281 | 0.00010275 | 0.31141 | 0.31141 | 0.31141 | 0.99272 | -0.13845 | 0.99357 | -0.12216 | 17.1103
16 | 0.18047 | 0.045763 | -0.18034 | -0.045685 | 0.00012381 | 7.7797e-05 | 0.27126 | 0.27126 | 0.27126 | 0.99066 | -0.17801 | 0.98991 | -0.1923 | 14.9044
17 | 0.0096107 | 0.0024086 | -0.0096107 | -0.0024086 | 4.4153e-08 | 2.0983e-08 | 0.014436 | 0.014436 | 0.014436 | 0.99066 | -0.17801 | 0.99065 | -0.17811 | 3.9659
18 | 0.002246 | 0.00056275 | -0.0022459 | -0.00056288 | 5.4461e-08 | -1.2927e-07 | 0.0033744 | 0.0033745 | 0.0033745 | 0.9904 | -0.18296 | 0.99038 | -0.18347 | 0.92705
19 | -0.0096099 | -0.0024083 | 0.0096107 | 0.0024086 | 7.4457e-07 | 3.5386e-07 | 0.014436 | 0.014436 | 0.014436 | 0.99057 | -0.17974 | 0.99065 | -0.17811 | 3.9659
20 | -0.20775 | -0.052807 | 0.20789 | 0.052894 | 0.00013785 | 8.6998e-05 | 0.31141 | 0.31141 | 0.31141 | 0.99357 | -0.12216 | 0.99429 | -0.1084 | 17.1102
21 | 0.17795 | 0.045086 | -0.17788 | -0.045039 | 7.5585e-05 | 4.7471e-05 | 0.26767 | 0.26767 | 0.26767 | 0.98991 | -0.1923 | 0.98946 | -0.20114 | 14.707
22 | -0.0051077 | -0.0012801 | 0.0051086 | 0.0012802 | 9.3622e-07 | 8.238e-08 | 0.007779 | 0.0077788 | 0.007779 | 0.97703 | -0.44155 | 0.97723 | -0.43771 | 2.1371
23 | -0.0065413 | -0.0016392 | 0.0065419 | 0.0016394 | 5.8236e-07 | 1.7657e-07 | 0.0099603 | 0.0099602 | 0.0099603 | 0.97723 | -0.43771 | 0.97732 | -0.43584 | 2.7363
24 | -0.0065419 | -0.0016394 | 0.0065455 | 0.0016405 | 3.6539e-06 | 1.1069e-06 | 0.0099602 | 0.0099598 | 0.0099602 | 0.97732 | -0.43584 | 0.97792 | -0.42412 | 2.7363
25 | 0.10899 | 0.027636 | -0.10879 | -0.02751 | 0.00020641 | 0.0001257 | 0.16497 | 0.16497 | 0.16497 | 0.98379 | -0.3098 | 0.98176 | -0.34928 | 9.0645
26 | -0.10899 | -0.027636 | 0.10924 | 0.027786 | 0.00024577 | 0.00014963 | 0.16497 | 0.16497 | 0.16497 | 0.98379 | -0.3098 | 0.98621 | -0.263 | 9.0644
27 | 0.1081 | 0.027338 | -0.10802 | -0.027289 | 7.9824e-05 | 4.8585e-05 | 0.16393 | 0.16393 | 0.16393 | 0.98176 | -0.34928 | 0.98096 | -0.36468 | 9.0072
28 | -0.10924 | -0.027786 | 0.1096 | 0.028006 | 0.00036242 | 0.00022058 | 0.16497 | 0.16497 | 0.16497 | 0.98621 | -0.263 | 0.98979 | -0.19439 | 9.0642
29 | 0.082187 | 0.020726 | -0.082049 | -0.020645 | 0.00013718 | 8.048e-05 | 0.1251 | 0.12511 | 0.12511 | 0.97792 | -0.42412 | 0.97614 | -0.45905 | 6.8739
30 | -0.088732 | -0.022366 | 0.088868 | 0.022447 | 0.00013628 | 8.0958e-05 | 0.13506 | 0.13506 | 0.13506 | 0.97792 | -0.42412 | 0.97956 | -0.39207 | 7.421
31 | 0.098194 | 0.024827 | -0.098137 | -0.024792 | 5.7485e-05 | 3.4614e-05 | 0.14903 | 0.14903 | 0.14903 | 0.98096 | -0.36468 | 0.98034 | -0.3769 | 8.1884
32 | -0.11228 | -0.028677 | 0.11228 | 0.028678 | 2.814e-06 | 1.7165e-06 | 0.16898 | 0.16898 | 0.16898 | 0.98979 | -0.19439 | 0.98981 | -0.19387 | 9.2849
33 | 0.082049 | 0.020645 | -0.082029 | -0.020633 | 2.0606e-05 | 1.2091e-05 | 0.12511 | 0.12511 | 0.12511 | 0.97614 | -0.45905 | 0.97587 | -0.4643 | 6.8739
34 | -0.092329 | -0.023314 | 0.092366 | 0.023336 | 3.6412e-05 | 2.1751e-05 | 0.14032 | 0.14032 | 0.14032 | 0.97956 | -0.39207 | 0.97998 | -0.38384 | 7.7098
35 | 0.080301 | 0.0202 | -0.08026 | -0.020175 | 4.101e-05 | 2.5427e-05 | 0.12247 | 0.12247 | 0.12247 | 0.97587 | -0.4643 | 0.97532 | -0.475 | 11.2153
36 | 0.0034009 | 0.0008511 | -0.0034002 | -0.00085151 | 6.525e-07 | -4.0564e-07 | 0.0051616 | 0.0051619 | 0.0051619 | 0.98034 | -0.3769 | 0.98013 | -0.38093 | 1.4181
37 | 0.094736 | 0.023941 | -0.094704 | -0.023922 | 3.1526e-05 | 1.8897e-05 | 0.14387 | 0.14387 | 0.14387 | 0.98034 | -0.3769 | 0.97998 | -0.38384 | 7.9048
38 | 0.048901 | 0.012288 | -0.048841 | -0.01225 | 5.9758e-05 | 3.7889e-05 | 0.074671 | 0.074672 | 0.074672 | 0.97462 | -0.48885 | 0.97332 | -0.51449 | 20.5142
39 | 0.0014998 | 0.00037584 | -0.0014998 | -0.00037589 | 7.2132e-09 | -4.1099e-08 | 0.0022898 | 0.0022899 | 0.0022899 | 0.97462 | -0.48885 | 0.97462 | -0.48896 | 0.62908
40 | -0.050401 | -0.012664 | 0.050405 | 0.012666 | 4.1724e-06 | 2.5767e-06 | 0.076961 | 0.076961 | 0.076961 | 0.97462 | -0.48885 | 0.97471 | -0.48712 | 10.5716
41 | 0.034943 | 0.0087663 | -0.034927 | -0.0087563 | 1.6016e-05 | 1.0064e-05 | 0.053424 | 0.053424 | 0.053424 | 0.97332 | -0.51449 | 0.97283 | -0.52411 | 14.6768
42 | 0.013898 | 0.0034835 | -0.013898 | -0.0034831 | 8.5438e-07 | 4.8409e-07 | 0.021248 | 0.021248 | 0.021248 | 0.97332 | -0.51449 | 0.97325 | -0.51578 | 5.8374
43 | 0.024848 | 0.0062368 | -0.024841 | -0.0062329 | 6.2478e-06 | 3.8543e-06 | 0.037936 | 0.037936 | 0.037936 | 0.97471 | -0.48712 | 0.97444 | -0.49239 | 10.4221
44 | -0.075252 | -0.018903 | 0.075296 | 0.01893 | 4.3553e-05 | 2.7435e-05 | 0.1149 | 0.1149 | 0.1149 | 0.97471 | -0.48712 | 0.97532 | -0.475 | 15.7827
45 | 0.0070634 | 0.0017703 | -0.0070633 | -0.0017703 | 1.1801e-07 | 4.2053e-08 | 0.010804 | 0.010804 | 0.010804 | 0.97283 | -0.52411 | 0.97281 | -0.52446 | 2.9681
46 | 0.027863 | 0.006986 | -0.027858 | -0.0069828 | 5.0395e-06 | 3.1334e-06 | 0.04262 | 0.04262 | 0.04262 | 0.97283 | -0.52411 | 0.97264 | -0.5279 | 11.7087
47 | 0.0023095 | 0.00057814 | -0.0023093 | -0.00057843 | 1.3837e-07 | -2.8975e-07 | 0.0035059 | 0.0035061 | 0.0035061 | 0.98013 | -0.38093 | 0.98007 | -0.38219 | 0.96321
48 | 0.0043059 | 0.0010791 | -0.0043058 | -0.0010791 | 9.0795e-08 | -1.6051e-08 | 0.0064755 | 0.0064756 | 0.0064756 | 0.98946 | -0.20114 | 0.98943 | -0.20158 | 1.779
49 | 0.17357 | 0.043959 | -0.17351 | -0.043922 | 6.0437e-05 | 3.7921e-05 | 0.26119 | 0.26119 | 0.26119 | 0.98946 | -0.20114 | 0.98908 | -0.20839 | 14.3512
50 | 0.010247 | 0.0025685 | -0.010246 | -0.0025678 | 1.3404e-06 | 6.6488e-07 | 0.015416 | 0.015416 | 0.015416 | 0.98908 | -0.20839 | 0.98894 | -0.21114 | 4.2353
51 | 0.013341 | 0.0033444 | -0.013336 | -0.0033417 | 4.8118e-06 | 2.6709e-06 | 0.020071 | 0.020071 | 0.020071 | 0.98908 | -0.20839 | 0.98869 | -0.21597 | 5.514
52 | 0.14992 | 0.038009 | -0.14978 | -0.037917 | 0.00014633 | 9.1198e-05 | 0.2257 | 0.22571 | 0.22571 | 0.98908 | -0.20839 | 0.98803 | -0.22872 | 12.4014
53 | 0.12174 | 0.030825 | -0.12169 | -0.030792 | 5.4684e-05 | 3.3619e-05 | 0.18372 | 0.18372 | 0.18372 | 0.98665 | -0.25525 | 0.98617 | -0.26461 | 10.0944
54 | -0.12174 | -0.030825 | 0.12175 | 0.030831 | 9.8146e-06 | 6.0337e-06 | 0.18372 | 0.18372 | 0.18372 | 0.98665 | -0.25525 | 0.98674 | -0.25357 | 10.0944
55 | 0.12169 | 0.030792 | -0.12167 | -0.030782 | 1.5841e-05 | 9.7388e-06 | 0.18372 | 0.18372 | 0.18372 | 0.98617 | -0.26461 | 0.98603 | -0.26732 | 10.0944
56 | -0.13977 | -0.035348 | 0.13982 | 0.035373 | 4.1284e-05 | 2.5631e-05 | 0.21089 | 0.21089 | 0.21089 | 0.98674 | -0.25357 | 0.98706 | -0.24742 | 11.5876
57 | -0.13982 | -0.035373 | 0.13988 | 0.035416 | 6.8992e-05 | 4.2832e-05 | 0.21089 | 0.21089 | 0.21089 | 0.98706 | -0.24742 | 0.98759 | -0.23714 | 11.5876
58 | -0.13988 | -0.035416 | 0.1399 | 0.035424 | 1.2501e-05 | 7.7611e-06 | 0.21089 | 0.21089 | 0.21089 | 0.98759 | -0.23714 | 0.98769 | -0.23528 | 11.5876
59 | -0.14973 | -0.037888 | 0.14978 | 0.037917 | 4.7122e-05 | 2.9369e-05 | 0.22571 | 0.22571 | 0.22571 | 0.98769 | -0.23528 | 0.98803 | -0.22872 | 12.4014
60 | 0.12167 | 0.030782 | -0.12164 | -0.030764 | 2.899e-05 | 1.7824e-05 | 0.18372 | 0.18372 | 0.18372 | 0.98603 | -0.26732 | 0.98577 | -0.27229 | 10.0944
61 | -0.37842 | -0.096428 | 0.38031 | 0.097632 | 0.0018902 | 0.0012046 | 0.56673 | 0.56673 | 0.56673 | 0.99457 | -0.10296 | 1 | 0 | 31.1389
62 | 0.37842 | 0.096428 | -0.37832 | -0.096364 | 9.9293e-05 | 6.328e-05 | 0.56673 | 0.56673 | 0.56673 | 0.99457 | -0.10296 | 0.99429 | -0.1084 | 31.1389
63 | 0.17042 | 0.043471 | -0.17033 | -0.043411 | 9.5097e-05 | 5.9601e-05 | 0.25532 | 0.25532 | 0.25532 | 0.99429 | -0.1084 | 0.99368 | -0.11996 | 14.0287
64 | 0.16833 | 0.042911 | -0.16822 | -0.042841 | 0.00011044 | 6.9185e-05 | 0.25233 | 0.25233 | 0.25233 | 0.99368 | -0.11996 | 0.99297 | -0.13356 | 13.8645
65 | 0.14481 | 0.036969 | -0.14476 | -0.036939 | 4.7548e-05 | 2.9562e-05 | 0.21724 | 0.21724 | 0.21724 | 0.99297 | -0.13356 | 0.99261 | -0.14036 | 11.9365
66 | 0.023415 | 0.0058728 | -0.023413 | -0.0058714 | 2.3784e-06 | 1.4556e-06 | 0.03509 | 0.03509 | 0.03509 | 0.99297 | -0.13356 | 0.99286 | -0.13569 | 9.6401
67 | 0.0015141 | 0.00037917 | -0.0015141 | -0.00037947 | 4.8841e-08 | -2.9583e-07 | 0.0022692 | 0.0022693 | 0.0022693 | 0.99286 | -0.13569 | 0.99282 | -0.13637 | 0.62342
68 | 0.021898 | 0.0054922 | -0.021889 | -0.0054864 | 9.4863e-06 | 5.7677e-06 | 0.032821 | 0.032821 | 0.032821 | 0.99286 | -0.13569 | 0.99239 | -0.14478 | 9.0168
69 | 0.017514 | 0.0043899 | -0.017512 | -0.0043891 | 1.3721e-06 | 8.0962e-07 | 0.026261 | 0.026261 | 0.026261 | 0.99239 | -0.14478 | 0.9923 | -0.14643 | 7.2145
70 | 0.10395 | 0.026326 | -0.10377 | -0.026212 | 0.00018039 | 0.00011446 | 0.15702 | 0.15702 | 0.15702 | 0.98569 | -0.27382 | 0.98382 | -0.31002 | 21.5686
71 | -0.10395 | -0.026326 | 0.10396 | 0.026331 | 7.6167e-06 | 4.6122e-06 | 0.15702 | 0.15702 | 0.15702 | 0.98569 | -0.27382 | 0.98577 | -0.27229 | 8.6274
72 | 0.10117 | 0.025561 | -0.10095 | -0.02542 | 0.00022124 | 0.00014127 | 0.15309 | 0.15309 | 0.15309 | 0.98382 | -0.31002 | 0.98148 | -0.35575 | 42.0588
73 | -0.0022991 | -0.0005762 | 0.0022991 | 0.00057615 | 2.4597e-08 | -5.2424e-08 | 0.0034864 | 0.0034864 | 0.0034864 | 0.98125 | -0.36025 | 0.98126 | -0.36003 | 0.95781
74 | -0.0045999 | -0.0011528 | 0.0046002 | 0.0011528 | 2.8229e-07 | -1.4783e-08 | 0.0069754 | 0.0069754 | 0.0069754 | 0.98126 | -0.36003 | 0.98132 | -0.35874 | 1.9163
75 | 0.14276 | 0.036438 | -0.14276 | -0.036436 | 4.2012e-06 | 2.6099e-06 | 0.21425 | 0.21425 | 0.21425 | 0.99261 | -0.14036 | 0.99258 | -0.14097 | 11.772
76 | 0.001183 | 0.00029615 | -0.001183 | -0.00029648 | 3.3905e-08 | -3.3147e-07 | 0.001796 | 0.0017962 | 0.0017962 | 0.98007 | -0.38219 | 0.98004 | -0.38279 | 0.49345
77 | 0.023332 | 0.0058546 | -0.02333 | -0.0058534 | 1.9073e-06 | 1.1708e-06 | 0.035631 | 0.035631 | 0.035631 | 0.97444 | -0.49239 | 0.97435 | -0.49411 | 9.7888
78 | 0.021816 | 0.005474 | -0.021812 | -0.0054718 | 3.6372e-06 | 2.219e-06 | 0.033319 | 0.03332 | 0.03332 | 0.97435 | -0.49411 | 0.97418 | -0.4976 | 9.1537
79 | -0.0014991 | -0.00037572 | 0.0014991 | 0.00037562 | 1.6202e-08 | -9.1897e-08 | 0.0022917 | 0.0022917 | 0.0022917 | 0.97339 | -0.51309 | 0.9734 | -0.51286 | 0.62959
80 | -0.014477 | -0.0036288 | 0.014478 | 0.0036294 | 1.1103e-06 | 6.3541e-07 | 0.022131 | 0.022131 | 0.022131 | 0.9734 | -0.51286 | 0.97348 | -0.51126 | 6.08
81 | 0.012978 | 0.0032532 | -0.012977 | -0.0032524 | 1.4145e-06 | 7.8615e-07 | 0.019839 | 0.019839 | 0.019839 | 0.9734 | -0.51286 | 0.97329 | -0.51515 | 5.4504
82 | -0.002076 | -0.00052029 | 0.002076 | 0.00052023 | 2.0243e-08 | -5.5596e-08 | 0.003151 | 0.003151 | 0.003151 | 0.98034 | -0.37794 | 0.98035 | -0.37774 | 0.86567
83 | -0.004152 | -0.0010405 | 0.0041521 | 0.0010405 | 8.0979e-08 | -1.6733e-08 | 0.006302 | 0.006302 | 0.006302 | 0.98035 | -0.37774 | 0.98037 | -0.37733 | 1.7313
84 | 0.0070633 | 0.0017703 | -0.007063 | -0.0017701 | 2.9984e-07 | 1.0685e-07 | 0.010804 | 0.010804 | 0.010804 | 0.97281 | -0.52446 | 0.97277 | -0.52535 | 2.9681
85 | 0.027858 | 0.0069828 | -0.027856 | -0.0069813 | 2.5135e-06 | 1.5628e-06 | 0.04262 | 0.04262 | 0.04262 | 0.97264 | -0.5279 | 0.97254 | -0.5298 | 11.7087
86 | 0.020378 | 0.0051123 | -0.020371 | -0.0051083 | 6.6435e-06 | 4.0243e-06 | 0.031128 | 0.031128 | 0.031128 | 0.97418 | -0.4976 | 0.97383 | -0.50445 | 8.5518
87 | 0.12342 | 0.031516 | -0.12342 | -0.031516 | 2.125e-07 | 1.307e-07 | 0.18552 | 0.18552 | 0.18552 | 0.991 | -0.17112 | 0.991 | -0.17115 | 10.1936
88 | -0.12609 | -0.032186 | 0.12609 | 0.032188 | 3.942e-06 | 2.4286e-06 | 0.18954 | 0.18954 | 0.18954 | 0.991 | -0.17112 | 0.99104 | -0.17047 | 10.4141
89 | 0.12142 | 0.031016 | -0.1214 | -0.031001 | 2.4238e-05 | 1.4888e-05 | 0.18253 | 0.18253 | 0.18253 | 0.991 | -0.17115 | 0.99079 | -0.17528 | 10.029
90 | -0.12809 | -0.032688 | 0.1281 | 0.032694 | 9.4731e-06 | 5.8433e-06 | 0.19253 | 0.19253 | 0.19253 | 0.99104 | -0.17047 | 0.99112 | -0.16894 | 10.5787
91 | 0.11506 | 0.029411 | -0.11495 | -0.029348 | 0.00010333 | 6.3172e-05 | 0.173 | 0.173 | 0.173 | 0.99079 | -0.17528 | 0.98981 | -0.19387 | 9.5057
92 | -0.13007 | -0.033189 | 0.13012 | 0.033216 | 4.3404e-05 | 2.6802e-05 | 0.1955 | 0.1955 | 0.1955 | 0.99112 | -0.16894 | 0.99148 | -0.16203 | 10.7416
93 | -0.13224 | -0.033749 | 0.13228 | 0.03377 | 3.4111e-05 | 2.1088e-05 | 0.19869 | 0.19869 | 0.19869 | 0.99148 | -0.16203 | 0.99176 | -0.1567 | 10.9169
94 | -0.13427 | -0.03427 | 0.13428 | 0.034273 | 4.2476e-06 | 2.6286e-06 | 0.20168 | 0.20168 | 0.20168 | 0.99176 | -0.1567 | 0.99179 | -0.15604 | 11.0815
95 | -0.13641 | -0.034806 | 0.13641 | 0.034806 | 1.782e-07 | 1.1039e-07 | 0.20487 | 0.20487 | 0.20487 | 0.99179 | -0.15604 | 0.99179 | -0.15602 | 11.2568
96 | 0.044253 | 0.01115 | -0.044244 | -0.011145 | 9.2108e-06 | 5.8267e-06 | 0.067292 | 0.067292 | 0.067292 | 0.97888 | -0.40651 | 0.97865 | -0.41086 | 18.4867
97 | -0.046376 | -0.011682 | 0.046386 | 0.011689 | 1.0118e-05 | 6.4075e-06 | 0.070518 | 0.070518 | 0.070518 | 0.97888 | -0.40651 | 0.97911 | -0.40195 | 19.3731
98 | 0.04212 | 0.010612 | -0.042113 | -0.010608 | 7.1444e-06 | 4.5141e-06 | 0.064062 | 0.064063 | 0.064063 | 0.97865 | -0.41086 | 0.97847 | -0.41441 | 17.5996
99 | -0.048511 | -0.012221 | 0.048566 | 0.012256 | 5.5214e-05 | 3.4996e-05 | 0.073748 | 0.073748 | 0.073748 | 0.97911 | -0.40195 | 0.98033 | -0.37818 | 20.2604
100 | 0.039988 | 0.010075 | -0.039958 | -0.010057 | 2.9355e-05 | 1.8522e-05 | 0.060831 | 0.060831 | 0.060831 | 0.97847 | -0.41441 | 0.97769 | -0.42977 | 16.7117
101 | -0.05069 | -0.012789 | 0.05069 | 0.012789 | 1.3613e-07 | 8.6349e-08 | 0.076972 | 0.076972 | 0.076972 | 0.98033 | -0.37818 | 0.98033 | -0.37813 | 21.146
102 | 0.0020624 | 0.00051677 | -0.0020623 | -0.00051687 | 3.4024e-08 | -9.3707e-08 | 0.0031388 | 0.0031389 | 0.0031389 | 0.97769 | -0.42977 | 0.97767 | -0.43012 | 0.86232
103 | 0.037896 | 0.0095398 | -0.03788 | -0.0095297 | 1.6128e-05 | 1.016e-05 | 0.057692 | 0.057692 | 0.057692 | 0.97769 | -0.42977 | 0.97723 | -0.43868 | 15.8494
104 | -0.053231 | -0.013426 | 0.053232 | 0.013426 | 5.183e-07 | 3.2905e-07 | 0.080829 | 0.080829 | 0.080829 | 0.98033 | -0.37813 | 0.98034 | -0.37792 | 22.2057
105 | 0.0041219 | 0.001033 | -0.0041219 | -0.001033 | 6.7037e-08 | -1.3951e-08 | 0.0062764 | 0.0062764 | 0.0062764 | 0.97723 | -0.43868 | 0.97722 | -0.43902 | 1.7243
106 | 0.033758 | 0.0084966 | -0.033745 | -0.0084886 | 1.2869e-05 | 8.0735e-06 | 0.051416 | 0.051416 | 0.051416 | 0.97723 | -0.43868 | 0.97683 | -0.44666 | 14.1252
107 | -0.055826 | -0.014076 | 0.055829 | 0.014078 | 3.7213e-06 | 2.3642e-06 | 0.084766 | 0.084766 | 0.084766 | 0.98034 | -0.37792 | 0.98041 | -0.37653 | 23.2873
108 | 0.0028497 | 0.00071392 | -0.0028495 | -0.00071415 | 2.0328e-07 | -2.2999e-07 | 0.0043409 | 0.004341 | 0.004341 | 0.97683 | -0.44666 | 0.97675 | -0.44816 | 1.1926
109 | 0.030895 | 0.0077746 | -0.030819 | -0.0077267 | 7.674e-05 | 4.7961e-05 | 0.047075 | 0.047075 | 0.047075 | 0.97683 | -0.44666 | 0.97418 | -0.49877 | 12.9327
110 | -0.058425 | -0.014729 | 0.058429 | 0.014731 | 4.0883e-06 | 2.599e-06 | 0.088705 | 0.088705 | 0.088705 | 0.98041 | -0.37653 | 0.98049 | -0.37507 | 24.3695
111 | 0.0041173 | 0.0010318 | -0.0041172 | -0.0010318 | 7.9637e-08 | -1.7667e-08 | 0.0062477 | 0.0062477 | 0.0062477 | 0.98061 | -0.37271 | 0.98059 | -0.37311 | 1.7164
112 | -0.0061758 | -0.0015477 | 0.006176 | 0.0015478 | 1.7912e-07 | 4.6022e-08 | 0.0093714 | 0.0093714 | 0.0093714 | 0.98061 | -0.37271 | 0.98064 | -0.3721 | 2.5746
113 | 0.0020586 | 0.00051587 | -0.0020586 | -0.00051593 | 1.9903e-08 | -5.5872e-08 | 0.0031238 | 0.0031239 | 0.0031239 | 0.98059 | -0.37311 | 0.98058 | -0.37332 | 0.85821
114 | -0.0082346 | -0.0020637 | 0.0082349 | 0.0020638 | 3.1853e-07 | 1.3522e-07 | 0.012495 | 0.012495 | 0.012495 | 0.98064 | -0.3721 | 0.98068 | -0.37129 | 3.4327
115 | -0.010293 | -0.0025798 | 0.010294 | 0.00258 | 4.9753e-07 | 2.4979e-07 | 0.015619 | 0.015619 | 0.015619 | 0.98068 | -0.37129 | 0.98073 | -0.37027 | 4.2908
116 | -0.012353 | -0.0030959 | 0.012354 | 0.0030968 | 1.5597e-06 | 8.4876e-07 | 0.018742 | 0.018742 | 0.018742 | 0.98073 | -0.37027 | 0.98087 | -0.36762 | 5.1489
117 | 0.018671 | 0.0046813 | -0.01867 | -0.0046804 | 1.5453e-06 | 9.2417e-07 | 0.028325 | 0.028325 | 0.028325 | 0.98087 | -0.36762 | 0.98078 | -0.36936 | 7.7817
118 | -0.031025 | -0.0077781 | 0.031028 | 0.0077799 | 2.8255e-06 | 1.7654e-06 | 0.047067 | 0.047067 | 0.047067 | 0.98087 | -0.36762 | 0.98097 | -0.36571 | 12.9306
119 | 0.011295 | 0.0028312 | -0.011293 | -0.0028304 | 1.5773e-06 | 8.3358e-07 | 0.017253 | 0.017253 | 0.017253 | 0.97418 | -0.49877 | 0.97403 | -0.50171 | 4.7398
120 | 0.019524 | 0.0048954 | -0.019519 | -0.0048928 | 4.3117e-06 | 2.5986e-06 | 0.029822 | 0.029822 | 0.029822 | 0.97418 | -0.49877 | 0.97394 | -0.50341 | 8.1929
121 | 0.061081 | 0.015418 | -0.061024 | -0.015382 | 5.6471e-05 | 3.592e-05 | 0.092644 | 0.092644 | 0.092644 | 0.98148 | -0.35575 | 0.98049 | -0.37507 | 25.4516
122 | 0.03987 | 0.010002 | -0.039864 | -0.0099987 | 5.6828e-06 | 3.5846e-06 | 0.06045 | 0.06045 | 0.06045 | 0.98148 | -0.35575 | 0.98132 | -0.35874 | 16.6072
123 | 0.035264 | 0.0088459 | -0.035252 | -0.0088386 | 1.1714e-05 | 7.3589e-06 | 0.053475 | 0.053475 | 0.053475 | 0.98132 | -0.35874 | 0.98097 | -0.36571 | 14.6909
124 | 0.0059606 | 0.0014939 | -0.0059602 | -0.0014938 | 3.9085e-07 | 9.3706e-08 | 0.009106 | 0.009106 | 0.009106 | 0.97403 | -0.50171 | 0.97396 | -0.50308 | 2.5017
125 | 0.015818 | 0.0039651 | -0.015817 | -0.0039648 | 5.1228e-07 | 2.9875e-07 | 0.024167 | 0.024167 | 0.024167 | 0.97394 | -0.50341 | 0.97391 | -0.50409 | 6.6392
126 | 0.016611 | 0.0041645 | -0.016608 | -0.0041628 | 2.8625e-06 | 1.6804e-06 | 0.025202 | 0.025202 | 0.025202 | 0.98078 | -0.36936 | 0.9806 | -0.37297 | 6.9237
127 | 0.012758 | 0.0031983 | -0.012756 | -0.003197 | 2.3138e-06 | 1.2788e-06 | 0.019494 | 0.019494 | 0.019494 | 0.97391 | -0.50409 | 0.97372 | -0.5079 | 5.3554
128 | -0.0062277 | -0.0015607 | 0.0062279 | 0.0015608 | 1.8221e-07 | 4.804e-08 | 0.0094525 | 0.0094524 | 0.0094525 | 0.98037 | -0.37733 | 0.98041 | -0.37671 | 2.5968
129 | -0.0083019 | -0.0020806 | 0.0083023 | 0.0020807 | 3.1244e-07 | 1.3378e-07 | 0.0126 | 0.0126 | 0.0126 | 0.98041 | -0.37671 | 0.98045 | -0.37592 | 3.4616
130 | -0.010381 | -0.0026016 | 0.010381 | 0.0026019 | 5.0645e-07 | 2.555e-07 | 0.015755 | 0.015755 | 0.015755 | 0.98045 | -0.37592 | 0.9805 | -0.3749 | 4.3282
131 | -0.012457 | -0.0031222 | 0.012458 | 0.0031226 | 7.2877e-07 | 3.9783e-07 | 0.018905 | 0.018905 | 0.018905 | 0.9805 | -0.3749 | 0.98056 | -0.37367 | 5.1937
132 | -0.014534 | -0.0036428 | 0.014534 | 0.003643 | 4.8129e-07 | 2.7474e-07 | 0.022055 | 0.022055 | 0.022055 | 0.98056 | -0.37367 | 0.9806 | -0.37297 | 6.0591
133 | 0.002074 | 0.00051977 | -0.002074 | -0.0005198 | 9.9993e-09 | -2.756e-08 | 0.0031472 | 0.0031473 | 0.0031473 | 0.9806 | -0.37297 | 0.98059 | -0.37308 | 0.86463
134 | 0.14063 | 0.035903 | -0.14059 | -0.035877 | 4.1263e-05 | 2.561e-05 | 0.21106 | 0.21106 | 0.21106 | 0.99258 | -0.14097 | 0.99226 | -0.14704 | 11.5968
135 | 0.13846 | 0.035344 | -0.1384 | -0.035307 | 6.0028e-05 | 3.7222e-05 | 0.20787 | 0.20787 | 0.20787 | 0.99226 | -0.14704 | 0.99179 | -0.15602 | 11.4214
136 | 0.013134 | 0.0032918 | -0.013134 | -0.0032916 | 2.4654e-07 | 1.3589e-07 | 0.019695 | 0.019695 | 0.019695 | 0.9923 | -0.14643 | 0.99228 | -0.14682 | 5.4108
137 | 0.018859 | 0.0047293 | -0.018857 | -0.0047282 | 1.8209e-06 | 1.0926e-06 | 0.028818 | 0.028818 | 0.028818 | 0.97383 | -0.50445 | 0.97373 | -0.50647 | 7.917
138 | 0.017424 | 0.0043691 | -0.017422 | -0.0043679 | 1.9214e-06 | 1.1398e-06 | 0.026628 | 0.026628 | 0.026628 | 0.97373 | -0.50647 | 0.97361 | -0.50879 | 7.3154
139 | 0.015913 | 0.0039897 | -0.015911 | -0.0039886 | 1.8724e-06 | 1.0934e-06 | 0.024321 | 0.024321 | 0.024321 | 0.97361 | -0.50879 | 0.97348 | -0.51126 | 6.6817
140 | 0.011467 | 0.002874 | -0.011467 | -0.002874 | 7.0618e-08 | 3.7581e-08 | 0.017531 | 0.017531 | 0.017531 | 0.97329 | -0.51515 | 0.97328 | -0.51528 | 4.8163
141 | 0.0094945 | 0.0023797 | -0.009494 | -0.0023794 | 4.6331e-07 | 2.2365e-07 | 0.014516 | 0.014516 | 0.014516 | 0.97328 | -0.51528 | 0.97323 | -0.51631 | 3.9879

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38633 | 0.098729

## res_load
| p_mw | q_mvar
0 | 0.002218 | 0.00055587
1 | 0.011115 | 0.0027856
2 | 0.0027413 | 0.00068703
3 | 0.002703 | 0.00067744
4 | 0.0023872 | 0.00059828
5 | 0.0022288 | 0.00055859
6 | 0.0024934 | 0.00062491
7 | 0.0023835 | 0.00059736
8 | 0.001858 | 0.00046567
9 | 0.0027247 | 0.00068288
10 | 0.0024477 | 0.00061345
11 | 0.0025319 | 0.00063455
12 | 0.002391 | 0.00059923
13 | 0.0022459 | 0.00056288
14 | 0.0051077 | 0.0012801
15 | 0.0014326 | 0.00035906
16 | 0.000689 | 0.00017268
17 | 0.0098246 | 0.0024623
18 | 0.0026738 | 0.00067012
19 | 0.0034611 | 0.00086742
20 | 0.0017277 | 0.000433
21 | 0.0023385 | 0.00058609
22 | 0.0014998 | 0.00037589
23 | 0.013898 | 0.0034831
24 | 0.0049643 | 0.0012442
25 | 0.0010907 | 0.00027337
26 | 0.0043058 | 0.0010791
27 | 0.018021 | 0.0045166
28 | 0.0098319 | 0.0024641
29 | 0.010246 | 0.0025678
30 | 0.0043755 | 0.0010966
31 | 0.0019963 | 0.00050031
32 | 0.0015141 | 0.00037947
33 | 0.0043751 | 0.0010965
34 | 0.0025954 | 0.00065048
35 | 0.017688 | 0.004433
36 | 0.0022991 | 0.0005762
37 | 0.0023008 | 0.00057664
38 | 0.0019972 | 0.00050054
39 | 0.0011263 | 0.00028228
40 | 0.001183 | 0.00029648
41 | 0.0015096 | 0.00037835
42 | 0.0015137 | 0.00037938
43 | 0.0014991 | 0.00037572
44 | 0.002076 | 0.00052029
45 | 0.002076 | 0.00052029
46 | 0.027856 | 0.0069813
47 | 0.0014345 | 0.00035952
48 | 0.0026719 | 0.00066964
49 | 0.0019962 | 0.00050029
50 | 0.0019952 | 0.00050005
51 | 0.006342 | 0.0015894
52 | 0.0019745 | 0.00049485
53 | 0.0026734 | 0.00067001
54 | 0.0021269 | 0.00053306
55 | 0.0019962 | 0.00050029
56 | 0.0021269 | 0.00053306
57 | 0.0021224 | 0.00053193
58 | 0.0021238 | 0.00053229
59 | 0.0021253 | 0.00053264
60 | 0.0021252 | 0.00053264
61 | 0.0021238 | 0.00053229
62 | 0.0025413 | 0.0006369
63 | 0.0020623 | 0.00051687
64 | 0.0025937 | 0.00065004
65 | 0.0041219 | 0.001033
66 | 0.0025954 | 0.00065048
67 | 0.0020586 | 0.00051593
68 | 0.0020586 | 0.00051593
69 | 0.0020586 | 0.00051593
70 | 0.0020586 | 0.00051593
71 | 0.0020586 | 0.00051593
72 | 0.0020586 | 0.00051593
73 | 0.0028495 | 0.00071415
74 | 0.0025954 | 0.00065048
75 | 0.0053328 | 0.0013365
76 | 0.0037016 | 0.00092771
77 | 0.0042241 | 0.0010587
78 | 0.0020586 | 0.00051593
79 | 0.0059602 | 0.0014938
80 | 0.0030586 | 0.00076656
81 | 0.0020757 | 0.00052022
82 | 0.002074 | 0.0005198
83 | 0.0020784 | 0.0005209
84 | 0.002076 | 0.00052029
85 | 0.0020757 | 0.00052022
86 | 0.012756 | 0.003197
87 | 0.002074 | 0.0005198
88 | 0.0021269 | 0.00053306
89 | 0.0021285 | 0.00053344
90 | 0.0019972 | 0.00050055
91 | 0.0043784 | 0.0010973
92 | 0.013134 | 0.0032916
93 | 0.0015121 | 0.00037898
94 | 0.001433 | 0.00035915
95 | 0.0015093 | 0.00037826
96 | 0.001433 | 0.00035914
97 | 0.0015096 | 0.00037835
98 | 0.0019724 | 0.00049433
99 | 0.009494 | 0.0023794
100 | 0.007063 | 0.0017701

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1