## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1053-4_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1053-4_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1053-4_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1053-4_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1053-4_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1053-4_0_3_node_125 | 0.4 | n |  | TRUE
6 | bus_LV_1053-4_0_3_node_124 | 0.4 | n |  | TRUE
7 | bus_LV_1053-4_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1053-4_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1053-4_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1053-4_0_3_node_34 | 0.4 | n |  | TRUE
11 | bus_LV_1053-4_0_3_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_1053-4_0_3_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_1053-4_0_3_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1053-4_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1053-4_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1053-4_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1053-4_0_3_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1053-4_0_3_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_1053-4_0_3_node_81 | 0.4 | n |  | TRUE
20 | bus_LV_1053-4_0_3_node_68 | 0.4 | n |  | TRUE
21 | bus_LV_1053-4_0_3_node_80 | 0.4 | n |  | TRUE
22 | bus_LV_1053-4_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1053-4_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1053-4_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1053-4_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1053-4_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1053-4_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1053-4_0_3_node_93 | 0.4 | n |  | TRUE
29 | bus_LV_1053-4_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1053-4_0_3_node_94 | 0.4 | n |  | TRUE
31 | bus_LV_1053-4_0_3_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1053-4_0_3_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_1053-4_0_3_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_1053-4_0_3_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_1053-4_0_3_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_1053-4_0_3_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_1053-4_0_3_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1053-4_0_3_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1053-4_0_3_node_85 | 0.4 | n |  | TRUE
40 | bus_LV_1053-4_0_3_node_86 | 0.4 | n |  | TRUE
41 | bus_LV_1053-4_0_3_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1053-4_0_3_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1053-4_0_3_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1053-4_0_3_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1053-4_0_3_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_1053-4_0_3_node_82 | 0.4 | n |  | TRUE
47 | bus_LV_1053-4_0_3_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_1053-4_0_3_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_1053-4_0_3_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_1053-4_0_3_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_1053-4_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_1053-4_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1053-4_0_3_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_1053-4_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1053-4_0_3_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_1053-4_0_3_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_1053-4_0_3_node_118 | 0.4 | n |  | TRUE
58 | bus_LV_1053-4_0_3_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_1053-4_0_3_node_73 | 0.4 | n |  | TRUE
60 | bus_LV_1053-4_0_3_node_75 | 0.4 | n |  | TRUE
61 | bus_LV_1053-4_0_3_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_1053-4_0_3_node_130 | 0.4 | n |  | TRUE
63 | bus_LV_1053-4_0_3_node_117 | 0.4 | n |  | TRUE
64 | bus_LV_1053-4_0_3_node_114 | 0.4 | n |  | TRUE
65 | bus_LV_1053-4_0_3_node_74 | 0.4 | n |  | TRUE
66 | bus_LV_1053-4_0_3_node_47 | 0.4 | n |  | TRUE
67 | bus_LV_1053-4_0_3_node_127 | 0.4 | n |  | TRUE
68 | bus_LV_1053-4_0_3_node_128 | 0.4 | n |  | TRUE
69 | bus_LV_1053-4_0_3_node_122 | 0.4 | n |  | TRUE
70 | bus_LV_1053-4_0_3_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_1053-4_0_3_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1053-4_0_3_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_1053-4_0_3_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_1053-4_0_3_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_1053-4_0_3_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_1053-4_0_3_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_1053-4_0_3_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_1053-4_0_3_node_112 | 0.4 | n |  | TRUE
79 | bus_LV_1053-4_0_3_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_1053-4_0_3_node_111 | 0.4 | n |  | TRUE
81 | bus_LV_1053-4_0_3_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_1053-4_0_3_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_1053-4_0_3_node_56 | 0.4 | n |  | TRUE
84 | bus_LV_1053-4_0_3_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_1053-4_0_3_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_1053-4_0_3_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_1053-4_0_3_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_1053-4_0_3_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_1053-4_0_3_node_109 | 0.4 | n |  | TRUE
90 | bus_LV_1053-4_0_3_node_92 | 0.4 | n |  | TRUE
91 | bus_LV_1053-4_0_3_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_1053-4_0_3_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_1053-4_0_3_node_62 | 0.4 | n |  | TRUE
94 | bus_LV_1053-4_0_3_node_63 | 0.4 | n |  | TRUE
95 | bus_LV_1053-4_0_3_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_1053-4_0_3_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_1053-4_0_3_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_1053-4_0_3_node_108 | 0.4 | n |  | TRUE
99 | bus_LV_1053-4_0_3_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_1053-4_0_3_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_1053-4_0_3_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1053-4_0_3_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_1053-4_0_3_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_1053-4_0_3_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_1053-4_0_3_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_1053-4_0_3_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_1053-4_0_3_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_1053-4_0_3_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_1053-4_0_3_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_1053-4_0_3_node_90 | 0.4 | n |  | TRUE
111 | bus_LV_1053-4_0_3_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_1053-4_0_3_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_1053-4_0_3_node_110 | 0.4 | n |  | TRUE
114 | bus_LV_1053-4_0_3_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_1053-4_0_3_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_1053-4_0_3_node_95 | 0.4 | n |  | TRUE
117 | bus_LV_1053-4_0_3_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_1053-4_0_3_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_1053-4_0_3_node_107 | 0.4 | n |  | TRUE
120 | bus_LV_1053-4_0_3_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_1053-4_0_3_node_113 | 0.4 | n |  | TRUE
122 | bus_LV_1053-4_0_3_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_1053-4_0_3_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_1053-4_0_3_node_120 | 0.4 | n |  | TRUE
125 | bus_LV_1053-4_0_3_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_1053-4_0_3_node_123 | 0.4 | n |  | TRUE
127 | bus_MV_212_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1053-4_0_3_load_0 | 0 | 0.00084011 | 0.00021055 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1053-4_0_3_load_1 | 1 | 0.0041143 | 0.0010311 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1053-4_0_3_load_2 | 2 | 0.001011 | 0.00025338 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1053-4_0_3_load_3 | 3 | 0.00055319 | 0.00013864 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1053-4_0_3_load_4 | 4 | 0.00072795 | 0.00018244 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1053-4_0_3_load_124 | 6 | 0.0035175 | 0.00088156 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1053-4_0_3_load_5 | 7 | 0.00064607 | 0.00016192 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1053-4_0_3_load_6 | 9 | 0.0015935 | 0.00039936 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1053-4_0_3_load_67 | 11 | 0.0075007 | 0.0018798 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1053-4_0_3_load_9 | 13 | 0.0011477 | 0.00028764 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1053-4_0_3_load_13 | 17 | 0.0015071 | 0.00037772 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1053-4_0_3_load_69 | 18 | 0.0033293 | 0.0008344 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1053-4_0_3_load_81 | 19 | 0.0022441 | 0.00056241 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1053-4_0_3_load_68 | 20 | 0.0021697 | 0.00054377 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1053-4_0_3_load_15 | 22 | 0.0030428 | 0.00076261 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1053-4_0_3_load_16 | 23 | 0.0017856 | 0.00044751 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1053-4_0_3_load_17 | 24 | 0.0019103 | 0.00047876 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1053-4_0_3_load_18 | 25 | 0.0022999 | 0.00057642 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1053-4_0_3_load_19 | 26 | 0.0020205 | 0.00050639 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1053-4_0_3_load_20 | 27 | 0.0020402 | 0.00051132 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1053-4_0_3_load_93 | 28 | 0.0022447 | 0.00056257 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1053-4_0_3_load_21 | 29 | 0.0066221 | 0.0016597 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1053-4_0_3_load_94 | 30 | 0.0021297 | 0.00053376 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1053-4_0_3_load_22 | 31 | 0.0015877 | 0.00039791 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1053-4_0_3_load_44 | 32 | 0.0014091 | 0.00035314 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1053-4_0_3_load_43 | 33 | 0.0019722 | 0.00049427 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1053-4_0_3_load_23 | 34 | 0.002157 | 0.0005406 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1053-4_0_3_load_24 | 35 | 0.0039766 | 0.00099662 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1053-4_0_3_load_25 | 36 | 0.0046497 | 0.0011653 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1053-4_0_3_load_26 | 37 | 0.001021 | 0.00025588 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1053-4_0_3_load_27 | 38 | 0.004678 | 0.0011724 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1053-4_0_3_load_85 | 39 | 0.0033294 | 0.00083442 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1053-4_0_3_load_86 | 40 | 0.0045684 | 0.0011449 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1053-4_0_3_load_35 | 41 | 0.0018353 | 0.00045996 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1053-4_0_3_load_28 | 42 | 0.0012072 | 0.00030255 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1053-4_0_3_load_29 | 43 | 0.0015462 | 0.00038752 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1053-4_0_3_load_32 | 45 | 0.0019458 | 0.00048767 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1053-4_0_3_load_82 | 46 | 0.0070484 | 0.0017665 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1053-4_0_3_load_83 | 47 | 0.0036339 | 0.00091075 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1053-4_0_3_load_36 | 48 | 0.001376 | 0.00034486 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1053-4_0_3_load_41 | 53 | 0.00074016 | 0.0001855 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1053-4_0_3_load_42 | 54 | 0.00070356 | 0.00017633 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1053-4_0_3_load_48 | 55 | 0.0022537 | 0.00056483 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1053-4_0_3_load_45 | 56 | 0.0013712 | 0.00034365 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1053-4_0_3_load_116 | 58 | 0.00090981 | 0.00022802 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1053-4_0_3_load_73 | 59 | 0.00072067 | 0.00018062 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1053-4_0_3_load_75 | 60 | 0.0055285 | 0.0013856 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1053-4_0_3_load_130 | 62 | 0.0047349 | 0.0011867 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1053-4_0_3_load_117 | 63 | 0.00085235 | 0.00021362 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1053-4_0_3_load_114 | 64 | 0.0013355 | 0.00033471 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1053-4_0_3_load_74 | 65 | 0.00062689 | 0.00015711 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1053-4_0_3_load_127 | 67 | 0.0023273 | 0.00058326 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1053-4_0_3_load_128 | 68 | 0.0025532 | 0.00063989 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1053-4_0_3_load_122 | 69 | 0.00087117 | 0.00021834 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1053-4_0_3_load_129 | 70 | 0.0023575 | 0.00059084 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1053-4_0_3_load_49 | 71 | 0.0027096 | 0.00067909 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1053-4_0_3_load_51 | 73 | 0.0026219 | 0.0006571 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1053-4_0_3_load_52 | 74 | 0.003153 | 0.00079022 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1053-4_0_3_load_53 | 75 | 0.0056671 | 0.0014203 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1053-4_0_3_load_54 | 76 | 0.002036 | 0.00051027 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1053-4_0_3_load_55 | 77 | 0.0025863 | 0.0006482 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1053-4_0_3_load_112 | 78 | 0.0077423 | 0.0019404 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1053-4_0_3_load_111 | 80 | 0.0020431 | 0.00051205 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1053-4_0_3_load_78 | 81 | 0.0020786 | 0.00052094 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1053-4_0_3_load_56 | 83 | 0.0022641 | 0.00056745 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1053-4_0_3_load_57 | 84 | 0.0033883 | 0.00084918 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1053-4_0_3_load_59 | 86 | 0.002706 | 0.00067819 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1053-4_0_3_load_60 | 87 | 0.003051 | 0.00076465 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1053-4_0_3_load_61 | 88 | 0.0030487 | 0.00076409 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1053-4_0_3_load_109 | 89 | 0.002191 | 0.0005491 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1053-4_0_3_load_92 | 90 | 0.0024006 | 0.00060164 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1053-4_0_3_load_66 | 91 | 0.0025383 | 0.00063616 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1053-4_0_3_load_62 | 93 | 0.0028607 | 0.00071695 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1053-4_0_3_load_63 | 94 | 0.0029398 | 0.00073679 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1053-4_0_3_load_64 | 95 | 0.0032729 | 0.00082027 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1053-4_0_3_load_65 | 96 | 0.0023964 | 0.00060058 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1053-4_0_3_load_96 | 97 | 0.0026786 | 0.00067131 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1053-4_0_3_load_108 | 98 | 0.0036633 | 0.00091811 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1053-4_0_3_load_71 | 100 | 0.0010275 | 0.00025753 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1053-4_0_3_load_72 | 101 | 0.0025833 | 0.00064744 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1053-4_0_3_load_99 | 102 | 0.0028939 | 0.00072527 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1053-4_0_3_load_105 | 104 | 0.0040397 | 0.0010124 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1053-4_0_3_load_103 | 105 | 0.0025723 | 0.00064469 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1053-4_0_3_load_84 | 107 | 0.0063228 | 0.0015846 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1053-4_0_3_load_87 | 108 | 0.0030892 | 0.00077423 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1053-4_0_3_load_88 | 109 | 0.0015927 | 0.00039917 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1053-4_0_3_load_90 | 110 | 0.0030241 | 0.00075791 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1053-4_0_3_load_97 | 112 | 0.0020794 | 0.00052114 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1053-4_0_3_load_110 | 113 | 0.0030333 | 0.00076023 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1053-4_0_3_load_102 | 114 | 0.0020474 | 0.00051312 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1053-4_0_3_load_98 | 115 | 0.0020244 | 0.00050736 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1053-4_0_3_load_95 | 116 | 0.0024237 | 0.00060742 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1053-4_0_3_load_101 | 117 | 0.0010198 | 0.00025559 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1053-4_0_3_load_106 | 118 | 0.00093688 | 0.0002348 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1053-4_0_3_load_107 | 119 | 0.0037335 | 0.0009357 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1053-4_0_3_load_126 | 120 | 0.0042121 | 0.0010557 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1053-4_0_3_load_113 | 121 | 0.0012487 | 0.00031295 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1053-4_0_3_load_115 | 122 | 0.0011681 | 0.00029275 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1053-4_0_3_load_119 | 123 | 0.00075868 | 0.00019014 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1053-4_0_3_load_120 | 124 | 0.0024004 | 0.0006016 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1053-4_0_3_load_121 | 125 | 0.0022154 | 0.00055522 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1053-4_0_3_load_123 | 126 | 0.0023089 | 0.00057867 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 108 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1053-4_0_3_line_0 |  | 0 | 1 | 0.038176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1053-4_0_3_line_1 |  | 0 | 2 | 0.033115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1053-4_0_3_line_2 |  | 1 | 3 | 0.027078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1053-4_0_3_line_3 |  | 2 | 4 | 0.020352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1053-4_0_3_line_4 |  | 3 | 5 | 0.096153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1053-4_0_3_line_5 |  | 4 | 7 | 0.037651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1053-4_0_3_line_6 |  | 5 | 6 | 0.052338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1053-4_0_3_line_7 |  | 6 | 32 | 0.047569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1053-4_0_3_line_8 |  | 7 | 8 | 0.067216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1053-4_0_3_line_9 |  | 8 | 9 | 0.033814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1053-4_0_3_line_10 |  | 10 | 11 | 0.042171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1053-4_0_3_line_11 |  | 10 | 12 | 0.005918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1053-4_0_3_line_12 |  | 12 | 41 | 0.030229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1053-4_0_3_line_13 |  | 12 | 38 | 0.035694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1053-4_0_3_line_14 |  | 13 | 14 | 0.031429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1053-4_0_3_line_15 |  | 13 | 15 | 0.012779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1053-4_0_3_line_16 |  | 14 | 16 | 0.011066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1053-4_0_3_line_17 |  | 15 | 17 | 0.028264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1053-4_0_3_line_18 |  | 16 | 18 | 0.015271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1053-4_0_3_line_19 |  | 16 | 19 | 0.037817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1053-4_0_3_line_20 |  | 18 | 20 | 0.027902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1053-4_0_3_line_21 |  | 19 | 21 | 0.0030948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1053-4_0_3_line_22 |  | 21 | 91 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1053-4_0_3_line_23 |  | 21 | 86 | 0.020599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1053-4_0_3_line_24 |  | 22 | 23 | 0.0060716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1053-4_0_3_line_25 |  | 22 | 24 | 0.00096602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1053-4_0_3_line_26 |  | 23 | 25 | 0.013644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1053-4_0_3_line_27 |  | 24 | 26 | 0.0073021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1053-4_0_3_line_28 |  | 25 | 27 | 0.0082695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1053-4_0_3_line_29 |  | 26 | 28 | 0.011237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1053-4_0_3_line_30 |  | 27 | 29 | 0.0013202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1053-4_0_3_line_31 |  | 28 | 30 | 0.0041575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1053-4_0_3_line_32 |  | 29 | 31 | 0.015855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1053-4_0_3_line_33 |  | 30 | 116 | 0.0038805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1053-4_0_3_line_34 |  | 31 | 32 | 0.0066415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1053-4_0_3_line_35 |  | 32 | 33 | 0.0065257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1053-4_0_3_line_36 |  | 33 | 41 | 0.0095907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1053-4_0_3_line_37 |  | 34 | 35 | 0.0090001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1053-4_0_3_line_38 |  | 34 | 36 | 0.020582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1053-4_0_3_line_39 |  | 35 | 37 | 0.0017577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1053-4_0_3_line_40 |  | 36 | 38 | 0.0068223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1053-4_0_3_line_41 |  | 37 | 39 | 0.012516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_1053-4_0_3_line_42 |  | 39 | 40 | 0.012082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1053-4_0_3_line_43 |  | 40 | 89 | 0.0091394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_1053-4_0_3_line_44 |  | 42 | 43 | 0.035168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1053-4_0_3_line_45 |  | 42 | 44 | 0.0096285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1053-4_0_3_line_46 |  | 44 | 45 | 0.0060254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1053-4_0_3_line_47 |  | 45 | 46 | 0.019389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1053-4_0_3_line_48 |  | 46 | 47 | 0.0034139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1053-4_0_3_line_49 |  | 47 | 107 | 0.022261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1053-4_0_3_line_50 |  | 48 | 49 | 0.026609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1053-4_0_3_line_51 |  | 48 | 50 | 0.0045737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1053-4_0_3_line_52 |  | 49 | 51 | 0.027255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1053-4_0_3_line_53 |  | 49 | 52 | 0.026616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1053-4_0_3_line_54 |  | 50 | 53 | 0.002655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1053-4_0_3_line_55 |  | 50 | 54 | 0.0061586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1053-4_0_3_line_56 |  | 51 | 55 | 0.013964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1053-4_0_3_line_57 |  | 51 | 56 | 0.033836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1053-4_0_3_line_58 |  | 52 | 57 | 0.007968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1053-4_0_3_line_59 |  | 52 | 58 | 0.019965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1053-4_0_3_line_60 |  | 54 | 59 | 0.0085881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1053-4_0_3_line_61 |  | 55 | 60 | 0.015723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1053-4_0_3_line_62 |  | 56 | 61 | 0.01804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1053-4_0_3_line_63 |  | 57 | 62 | 0.025853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1053-4_0_3_line_64 |  | 57 | 63 | 0.033459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1053-4_0_3_line_65 |  | 58 | 64 | 0.0061199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1053-4_0_3_line_66 |  | 59 | 65 | 0.0091202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1053-4_0_3_line_67 |  | 61 | 66 | 0.028204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1053-4_0_3_line_68 |  | 63 | 118 | 0.0028359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1053-4_0_3_line_69 |  | 64 | 121 | 0.0070957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1053-4_0_3_line_70 |  | 66 | 67 | 0.013023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1053-4_0_3_line_71 |  | 66 | 68 | 0.005578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1053-4_0_3_line_72 |  | 67 | 69 | 0.0018093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1053-4_0_3_line_73 |  | 68 | 70 | 0.00066788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1053-4_0_3_line_74 |  | 69 | 124 | 0.006112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1053-4_0_3_line_75 |  | 71 | 72 | 0.00019214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1053-4_0_3_line_76 |  | 71 | 73 | 0.020909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1053-4_0_3_line_77 |  | 72 | 74 | 0.00726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1053-4_0_3_line_78 |  | 72 | 75 | 0.023342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_1053-4_0_3_line_79 |  | 73 | 76 | 0.007607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1053-4_0_3_line_80 |  | 73 | 77 | 0.019015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_1053-4_0_3_line_81 |  | 75 | 78 | 0.0001956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_1053-4_0_3_line_82 |  | 77 | 79 | 0.00032477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_1053-4_0_3_line_83 |  | 78 | 80 | 0.023254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_1053-4_0_3_line_84 |  | 79 | 81 | 0.007405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1053-4_0_3_line_85 |  | 79 | 82 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_1053-4_0_3_line_86 |  | 80 | 116 | 0.0033349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_1053-4_0_3_line_87 |  | 82 | 104 | 0.00629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1053-4_0_3_line_88 |  | 82 | 105 | 0.0027848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_1053-4_0_3_line_89 |  | 83 | 84 | 0.00031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1053-4_0_3_line_90 |  | 83 | 85 | 0.013663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1053-4_0_3_line_91 |  | 84 | 86 | 0.032701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1053-4_0_3_line_92 |  | 85 | 87 | 0.014622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_1053-4_0_3_line_93 |  | 85 | 88 | 0.014506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_1053-4_0_3_line_94 |  | 87 | 89 | 0.016157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_1053-4_0_3_line_95 |  | 88 | 90 | 0.0011503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_1053-4_0_3_line_96 |  | 90 | 92 | 0.023076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1053-4_0_3_line_97 |  | 91 | 95 | 0.0062337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1053-4_0_3_line_98 |  | 92 | 111 | 0.009156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1053-4_0_3_line_99 |  | 92 | 108 | 0.025721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_1053-4_0_3_line_100 |  | 93 | 94 | 0.0058978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1053-4_0_3_line_101 |  | 93 | 95 | 0.021039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1053-4_0_3_line_102 |  | 94 | 96 | 0.02351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1053-4_0_3_line_103 |  | 96 | 97 | 0.0026259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1053-4_0_3_line_104 |  | 97 | 98 | 0.024501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1053-4_0_3_line_105 |  | 98 | 107 | 0.0017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1053-4_0_3_line_106 |  | 99 | 100 | 0.0267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1053-4_0_3_line_107 |  | 99 | 101 | 0.02077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1053-4_0_3_line_108 |  | 100 | 102 | 0.012206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1053-4_0_3_line_109 |  | 102 | 103 | 0.02978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1053-4_0_3_line_110 |  | 103 | 117 | 0.009806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1053-4_0_3_line_111 |  | 103 | 114 | 0.0051928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1053-4_0_3_line_112 |  | 105 | 106 | 0.017153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_1053-4_0_3_line_113 |  | 106 | 118 | 0.013141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_1053-4_0_3_line_114 |  | 106 | 119 | 0.014932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1053-4_0_3_line_115 |  | 108 | 109 | 0.040201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1053-4_0_3_line_116 |  | 109 | 110 | 0.0050228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1053-4_0_3_line_117 |  | 110 | 112 | 0.024865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1053-4_0_3_line_118 |  | 111 | 113 | 0.008312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1053-4_0_3_line_119 |  | 111 | 114 | 0.019517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1053-4_0_3_line_120 |  | 112 | 115 | 0.0053805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1053-4_0_3_line_121 |  | 119 | 120 | 0.0065276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1053-4_0_3_line_122 |  | 121 | 122 | 0.0080352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1053-4_0_3_line_123 |  | 123 | 124 | 0.002513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1053-4_0_3_line_124 |  | 123 | 125 | 0.0058742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1053-4_0_3_line_125 |  | 125 | 126 | 0.0028352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1053-4_0_3_trafo_87 | 0.63 MVA 20/0.4 kV | 127 | 108 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2670746.3942 | 1216142.0426 | 2670737.1088 | 1216134.3586 | 2670731.4392 | 1216129.6772 | 2670716.0292 | 1216118.9582
1 | 2670746.3942 | 1216142.0426 | 2670771.9066 | 1216163.1553
2 | 2670716.0292 | 1216118.9582 | 2670695.5994 | 1216104.7475 | 2670693.8594 | 1216103.4142
3 | 2670786.8154 | 1216176.9854 | 2670781.2791 | 1216171.3173 | 2670772.0579 | 1216163.2806 | 2670771.9066 | 1216163.1553
4 | 2670597.7675 | 1216106.8452 | 2670693.8594 | 1216103.4142
5 | 2670786.8154 | 1216176.9854 | 2670811.7138 | 1216202.4763 | 2670812.9689 | 1216204.0563
6 | 2670597.7675 | 1216106.8452 | 2670595.2223 | 1216108.8941 | 2670590.1415 | 1216116.6722 | 2670586.9824 | 1216121.1932 | 2670585.2971 | 1216126.2876 | 2670584.4432 | 1216137.4735 | 2670581.7378 | 1216149.2045 | 2670580.7944 | 1216154.766
7 | 2670547.2167 | 1216188.4607 | 2670580.7944 | 1216154.766
8 | 2670812.9689 | 1216204.0563 | 2670760.6399 | 1216246.2422
9 | 2670760.6399 | 1216246.2422 | 2670776.1614 | 1216262.092 | 2670784.2695 | 1216270.4299
10 | 2670563.3393 | 1216233.24 | 2670563.6008 | 1216236.1672 | 2670563.9347 | 1216250.925 | 2670562.8694 | 1216265.8663 | 2670559.891 | 1216274.8782
11 | 2670558.6904 | 1216229.5605 | 2670563.3393 | 1216233.24
12 | 2670558.6904 | 1216229.5605 | 2670560.8079 | 1216224.5156 | 2670562.0362 | 1216218.2484 | 2670561.9652 | 1216212.0659 | 2670559.7529 | 1216204.6016 | 2670557.489 | 1216200.8255
13 | 2670558.6904 | 1216229.5605 | 2670555.4947 | 1216233.9699 | 2670550.254 | 1216239.2334 | 2670544.1657 | 1216242.3411 | 2670538.0113 | 1216243.9694 | 2670531.2118 | 1216244.2891 | 2670528.4383 | 1216243.8256
14 | 2670368.9426 | 1216231.4747 | 2670365.3944 | 1216230.3766 | 2670359.5779 | 1216226.55 | 2670353.2185 | 1216221.7497 | 2670348.7584 | 1216220.7186 | 2670342.7164 | 1216224.4052 | 2670341.9076 | 1216225.1924
15 | 2670334.1716 | 1216234.9333 | 2670334.9507 | 1216231.9629 | 2670341.9076 | 1216225.1924
16 | 2670368.9426 | 1216231.4747 | 2670364.9415 | 1216221.1543
17 | 2670334.1716 | 1216234.9333 | 2670318.1061 | 1216224.5372 | 2670311.25 | 1216218.5102
18 | 2670364.9415 | 1216221.1543 | 2670359.7846 | 1216209.0413 | 2670358.9596 | 1216207.1032
19 | 2670364.9415 | 1216221.1543 | 2670377.8696 | 1216221.3848 | 2670387.1528 | 1216224.8522 | 2670399.5636 | 1216233.2363
20 | 2670348.0318 | 1216181.4304 | 2670358.9596 | 1216207.1032
21 | 2670402.128 | 1216234.9687 | 2670399.5636 | 1216233.2363
22 | 2670402.128 | 1216234.9687 | 2670416.8537 | 1216244.9825
23 | 2670402.128 | 1216234.9687 | 2670408.3632 | 1216227.1485 | 2670414.4529 | 1216218.4757
24 | 2670512.0829 | 1216150.4053 | 2670516.2691 | 1216154.803
25 | 2670511.4169 | 1216149.7056 | 2670512.0829 | 1216150.4053
26 | 2670525.6761 | 1216164.685 | 2670516.2691 | 1216154.803
27 | 2670511.4169 | 1216149.7056 | 2670506.3822 | 1216144.4167
28 | 2670531.3777 | 1216170.6747 | 2670525.6761 | 1216164.685
29 | 2670498.6344 | 1216136.2774 | 2670506.3822 | 1216144.4167
30 | 2670531.3777 | 1216170.6747 | 2670531.8195 | 1216171.1388 | 2670532.2709 | 1216171.6466
31 | 2670495.7679 | 1216133.2662 | 2670498.6344 | 1216136.2774
32 | 2670532.2709 | 1216171.6466 | 2670542.8044 | 1216183.4968
33 | 2670495.7679 | 1216133.2662 | 2670495.7679 | 1216133.2662 | 2670493.1414 | 1216130.4096
34 | 2670547.2167 | 1216188.4607 | 2670542.8044 | 1216183.4968
35 | 2670547.2167 | 1216188.4607 | 2670551.5521 | 1216193.3381
36 | 2670557.489 | 1216200.8255 | 2670556.0001 | 1216198.3421 | 2670551.5521 | 1216193.3381
37 | 2670504.3478 | 1216231.6544 | 2670497.0289 | 1216226.4164
38 | 2670504.3478 | 1216231.6544 | 2670515.1651 | 1216239.3962 | 2670521.8093 | 1216242.3697
39 | 2670495.5996 | 1216225.3934 | 2670497.0289 | 1216226.4164
40 | 2670528.4383 | 1216243.8256 | 2670523.0504 | 1216242.9251 | 2670521.8093 | 1216242.3697
41 | 2670495.5996 | 1216225.3934 | 2670485.4217 | 1216218.1092
42 | 2670475.5963 | 1216211.0772 | 2670485.4217 | 1216218.1092
43 | 2670475.5963 | 1216211.0772 | 2670468.1643 | 1216205.7582
44 | 2670528.4791 | 1216332.5689 | 2670527.8803 | 1216351.262 | 2670538.3435 | 1216363.9754
45 | 2670529.0354 | 1216322.9577 | 2670528.5667 | 1216329.8343 | 2670528.4791 | 1216332.5689
46 | 2670529.0354 | 1216322.9577 | 2670524.1083 | 1216319.4894
47 | 2670508.2539 | 1216308.3288 | 2670524.1083 | 1216319.4894
48 | 2670508.2539 | 1216308.3288 | 2670505.4623 | 1216306.3636
49 | 2670505.4623 | 1216306.3636 | 2670487.2592 | 1216293.5497
50 | 2670363.6129 | 1215967.1443 | 2670357.8147 | 1215973.958 | 2670352.4227 | 1215969.5249 | 2670351.3944 | 1215971.0804 | 2670356.7872 | 1215975.4468 | 2670355.5045 | 1215976.8183
51 | 2670351.9188 | 1215974.9001 | 2670355.08 | 1215977.2722 | 2670355.5045 | 1215976.8183
52 | 2670363.6129 | 1215967.1443 | 2670341.6009 | 1215950.9854
53 | 2670384.3742 | 1215983.7554 | 2670383.8373 | 1215982.9263 | 2670377.1257 | 1215977.0656 | 2670363.6129 | 1215967.1443
54 | 2670351.9188 | 1215974.9001 | 2670349.7964 | 1215973.2963
55 | 2670351.9188 | 1215974.9001 | 2670351.072 | 1215975.8796 | 2670348.6083 | 1215978.7412 | 2670347.9 | 1215979.5667
56 | 2670341.6009 | 1215950.9854 | 2670346.0624 | 1215947.4136 | 2670349.7265 | 1215945.778 | 2670353.8244 | 1215944.7039
57 | 2670341.6009 | 1215950.9854 | 2670335.473 | 1215946.4881 | 2670314.2967 | 1215931.0012
58 | 2670384.3742 | 1215983.7554 | 2670388.0736 | 1215989.4138 | 2670388.2341 | 1215990.6164
59 | 2670384.3742 | 1215983.7554 | 2670380.4329 | 1215992.1475 | 2670378.485 | 1215995.7046 | 2670377.1785 | 1215997.0233 | 2670374.3839 | 1216000.9039
60 | 2670347.9 | 1215979.5667 | 2670349.7654 | 1215981.0675 | 2670349.0652 | 1215981.8486 | 2670346.2873 | 1215984.9622 | 2670345.6409 | 1215985.6884
61 | 2670353.8244 | 1215944.7039 | 2670361.944 | 1215942.5757 | 2670364.597 | 1215941.0394 | 2670366.7589 | 1215938.6522 | 2670367.2771 | 1215937.7472
62 | 2670299.9595 | 1215920.0636 | 2670304.5691 | 1215923.8871 | 2670314.2967 | 1215931.0012
63 | 2670388.2341 | 1215990.6164 | 2670393.9679 | 1215990.5396 | 2670399.4507 | 1215991.7829 | 2670413.3164 | 1215996.2495
64 | 2670388.2341 | 1215990.6164 | 2670388.8355 | 1215994.9818 | 2670390.1351 | 1216001.3123 | 2670390.8463 | 1216004.7451 | 2670394.5585 | 1216015.1066 | 2670398.3137 | 1216022.2583
65 | 2670371.0132 | 1216005.9896 | 2670371.0132 | 1216005.9896 | 2670373.7223 | 1216002.2747 | 2670374.3839 | 1216000.9039 | 2670374.3839 | 1216000.9039
66 | 2670343.0638 | 1215992.3734 | 2670344.3417 | 1215990.8986 | 2670346.9437 | 1215987.8941 | 2670347.4441 | 1215987.3107 | 2670345.6409 | 1215985.6884
67 | 2670295.58 | 1215932.7756 | 2670296.8979 | 1215931.1345 | 2670293.3472 | 1215928.302 | 2670294.4801 | 1215926.8922 | 2670298.798 | 1215930.3342 | 2670299.9927 | 1215928.8362 | 2670295.6823 | 1215925.3944 | 2670299.9595 | 1215920.0636
68 | 2670399.6321 | 1216024.769 | 2670398.3137 | 1216022.2583
69 | 2670367.6159 | 1216012.146 | 2670368.1637 | 1216011.3037 | 2670370.5452 | 1216007.6851 | 2670371.0132 | 1216005.9896
70 | 2670295.58 | 1215932.7756 | 2670295.0715 | 1215933.4033 | 2670292.2431 | 1215936.9278 | 2670291.8578 | 1215937.4124 | 2670292.5197 | 1215937.9428 | 2670292.0651 | 1215938.5045 | 2670288.9592 | 1215942.3814 | 2670288.6202 | 1215942.7999
71 | 2670295.58 | 1215932.7756 | 2670293.1886 | 1215930.8017 | 2670292.2654 | 1215930.5351 | 2670291.5025 | 1215930.8374 | 2670291.0239 | 1215931.3423
72 | 2670290.0344 | 1215943.9284 | 2670288.6202 | 1215942.7999 | 2670288.6202 | 1215942.7999
73 | 2670290.5644 | 1215931.827 | 2670291.0239 | 1215931.3423
74 | 2670290.0344 | 1215943.9284 | 2670290.0344 | 1215943.9284 | 2670289.6645 | 1215944.391 | 2670286.5432 | 1215948.29 | 2670286.2119 | 1215948.6975 | 2670286.2119 | 1215948.6975
75 | 2670459.0594 | 1216093.3909 | 2670459.1911 | 1216093.5309
76 | 2670444.7332 | 1216078.1614 | 2670459.0594 | 1216093.3909
77 | 2670459.1911 | 1216093.5309 | 2670453.953 | 1216098.5722
78 | 2670459.1911 | 1216093.5309 | 2670460.8559 | 1216095.2961 | 2670475.0122 | 1216110.6924
79 | 2670444.7332 | 1216078.1614 | 2670439.1592 | 1216083.3544
80 | 2670444.7332 | 1216078.1614 | 2670431.7052 | 1216064.3103
81 | 2670475.0122 | 1216110.6924 | 2670475.1446 | 1216110.8364
82 | 2670431.4826 | 1216064.0737 | 2670431.7052 | 1216064.3103
83 | 2670490.8842 | 1216127.9547 | 2670475.1446 | 1216110.8364
84 | 2670431.4826 | 1216064.0737 | 2670426.0321 | 1216069.1014
85 | 2670431.4826 | 1216064.0737 | 2670427.7931 | 1216060.161 | 2670419.6859 | 1216050.9705
86 | 2670493.1414 | 1216130.4096 | 2670490.8842 | 1216127.9547
87 | 2670419.6859 | 1216050.9705 | 2670415.0867 | 1216055.2745
88 | 2670419.6859 | 1216050.9705 | 2670417.8443 | 1216048.8815
89 | 2670434.6903 | 1216199.8786 | 2670434.8709 | 1216199.6216
90 | 2670442.7233 | 1216188.4409 | 2670436.6221 | 1216197.1299 | 2670434.8709 | 1216199.6216
91 | 2670414.4529 | 1216218.4757 | 2670420.5654 | 1216209.7705 | 2670425.3776 | 1216213.1294 | 2670434.6903 | 1216199.8786
92 | 2670442.7233 | 1216188.4409 | 2670454.8858 | 1216196.5574
93 | 2670442.7233 | 1216188.4409 | 2670430.6617 | 1216180.3827
94 | 2670468.1643 | 1216205.7582 | 2670461.1429 | 1216200.733 | 2670454.8858 | 1216196.5574
95 | 2670430.6617 | 1216180.3827 | 2670429.7052 | 1216179.7437
96 | 2670410.5175 | 1216166.9246 | 2670429.7052 | 1216179.7437
97 | 2670416.8537 | 1216244.9825 | 2670422.0085 | 1216248.4879
98 | 2670402.9091 | 1216161.7982 | 2670410.5175 | 1216166.9246
99 | 2670410.5175 | 1216166.9246 | 2670414.8353 | 1216159.4375 | 2670416.8522 | 1216153.2463 | 2670415.1087 | 1216144.0088 | 2670414.587 | 1216142.9664
100 | 2670439.4063 | 1216260.3188 | 2670444.2833 | 1216263.6352
101 | 2670439.4063 | 1216260.3188 | 2670422.0085 | 1216248.4879
102 | 2670444.2833 | 1216263.6352 | 2670458.4175 | 1216273.2468 | 2670463.665 | 1216276.9407
103 | 2670465.8122 | 1216278.4523 | 2670463.665 | 1216276.9407
104 | 2670485.8469 | 1216292.5555 | 2670465.8122 | 1216278.4523
105 | 2670485.8469 | 1216292.5555 | 2670487.2592 | 1216293.5497
106 | 2670330.1265 | 1216106.1039 | 2670335.6422 | 1216105.8466 | 2670342.1467 | 1216109.2922 | 2670351.9338 | 1216119.0456
107 | 2670330.1265 | 1216106.1039 | 2670322.3316 | 1216089.1012 | 2670321.279 | 1216087.3235
108 | 2670360.5797 | 1216127.6618 | 2670351.9338 | 1216119.0456
109 | 2670383.0056 | 1216147.1873 | 2670369.0289 | 1216136.0819 | 2670360.5797 | 1216127.6618
110 | 2670383.0056 | 1216147.1873 | 2670390.3417 | 1216140.6586
111 | 2670383.0056 | 1216147.1873 | 2670387.0725 | 1216150.4162
112 | 2670406.9278 | 1216035.6768 | 2670409.9003 | 1216039.8701 | 2670417.8443 | 1216048.8815
113 | 2670406.9278 | 1216035.6768 | 2670400.8558 | 1216027.0997 | 2670399.6321 | 1216024.769
114 | 2670406.9278 | 1216035.6768 | 2670402.4496 | 1216037.4473 | 2670400.1545 | 1216036.9754 | 2670396.207 | 1216033.6823 | 2670394.2615 | 1216031.9081
115 | 2670414.587 | 1216142.9664 | 2670410.5689 | 1216134.9383 | 2670398.1634 | 1216120.0268 | 2670390.2703 | 1216111.2197
116 | 2670386.918 | 1216107.4792 | 2670390.2703 | 1216111.2197
117 | 2670370.3231 | 1216088.9626 | 2670386.918 | 1216107.4792
118 | 2670402.9091 | 1216161.7982 | 2670398.6485 | 1216168.9413
119 | 2670402.9091 | 1216161.7982 | 2670393.0557 | 1216155.1665 | 2670387.0725 | 1216150.4162
120 | 2670366.7321 | 1216084.9558 | 2670370.3231 | 1216088.9626
121 | 2670389.4384 | 1216027.5096 | 2670394.2615 | 1216031.9081
122 | 2670362.4915 | 1216017.096 | 2670363.6403 | 1216017.5543 | 2670364.3434 | 1216017.1735 | 2670364.8386 | 1216016.39 | 2670367.1661 | 1216012.8374 | 2670367.6159 | 1216012.146
123 | 2670288.1753 | 1215950.2661 | 2670286.2119 | 1215948.6975
124 | 2670288.1753 | 1215950.2661 | 2670287.8361 | 1215950.6957 | 2670284.7073 | 1215954.5835 | 2670284.4992 | 1215954.8478
125 | 2670284.4278 | 1215957.6821 | 2670284.4992 | 1215954.8478

## bus_geodata
| x | y | coords
0 | 2670746.3942 | 1216142.0426
1 | 2670716.0292 | 1216118.9582
2 | 2670771.9066 | 1216163.1553
3 | 2670693.8594 | 1216103.4142
4 | 2670786.8154 | 1216176.9854
5 | 2670597.7675 | 1216106.8452
6 | 2670580.7944 | 1216154.766
7 | 2670812.9689 | 1216204.0563
8 | 2670760.6399 | 1216246.2422
9 | 2670784.2695 | 1216270.4299
10 | 2670563.3393 | 1216233.24
11 | 2670559.891 | 1216274.8782
12 | 2670558.6904 | 1216229.5605
13 | 2670341.9076 | 1216225.1924
14 | 2670368.9426 | 1216231.4747
15 | 2670334.1716 | 1216234.9333
16 | 2670364.9415 | 1216221.1543
17 | 2670311.25 | 1216218.5102
18 | 2670358.9596 | 1216207.1032
19 | 2670399.5636 | 1216233.2363
20 | 2670348.0318 | 1216181.4304
21 | 2670402.128 | 1216234.9687
22 | 2670512.0829 | 1216150.4053
23 | 2670516.2691 | 1216154.803
24 | 2670511.4169 | 1216149.7056
25 | 2670525.6761 | 1216164.685
26 | 2670506.3822 | 1216144.4167
27 | 2670531.3777 | 1216170.6747
28 | 2670498.6344 | 1216136.2774
29 | 2670532.2709 | 1216171.6466
30 | 2670495.7679 | 1216133.2662
31 | 2670542.8044 | 1216183.4968
32 | 2670547.2167 | 1216188.4607
33 | 2670551.5521 | 1216193.3381
34 | 2670504.3478 | 1216231.6544
35 | 2670497.0289 | 1216226.4164
36 | 2670521.8093 | 1216242.3697
37 | 2670495.5996 | 1216225.3934
38 | 2670528.4383 | 1216243.8256
39 | 2670485.4217 | 1216218.1092
40 | 2670475.5963 | 1216211.0772
41 | 2670557.489 | 1216200.8255
42 | 2670528.4791 | 1216332.5689
43 | 2670538.3435 | 1216363.9754
44 | 2670529.0354 | 1216322.9577
45 | 2670524.1083 | 1216319.4894
46 | 2670508.2539 | 1216308.3288
47 | 2670505.4623 | 1216306.3636
48 | 2670355.5045 | 1215976.8183
49 | 2670363.6129 | 1215967.1443
50 | 2670351.9188 | 1215974.9001
51 | 2670341.6009 | 1215950.9854
52 | 2670384.3742 | 1215983.7554
53 | 2670349.7964 | 1215973.2963
54 | 2670347.9 | 1215979.5667
55 | 2670353.8244 | 1215944.7039
56 | 2670314.2967 | 1215931.0012
57 | 2670388.2341 | 1215990.6164
58 | 2670374.3839 | 1216000.9039
59 | 2670345.6409 | 1215985.6884
60 | 2670367.2771 | 1215937.7472
61 | 2670299.9595 | 1215920.0636
62 | 2670413.3164 | 1215996.2495
63 | 2670398.3137 | 1216022.2583
64 | 2670371.0132 | 1216005.9896
65 | 2670343.0638 | 1215992.3734
66 | 2670295.58 | 1215932.7756
67 | 2670288.6202 | 1215942.7999
68 | 2670291.0239 | 1215931.3423
69 | 2670290.0344 | 1215943.9284
70 | 2670290.5644 | 1215931.827
71 | 2670459.0594 | 1216093.3909
72 | 2670459.1911 | 1216093.5309
73 | 2670444.7332 | 1216078.1614
74 | 2670453.953 | 1216098.5722
75 | 2670475.0122 | 1216110.6924
76 | 2670439.1592 | 1216083.3544
77 | 2670431.7052 | 1216064.3103
78 | 2670475.1446 | 1216110.8364
79 | 2670431.4826 | 1216064.0737
80 | 2670490.8842 | 1216127.9547
81 | 2670426.0321 | 1216069.1014
82 | 2670419.6859 | 1216050.9705
83 | 2670434.8709 | 1216199.6216
84 | 2670434.6903 | 1216199.8786
85 | 2670442.7233 | 1216188.4409
86 | 2670414.4529 | 1216218.4757
87 | 2670454.8858 | 1216196.5574
88 | 2670430.6617 | 1216180.3827
89 | 2670468.1643 | 1216205.7582
90 | 2670429.7052 | 1216179.7437
91 | 2670416.8537 | 1216244.9825
92 | 2670410.5175 | 1216166.9246
93 | 2670439.4063 | 1216260.3188
94 | 2670444.2833 | 1216263.6352
95 | 2670422.0085 | 1216248.4879
96 | 2670463.665 | 1216276.9407
97 | 2670465.8122 | 1216278.4523
98 | 2670485.8469 | 1216292.5555
99 | 2670330.1265 | 1216106.1039
100 | 2670351.9338 | 1216119.0456
101 | 2670321.279 | 1216087.3235
102 | 2670360.5797 | 1216127.6618
103 | 2670383.0056 | 1216147.1873
104 | 2670415.0867 | 1216055.2745
105 | 2670417.8443 | 1216048.8815
106 | 2670406.9278 | 1216035.6768
107 | 2670487.2592 | 1216293.5497
108 | 2670414.587 | 1216142.9664
109 | 2670390.2703 | 1216111.2197
110 | 2670386.918 | 1216107.4792
111 | 2670402.9091 | 1216161.7982
112 | 2670370.3231 | 1216088.9626
113 | 2670398.6485 | 1216168.9413
114 | 2670387.0725 | 1216150.4162
115 | 2670366.7321 | 1216084.9558
116 | 2670493.1414 | 1216130.4096
117 | 2670390.3417 | 1216140.6586
118 | 2670399.6321 | 1216024.769
119 | 2670394.2615 | 1216031.9081
120 | 2670389.4384 | 1216027.5096
121 | 2670367.6159 | 1216012.146
122 | 2670362.4915 | 1216017.096
123 | 2670288.1753 | 1215950.2661
124 | 2670286.2119 | 1215948.6975
125 | 2670284.4992 | 1215954.8478
126 | 2670284.4278 | 1215957.6821
127 | 2670410.5175 | 1216166.9246

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97793 | -0.42381 | 0.00084011 | 0.00021055
1 | 0.9781 | -0.42045 | 0.0041143 | 0.0010311
2 | 0.97781 | -0.42622 | 0.001011 | 0.00025338
3 | 0.97833 | -0.41604 | 0.00055319 | 0.00013864
4 | 0.97775 | -0.42732 | 0.00072795 | 0.00018244
5 | 0.97917 | -0.39943 | 0 | 0
6 | 0.97963 | -0.3904 | 0.0035175 | 0.00088156
7 | 0.97767 | -0.42886 | 0.00064607 | 0.00016192
8 | 0.97758 | -0.43081 | 0 | 0
9 | 0.97753 | -0.4318 | 0.0015935 | 0.00039936
10 | 0.98299 | -0.32507 | 0 | 0
11 | 0.9827 | -0.33078 | 0.0075007 | 0.0018798
12 | 0.98303 | -0.32427 | 0 | 0
13 | 0.98902 | -0.20957 | 0.0011477 | 0.00028764
14 | 0.9891 | -0.20808 | 0 | 0
15 | 0.98901 | -0.20991 | 0 | 0
16 | 0.98913 | -0.20755 | 0 | 0
17 | 0.98897 | -0.21067 | 0.0015071 | 0.00037772
18 | 0.98905 | -0.20905 | 0.0033293 | 0.0008344
19 | 0.98941 | -0.20206 | 0.0022441 | 0.00056241
20 | 0.989 | -0.21013 | 0.0021697 | 0.00054377
21 | 0.98944 | -0.20149 | 0 | 0
22 | 0.97764 | -0.42924 | 0.0030428 | 0.00076261
23 | 0.97792 | -0.42375 | 0.0017856 | 0.00044751
24 | 0.9776 | -0.43009 | 0.0019103 | 0.00047876
25 | 0.97856 | -0.41119 | 0.0022999 | 0.00057642
26 | 0.97728 | -0.43638 | 0.0020205 | 0.00050639
27 | 0.97896 | -0.40341 | 0.0020402 | 0.00051132
28 | 0.97679 | -0.44585 | 0.0022447 | 0.00056257
29 | 0.97903 | -0.40215 | 0.0066221 | 0.0016597
30 | 0.97662 | -0.44927 | 0.0021297 | 0.00053376
31 | 0.97985 | -0.38601 | 0.0015877 | 0.00039791
32 | 0.9802 | -0.37916 | 0.0014091 | 0.00035314
33 | 0.98059 | -0.37158 | 0.0019722 | 0.00049427
34 | 0.98722 | -0.24329 | 0.002157 | 0.0005406
35 | 0.98785 | -0.23115 | 0.0039766 | 0.00099662
36 | 0.9858 | -0.27069 | 0.0046497 | 0.0011653
37 | 0.98798 | -0.22872 | 0.001021 | 0.00025588
38 | 0.98534 | -0.27951 | 0.004678 | 0.0011724
39 | 0.98889 | -0.21132 | 0.0033294 | 0.00083442
40 | 0.98978 | -0.1942 | 0.0045684 | 0.0011449
41 | 0.98117 | -0.36029 | 0.0018353 | 0.00045996
42 | 0.98584 | -0.27154 | 0.0012072 | 0.00030255
43 | 0.98579 | -0.27251 | 0.0015462 | 0.00038752
44 | 0.98586 | -0.27106 | 0 | 0
45 | 0.98588 | -0.27076 | 0.0019458 | 0.00048767
46 | 0.98596 | -0.26913 | 0.0070484 | 0.0017665
47 | 0.986 | -0.26841 | 0.0036339 | 0.00091075
48 | 0.97109 | -0.55822 | 0.001376 | 0.00034486
49 | 0.97119 | -0.55617 | 0 | 0
50 | 0.97107 | -0.55846 | 0 | 0
51 | 0.97087 | -0.56246 | 0 | 0
52 | 0.97155 | -0.54901 | 0 | 0
53 | 0.97107 | -0.55849 | 0.00074016 | 0.0001855
54 | 0.97106 | -0.55869 | 0.00070356 | 0.00017633
55 | 0.97077 | -0.56447 | 0.0022537 | 0.00056483
56 | 0.9706 | -0.56783 | 0.0013712 | 0.00034365
57 | 0.97168 | -0.54653 | 0 | 0
58 | 0.97146 | -0.55073 | 0.00090981 | 0.00022802
59 | 0.97105 | -0.5589 | 0.00072067 | 0.00018062
60 | 0.97069 | -0.56607 | 0.0055285 | 0.0013856
61 | 0.97047 | -0.57047 | 0 | 0
62 | 0.97156 | -0.54879 | 0.0047349 | 0.0011867
63 | 0.97228 | -0.53463 | 0.00085235 | 0.00021362
64 | 0.97144 | -0.55115 | 0.0013355 | 0.00033471
65 | 0.97105 | -0.55901 | 0.00062689 | 0.00015711
66 | 0.97026 | -0.57459 | 0 | 0
67 | 0.97013 | -0.57721 | 0.0023273 | 0.00058326
68 | 0.97023 | -0.5751 | 0.0025532 | 0.00063989
69 | 0.97011 | -0.5775 | 0.00087117 | 0.00021834
70 | 0.97023 | -0.57512 | 0.0023575 | 0.00059084
71 | 0.97464 | -0.488 | 0.0027096 | 0.00067909
72 | 0.97465 | -0.48789 | 0 | 0
73 | 0.97402 | -0.50033 | 0.0026219 | 0.0006571
74 | 0.97463 | -0.48831 | 0.003153 | 0.00079022
75 | 0.97541 | -0.47289 | 0.0056671 | 0.0014203
76 | 0.974 | -0.50061 | 0.002036 | 0.00051027
77 | 0.97349 | -0.51073 | 0.0025863 | 0.0006482
78 | 0.97542 | -0.47276 | 0.0077423 | 0.0019404
79 | 0.97348 | -0.5109 | 0 | 0
80 | 0.97633 | -0.45499 | 0.0020431 | 0.00051205
81 | 0.97347 | -0.51119 | 0.0020786 | 0.00052094
82 | 0.97303 | -0.5198 | 0 | 0
83 | 0.99211 | -0.14994 | 0.0022641 | 0.00056745
84 | 0.99209 | -0.15026 | 0.0033883 | 0.00084918
85 | 0.99287 | -0.13523 | 0 | 0
86 | 0.99043 | -0.18227 | 0.002706 | 0.00067819
87 | 0.99172 | -0.1571 | 0.003051 | 0.00076465
88 | 0.99441 | -0.10581 | 0.0030487 | 0.00076409
89 | 0.99048 | -0.18089 | 0.002191 | 0.0005491
90 | 0.99454 | -0.10345 | 0.0024006 | 0.00060164
91 | 0.98875 | -0.21483 | 0.0025383 | 0.00063616
92 | 0.99705 | -0.055729 | 0 | 0
93 | 0.98782 | -0.23284 | 0.0028607 | 0.00071695
94 | 0.98764 | -0.23635 | 0.0029398 | 0.00073679
95 | 0.98853 | -0.21922 | 0.0032729 | 0.00082027
96 | 0.98699 | -0.24915 | 0.0023964 | 0.00060058
97 | 0.98692 | -0.25047 | 0.0026786 | 0.00067131
98 | 0.98635 | -0.2616 | 0.0036633 | 0.00091811
99 | 0.99646 | -0.067103 | 0 | 0
100 | 0.99652 | -0.065892 | 0.0010275 | 0.00025753
101 | 0.99641 | -0.068045 | 0.0025833 | 0.00064744
102 | 0.99656 | -0.065118 | 0.0028939 | 0.00072527
103 | 0.99674 | -0.061718 | 0 | 0
104 | 0.97301 | -0.52026 | 0.0040397 | 0.0010124
105 | 0.97296 | -0.5211 | 0.0025723 | 0.00064469
106 | 0.97258 | -0.52872 | 0 | 0
107 | 0.98631 | -0.26227 | 0.0063228 | 0.0015846
108 | 1 | 0 | -0.26253 | -0.06704
109 | 0.99968 | -0.0061136 | 0.0015927 | 0.00039917
110 | 0.99965 | -0.0067381 | 0.0030241 | 0.00075791
111 | 0.99695 | -0.057754 | 0 | 0
112 | 0.99956 | -0.0085183 | 0.0020794 | 0.00052114
113 | 0.99692 | -0.058196 | 0.0030333 | 0.00076023
114 | 0.99678 | -0.061032 | 0.0020474 | 0.00051312
115 | 0.99955 | -0.0087083 | 0.0020244 | 0.00050736
116 | 0.97646 | -0.45239 | 0.0024237 | 0.00060742
117 | 0.99673 | -0.061893 | 0.0010198 | 0.00025559
118 | 0.97233 | -0.53361 | 0.00093688 | 0.0002348
119 | 0.97247 | -0.53091 | 0.0037335 | 0.0009357
120 | 0.97244 | -0.53142 | 0.0042121 | 0.0010557
121 | 0.97143 | -0.55147 | 0.0012487 | 0.00031295
122 | 0.97142 | -0.55164 | 0.0011681 | 0.00029275
123 | 0.97006 | -0.57861 | 0.00075868 | 0.00019014
124 | 0.97007 | -0.57837 | 0.0024004 | 0.0006016
125 | 0.97003 | -0.57911 | 0.0022154 | 0.00055522
126 | 0.97003 | -0.57923 | 0.0023089 | 0.00057867
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0048196 | -0.0012059 | 0.0048204 | 0.0012059 | 7.6975e-07 | 1.3572e-08 | 0.0073327 | 0.0073326 | 0.0073327 | 0.97793 | -0.42381 | 0.9781 | -0.42045 | 2.0145
1 | 0.0039795 | 0.00099533 | -0.003979 | -0.00099545 | 4.5522e-07 | -1.241e-07 | 0.0060544 | 0.0060546 | 0.0060546 | 0.97793 | -0.42381 | 0.97781 | -0.42622 | 1.6633
2 | -0.0089346 | -0.002237 | 0.0089365 | 0.0022379 | 1.8758e-06 | 8.606e-07 | 0.013592 | 0.013592 | 0.013592 | 0.9781 | -0.42045 | 0.97833 | -0.41604 | 3.734
3 | 0.002968 | 0.00074208 | -0.0029679 | -0.00074223 | 1.5565e-07 | -1.5565e-07 | 0.0045161 | 0.0045162 | 0.0045162 | 0.97781 | -0.42622 | 0.97775 | -0.42732 | 1.2407
4 | -0.0094897 | -0.0023765 | 0.0094972 | 0.0023801 | 7.5109e-06 | 3.5986e-06 | 0.014433 | 0.014433 | 0.014433 | 0.97833 | -0.41604 | 0.97917 | -0.39943 | 3.9651
5 | 0.0022399 | 0.00055979 | -0.0022398 | -0.00056016 | 1.6402e-07 | -3.6721e-07 | 0.0034083 | 0.0034085 | 0.0034085 | 0.97775 | -0.42732 | 0.97767 | -0.42886 | 0.9364
6 | -0.0094972 | -0.0023801 | 0.0095013 | 0.0023821 | 4.0881e-06 | 1.9578e-06 | 0.014433 | 0.014432 | 0.014433 | 0.97917 | -0.39943 | 0.97963 | -0.3904 | 3.965
7 | -0.013019 | -0.0032636 | 0.013026 | 0.0032675 | 6.9757e-06 | 3.8652e-06 | 0.019775 | 0.019775 | 0.019775 | 0.97963 | -0.3904 | 0.9802 | -0.37916 | 5.4327
8 | 0.0015937 | 0.00039824 | -0.0015935 | -0.00039898 | 1.4826e-07 | -7.4791e-07 | 0.0024252 | 0.0024255 | 0.0024255 | 0.97767 | -0.42886 | 0.97758 | -0.43081 | 0.66634
9 | 0.0015935 | 0.00039898 | -0.0015935 | -0.00039936 | 7.4602e-08 | -3.7618e-07 | 0.0024255 | 0.0024256 | 0.0024256 | 0.97758 | -0.43081 | 0.97753 | -0.4318 | 0.66638
10 | 0.0075027 | 0.0018806 | -0.0075007 | -0.0018798 | 2.0399e-06 | 7.7113e-07 | 0.011357 | 0.011358 | 0.011358 | 0.98299 | -0.32507 | 0.9827 | -0.33078 | 3.1202
11 | -0.0075027 | -0.0018806 | 0.007503 | 0.0018807 | 2.8627e-07 | 1.0819e-07 | 0.011357 | 0.011357 | 0.011357 | 0.98299 | -0.32507 | 0.98303 | -0.32427 | 3.1202
12 | 0.13287 | 0.033686 | -0.13264 | -0.03354 | 0.00022958 | 0.00014616 | 0.20126 | 0.20126 | 0.20126 | 0.98303 | -0.32427 | 0.98117 | -0.36029 | 27.6454
13 | -0.14037 | -0.035567 | 0.14067 | 0.035759 | 0.00030254 | 0.00019272 | 0.21262 | 0.21262 | 0.21262 | 0.98303 | -0.32427 | 0.98534 | -0.27951 | 29.2055
14 | -0.0026549 | -0.00066489 | 0.0026551 | 0.0006646 | 1.8802e-07 | -2.8302e-07 | 0.0039942 | 0.0039941 | 0.0039942 | 0.98902 | -0.20957 | 0.9891 | -0.20808 | 1.0973
15 | 0.0015072 | 0.00037725 | -0.0015072 | -0.0003774 | 2.4638e-08 | -1.4821e-07 | 0.0022675 | 0.0022675 | 0.0022675 | 0.98902 | -0.20957 | 0.98901 | -0.20991 | 0.62295
16 | -0.0026551 | -0.0006646 | 0.0026552 | 0.0006645 | 6.6198e-08 | -9.9668e-08 | 0.0039941 | 0.003994 | 0.0039941 | 0.9891 | -0.20808 | 0.98913 | -0.20755 | 1.0973
17 | 0.0015072 | 0.0003774 | -0.0015071 | -0.00037772 | 5.45e-08 | -3.2781e-07 | 0.0022675 | 0.0022677 | 0.0022677 | 0.98901 | -0.20991 | 0.98897 | -0.21067 | 0.62298
18 | 0.0054995 | 0.0013779 | -0.0054991 | -0.0013779 | 3.9197e-07 | 5.4859e-08 | 0.0082731 | 0.0082732 | 0.0082732 | 0.98913 | -0.20755 | 0.98905 | -0.20905 | 2.2729
19 | -0.0081546 | -0.0020424 | 0.0081568 | 0.0020433 | 2.134e-06 | 8.8024e-07 | 0.012267 | 0.012267 | 0.012267 | 0.98913 | -0.20755 | 0.98941 | -0.20206 | 3.3701
20 | 0.0021698 | 0.00054348 | -0.0021697 | -0.00054377 | 1.1149e-07 | -2.867e-07 | 0.0032643 | 0.0032644 | 0.0032644 | 0.98905 | -0.20905 | 0.989 | -0.21013 | 0.89681
21 | -0.010401 | -0.0026057 | 0.010401 | 0.0026059 | 2.8395e-07 | 1.4198e-07 | 0.015642 | 0.015642 | 0.015642 | 0.98941 | -0.20206 | 0.98944 | -0.20149 | 4.2972
22 | 0.042158 | 0.010604 | -0.042132 | -0.010587 | 2.6856e-05 | 1.6959e-05 | 0.063416 | 0.063416 | 0.063416 | 0.98944 | -0.20149 | 0.98875 | -0.21483 | 17.4219
23 | -0.05256 | -0.01321 | 0.052608 | 0.01324 | 4.8279e-05 | 3.0634e-05 | 0.079057 | 0.079057 | 0.079057 | 0.98944 | -0.20149 | 0.99043 | -0.18227 | 21.7191
24 | -0.099684 | -0.025134 | 0.09971 | 0.025151 | 2.6225e-05 | 1.6632e-05 | 0.15178 | 0.15178 | 0.15178 | 0.97764 | -0.42924 | 0.97792 | -0.42375 | 20.8487
25 | 0.096641 | 0.024371 | -0.096637 | -0.024369 | 3.9218e-06 | 2.4857e-06 | 0.14715 | 0.14715 | 0.14715 | 0.97764 | -0.42924 | 0.9776 | -0.43009 | 20.2125
26 | -0.1015 | -0.025598 | 0.10156 | 0.025637 | 6.106e-05 | 3.8736e-05 | 0.1545 | 0.15449 | 0.1545 | 0.97792 | -0.42375 | 0.97856 | -0.41119 | 21.2219
27 | 0.094727 | 0.02389 | -0.094698 | -0.023872 | 2.8485e-05 | 1.8047e-05 | 0.14424 | 0.14424 | 0.14424 | 0.9776 | -0.43009 | 0.97728 | -0.43638 | 19.8131
28 | -0.10386 | -0.026213 | 0.1039 | 0.026238 | 3.8704e-05 | 2.4562e-05 | 0.15799 | 0.15799 | 0.15799 | 0.97856 | -0.41119 | 0.97896 | -0.40341 | 21.7022
29 | 0.092678 | 0.023366 | -0.092636 | -0.023339 | 4.1986e-05 | 2.6589e-05 | 0.14116 | 0.14116 | 0.14116 | 0.97728 | -0.43638 | 0.97679 | -0.44585 | 19.3905
30 | -0.10594 | -0.026749 | 0.10594 | 0.026753 | 6.4237e-06 | 4.078e-06 | 0.16109 | 0.16109 | 0.16109 | 0.97896 | -0.40341 | 0.97903 | -0.40215 | 22.1282
31 | 0.090391 | 0.022777 | -0.090376 | -0.022767 | 1.479e-05 | 9.3616e-06 | 0.13774 | 0.13774 | 0.13774 | 0.97679 | -0.44585 | 0.97662 | -0.44927 | 18.9208
32 | -0.11256 | -0.028413 | 0.11265 | 0.028468 | 8.7089e-05 | 5.5338e-05 | 0.17116 | 0.17116 | 0.17116 | 0.97903 | -0.40215 | 0.97985 | -0.38601 | 23.5107
33 | 0.088247 | 0.022233 | -0.088234 | -0.022225 | 1.3162e-05 | 8.3267e-06 | 0.1345 | 0.1345 | 0.1345 | 0.97662 | -0.44927 | 0.97646 | -0.45239 | 18.4751
34 | -0.11424 | -0.028866 | 0.11428 | 0.02889 | 3.7515e-05 | 2.3843e-05 | 0.17357 | 0.17357 | 0.17357 | 0.97985 | -0.38601 | 0.9802 | -0.37916 | 23.8419
35 | -0.12871 | -0.032511 | 0.12876 | 0.03254 | 4.6757e-05 | 2.976e-05 | 0.19548 | 0.19548 | 0.19548 | 0.9802 | -0.37916 | 0.98059 | -0.37158 | 26.8521
36 | -0.13073 | -0.033035 | 0.1308 | 0.03308 | 7.0838e-05 | 4.5094e-05 | 0.19848 | 0.19848 | 0.19848 | 0.98059 | -0.37158 | 0.98117 | -0.36029 | 27.2631
37 | -0.15242 | -0.038803 | 0.15251 | 0.03886 | 8.923e-05 | 5.6877e-05 | 0.22995 | 0.22995 | 0.22995 | 0.98722 | -0.24329 | 0.98785 | -0.23115 | 31.5865
38 | 0.15026 | 0.038263 | -0.15006 | -0.038136 | 0.00019832 | 0.0001264 | 0.2267 | 0.2267 | 0.2267 | 0.98722 | -0.24329 | 0.9858 | -0.27069 | 31.1399
39 | -0.15648 | -0.039857 | 0.1565 | 0.039869 | 1.8346e-05 | 1.1697e-05 | 0.23594 | 0.23594 | 0.23594 | 0.98785 | -0.23115 | 0.98798 | -0.22872 | 32.4093
40 | 0.14541 | 0.036971 | -0.14535 | -0.036932 | 6.1733e-05 | 3.9335e-05 | 0.21968 | 0.21968 | 0.21968 | 0.9858 | -0.27069 | 0.98534 | -0.27951 | 30.1758
41 | -0.15752 | -0.040125 | 0.15765 | 0.040209 | 0.00013234 | 8.438e-05 | 0.23748 | 0.23748 | 0.23748 | 0.98798 | -0.22872 | 0.98889 | -0.21132 | 32.6205
42 | -0.16098 | -0.041043 | 0.16112 | 0.041128 | 0.00013321 | 8.4943e-05 | 0.24249 | 0.24249 | 0.24249 | 0.98889 | -0.21132 | 0.98978 | -0.1942 | 33.3086
43 | -0.16568 | -0.042273 | 0.16579 | 0.042341 | 0.00010655 | 6.7957e-05 | 0.24935 | 0.24935 | 0.24935 | 0.98978 | -0.1942 | 0.99048 | -0.18089 | 34.252
44 | 0.0015463 | 0.00038711 | -0.0015462 | -0.00038752 | 7.1835e-08 | -4.0241e-07 | 0.0023338 | 0.002334 | 0.002334 | 0.98584 | -0.27154 | 0.98579 | -0.27251 | 0.6412
45 | -0.0027534 | -0.00068966 | 0.0027535 | 0.00068958 | 6.2361e-08 | -8.2858e-08 | 0.0041559 | 0.0041558 | 0.0041559 | 0.98584 | -0.27154 | 0.98586 | -0.27106 | 1.1417
46 | -0.0027535 | -0.00068958 | 0.0027536 | 0.00068952 | 3.9024e-08 | -5.1855e-08 | 0.0041558 | 0.0041558 | 0.0041558 | 0.98586 | -0.27106 | 0.98588 | -0.27076 | 1.1417
47 | -0.0046994 | -0.0011772 | 0.0046998 | 0.0011772 | 3.6577e-07 | -1.3163e-08 | 0.0070927 | 0.0070927 | 0.0070927 | 0.98588 | -0.27076 | 0.98596 | -0.26913 | 1.9486
48 | -0.011748 | -0.0029437 | 0.011749 | 0.0029439 | 4.0244e-07 | 2.1402e-07 | 0.01773 | 0.01773 | 0.01773 | 0.98596 | -0.26913 | 0.986 | -0.26841 | 4.8709
49 | -0.015382 | -0.0038546 | 0.015387 | 0.0038572 | 4.4986e-06 | 2.5951e-06 | 0.023214 | 0.023214 | 0.023214 | 0.986 | -0.26841 | 0.98631 | -0.26227 | 6.3775
50 | -0.0041673 | -0.0010441 | 0.0041678 | 0.001044 | 4.0686e-07 | -6.8835e-08 | 0.0063856 | 0.0063855 | 0.0063856 | 0.97109 | -0.55822 | 0.97119 | -0.55617 | 1.7543
51 | 0.0027914 | 0.00069922 | -0.0027913 | -0.00069926 | 3.1376e-08 | -3.6502e-08 | 0.0042771 | 0.0042771 | 0.0042771 | 0.97109 | -0.55822 | 0.97107 | -0.55846 | 1.175
52 | 0.024966 | 0.0062615 | -0.024959 | -0.0062573 | 7.4781e-06 | 4.1117e-06 | 0.038253 | 0.038254 | 0.038254 | 0.97119 | -0.55617 | 0.97087 | -0.56246 | 5.2546
53 | -0.029134 | -0.0073055 | 0.029144 | 0.0073112 | 9.9442e-06 | 5.7053e-06 | 0.044639 | 0.044639 | 0.044639 | 0.97119 | -0.55617 | 0.97155 | -0.54901 | 6.1317
54 | 0.00074016 | 0.00018547 | -0.00074016 | -0.0001855 | 1.2807e-09 | -3.2026e-08 | 0.0011342 | 0.0011342 | 0.0011342 | 0.97107 | -0.55846 | 0.97107 | -0.55849 | 0.31159
55 | 0.0020512 | 0.00051379 | -0.0020511 | -0.00051385 | 2.2814e-08 | -6.1588e-08 | 0.003143 | 0.003143 | 0.003143 | 0.97107 | -0.55846 | 0.97106 | -0.55869 | 0.86346
56 | 0.0077833 | 0.0019508 | -0.0077826 | -0.0019505 | 7.452e-07 | 3.0426e-07 | 0.011929 | 0.011929 | 0.011929 | 0.97087 | -0.56246 | 0.97077 | -0.56447 | 3.2773
57 | 0.017175 | 0.0043066 | -0.017171 | -0.0043046 | 4.3965e-06 | 1.9771e-06 | 0.026324 | 0.026325 | 0.026325 | 0.97087 | -0.56246 | 0.9706 | -0.56783 | 3.616
58 | -0.033806 | -0.0084794 | 0.03381 | 0.0084818 | 4.0056e-06 | 2.3662e-06 | 0.05178 | 0.05178 | 0.05178 | 0.97155 | -0.54901 | 0.97168 | -0.54653 | 7.1126
59 | 0.0046626 | 0.0011682 | -0.0046622 | -0.0011682 | 3.8181e-07 | -2.8633e-09 | 0.0071411 | 0.0071412 | 0.0071412 | 0.97155 | -0.54901 | 0.97146 | -0.55073 | 1.9619
60 | 0.0013476 | 0.00033752 | -0.0013476 | -0.00033762 | 1.3732e-08 | -9.7454e-08 | 0.0020649 | 0.0020649 | 0.0020649 | 0.97106 | -0.55869 | 0.97105 | -0.5589 | 0.56729
61 | 0.0055289 | 0.0013856 | -0.0055285 | -0.0013856 | 4.2348e-07 | 7.6648e-08 | 0.0084748 | 0.0084748 | 0.0084748 | 0.97077 | -0.56447 | 0.97069 | -0.56607 | 2.3283
62 | 0.0158 | 0.0039609 | -0.015798 | -0.0039601 | 1.9847e-06 | 8.2433e-07 | 0.024223 | 0.024223 | 0.024223 | 0.9706 | -0.56783 | 0.97047 | -0.57047 | 3.3273
63 | 0.0047355 | 0.0011867 | -0.0047349 | -0.0011867 | 5.0985e-07 | 6.1065e-09 | 0.0072518 | 0.0072519 | 0.0072519 | 0.97168 | -0.54653 | 0.97156 | -0.54879 | 1.9923
64 | -0.038546 | -0.0096685 | 0.038568 | 0.0096816 | 2.1861e-05 | 1.3162e-05 | 0.059031 | 0.059031 | 0.059031 | 0.97168 | -0.54653 | 0.97228 | -0.53463 | 8.1087
65 | 0.0037524 | 0.00094023 | -0.0037523 | -0.00094025 | 7.5814e-08 | -2.7249e-08 | 0.0057476 | 0.0057476 | 0.0057476 | 0.97146 | -0.55073 | 0.97144 | -0.55115 | 1.579
66 | 0.00062689 | 0.000157 | -0.00062689 | -0.00015711 | 3.156e-09 | -1.108e-07 | 0.0009606 | 0.00096064 | 0.00096064 | 0.97105 | -0.5589 | 0.97105 | -0.55901 | 0.26391
67 | 0.015798 | 0.0039601 | -0.015795 | -0.0039588 | 3.1029e-06 | 1.289e-06 | 0.024223 | 0.024223 | 0.024223 | 0.97047 | -0.57047 | 0.97026 | -0.57459 | 3.3273
68 | -0.03942 | -0.0098953 | 0.039422 | 0.0098964 | 1.9357e-06 | 1.1685e-06 | 0.060336 | 0.060336 | 0.060336 | 0.97228 | -0.53463 | 0.97233 | -0.53361 | 8.2879
69 | 0.0024168 | 0.00060555 | -0.0024168 | -0.00060561 | 3.6466e-08 | -6.451e-08 | 0.0037019 | 0.003702 | 0.003702 | 0.97144 | -0.55115 | 0.97143 | -0.55147 | 1.017
70 | 0.010884 | 0.0027281 | -0.010882 | -0.0027274 | 1.3607e-06 | 7.1e-07 | 0.016692 | 0.016692 | 0.016692 | 0.97026 | -0.57459 | 0.97013 | -0.57721 | 4.5857
71 | 0.0049108 | 0.0012307 | -0.0049107 | -0.0012307 | 1.1865e-07 | 7.0441e-09 | 0.0075313 | 0.0075313 | 0.0075313 | 0.97026 | -0.57459 | 0.97023 | -0.5751 | 2.0691
72 | 0.0085551 | 0.0021441 | -0.008555 | -0.0021441 | 1.1683e-07 | 5.2432e-08 | 0.013122 | 0.013122 | 0.013122 | 0.97013 | -0.57721 | 0.97011 | -0.5775 | 3.605
73 | 0.0023575 | 0.00059083 | -0.0023575 | -0.00059084 | 3.2742e-09 | -6.1528e-09 | 0.0036156 | 0.0036156 | 0.0036156 | 0.97023 | -0.5751 | 0.97023 | -0.57512 | 0.99329
74 | 0.0076838 | 0.0019257 | -0.0076835 | -0.0019256 | 3.1838e-07 | 1.283e-07 | 0.011786 | 0.011786 | 0.011786 | 0.97011 | -0.5775 | 0.97007 | -0.57837 | 3.2379
75 | -0.067071 | -0.016871 | 0.067072 | 0.016871 | 3.7793e-07 | 2.3709e-07 | 0.10242 | 0.10242 | 0.10242 | 0.97464 | -0.488 | 0.97465 | -0.48789 | 14.0689
76 | 0.064362 | 0.016192 | -0.064324 | -0.016168 | 3.7871e-05 | 2.3717e-05 | 0.098285 | 0.098285 | 0.098285 | 0.97464 | -0.488 | 0.97402 | -0.50033 | 13.5007
77 | 0.0031531 | 0.00079017 | -0.003153 | -0.00079022 | 6.3089e-08 | -5.0099e-08 | 0.0048138 | 0.0048139 | 0.0048139 | 0.97465 | -0.48789 | 0.97463 | -0.48831 | 1.3225
78 | -0.070225 | -0.017661 | 0.070275 | 0.017693 | 5.0328e-05 | 3.1628e-05 | 0.10724 | 0.10724 | 0.10724 | 0.97465 | -0.48789 | 0.97541 | -0.47289 | 14.7302
79 | 0.002036 | 0.0005102 | -0.002036 | -0.00051027 | 2.7599e-08 | -7.7015e-08 | 0.0031105 | 0.0031105 | 0.0031105 | 0.97402 | -0.50033 | 0.974 | -0.50061 | 0.85453
80 | 0.059666 | 0.015001 | -0.059636 | -0.014982 | 2.9635e-05 | 1.8493e-05 | 0.091169 | 0.091169 | 0.091169 | 0.97402 | -0.50033 | 0.97349 | -0.51073 | 12.5233
81 | -0.075942 | -0.019113 | 0.075943 | 0.019114 | 4.9247e-07 | 3.103e-07 | 0.11588 | 0.11588 | 0.11588 | 0.97541 | -0.47289 | 0.97542 | -0.47276 | 15.9177
82 | 0.05705 | 0.014334 | -0.05705 | -0.014334 | 4.632e-07 | 2.8837e-07 | 0.087216 | 0.087216 | 0.087216 | 0.97349 | -0.51073 | 0.97348 | -0.5109 | 11.9802
83 | -0.083685 | -0.021054 | 0.083756 | 0.021099 | 7.1094e-05 | 4.4919e-05 | 0.12769 | 0.12769 | 0.12769 | 0.97542 | -0.47276 | 0.97633 | -0.45499 | 17.54
84 | 0.0020786 | 0.00052087 | -0.0020786 | -0.00052094 | 2.8032e-08 | -7.4122e-08 | 0.0031772 | 0.0031773 | 0.0031773 | 0.97348 | -0.5109 | 0.97347 | -0.51119 | 0.87287
85 | 0.054971 | 0.013813 | -0.054948 | -0.013798 | 2.3321e-05 | 1.4488e-05 | 0.084039 | 0.084039 | 0.084039 | 0.97348 | -0.5109 | 0.97303 | -0.5198 | 11.5438
86 | -0.085799 | -0.021611 | 0.08581 | 0.021618 | 1.0699e-05 | 6.7638e-06 | 0.13081 | 0.13081 | 0.13081 | 0.97633 | -0.45499 | 0.97646 | -0.45239 | 17.9678
87 | 0.0040398 | 0.0010124 | -0.0040397 | -0.0010124 | 9.0023e-08 | -2.0512e-08 | 0.0061778 | 0.0061779 | 0.0061779 | 0.97303 | -0.5198 | 0.97301 | -0.52026 | 1.6972
88 | 0.050908 | 0.012786 | -0.050905 | -0.012784 | 3.1655e-06 | 1.9567e-06 | 0.077861 | 0.077861 | 0.077861 | 0.97303 | -0.5198 | 0.97296 | -0.5211 | 10.6952
89 | 0.058788 | 0.014822 | -0.058787 | -0.014822 | 9.1647e-07 | 5.8249e-07 | 0.088205 | 0.088205 | 0.088205 | 0.99211 | -0.14994 | 0.99209 | -0.15026 | 24.2321
90 | -0.061052 | -0.01539 | 0.061095 | 0.015417 | 4.299e-05 | 2.7337e-05 | 0.091601 | 0.0916 | 0.091601 | 0.99211 | -0.14994 | 0.99287 | -0.13523 | 25.165
91 | 0.055399 | 0.013972 | -0.055314 | -0.013919 | 8.473e-05 | 5.3806e-05 | 0.083123 | 0.083123 | 0.083123 | 0.99209 | -0.15026 | 0.99043 | -0.18227 | 22.8359
92 | 0.17141 | 0.043894 | -0.17123 | -0.043778 | 0.0001814 | 0.00011572 | 0.25722 | 0.25722 | 0.25722 | 0.99287 | -0.13523 | 0.99172 | -0.1571 | 35.3329
93 | -0.2325 | -0.059311 | 0.23283 | 0.059522 | 0.00033094 | 0.00021143 | 0.34882 | 0.34882 | 0.34882 | 0.99287 | -0.13523 | 0.99441 | -0.10581 | 47.9153
94 | 0.16818 | 0.043014 | -0.16798 | -0.04289 | 0.00019337 | 0.00012334 | 0.25265 | 0.25265 | 0.25265 | 0.99172 | -0.1571 | 0.99048 | -0.18089 | 34.7041
95 | -0.23588 | -0.060287 | 0.23591 | 0.060304 | 2.6934e-05 | 1.7208e-05 | 0.35339 | 0.35339 | 0.35339 | 0.99441 | -0.10581 | 0.99454 | -0.10345 | 48.5419
96 | -0.23831 | -0.060905 | 0.23886 | 0.061258 | 0.00055137 | 0.00035227 | 0.35698 | 0.35698 | 0.35698 | 0.99454 | -0.10345 | 0.99705 | -0.055729 | 49.0353
97 | 0.039593 | 0.0099509 | -0.039585 | -0.0099456 | 8.3025e-06 | 5.2337e-06 | 0.059596 | 0.059596 | 0.059596 | 0.98875 | -0.21483 | 0.98853 | -0.21922 | 16.3724
98 | 0.01261 | 0.0031602 | -0.012609 | -0.0031595 | 1.216e-06 | 6.5884e-07 | 0.018819 | 0.018819 | 0.018819 | 0.99705 | -0.055729 | 0.99695 | -0.057754 | 5.1701
99 | -0.25147 | -0.064418 | 0.25215 | 0.064853 | 0.00068106 | 0.00043521 | 0.3758 | 0.3758 | 0.3758 | 0.99705 | -0.055729 | 1 | 0 | 51.6203
100 | 0.033428 | 0.0083936 | -0.033422 | -0.0083901 | 5.6091e-06 | 3.5143e-06 | 0.05036 | 0.05036 | 0.05036 | 0.98782 | -0.23284 | 0.98764 | -0.23635 | 13.8352
101 | -0.036289 | -0.0091105 | 0.036312 | 0.0091254 | 2.358e-05 | 1.4822e-05 | 0.054669 | 0.054669 | 0.054669 | 0.98782 | -0.23284 | 0.98853 | -0.21922 | 15.019
102 | 0.030482 | 0.0076533 | -0.030464 | -0.0076417 | 1.8599e-05 | 1.1603e-05 | 0.045931 | 0.045931 | 0.045931 | 0.98764 | -0.23635 | 0.98699 | -0.24915 | 12.6184
103 | 0.028067 | 0.0070411 | -0.028066 | -0.00704 | 1.7634e-06 | 1.095e-06 | 0.042318 | 0.042318 | 0.042318 | 0.98699 | -0.24915 | 0.98692 | -0.25047 | 11.6258
104 | 0.025387 | 0.0063687 | -0.025374 | -0.0063604 | 1.3463e-05 | 8.3035e-06 | 0.038279 | 0.03828 | 0.03828 | 0.98692 | -0.25047 | 0.98635 | -0.2616 | 10.5164
105 | 0.02171 | 0.0054423 | -0.02171 | -0.0054419 | 6.9478e-07 | 4.2261e-07 | 0.032753 | 0.032753 | 0.032753 | 0.98635 | -0.2616 | 0.98631 | -0.26227 | 8.9981
106 | -0.0025834 | -0.00064725 | 0.0025836 | 0.00064699 | 1.49e-07 | -2.5247e-07 | 0.0038578 | 0.0038577 | 0.0038578 | 0.99646 | -0.067103 | 0.99652 | -0.065892 | 1.0598
107 | 0.0025834 | 0.00064725 | -0.0025833 | -0.00064744 | 1.1592e-07 | -1.9636e-07 | 0.0038578 | 0.0038579 | 0.0038579 | 0.99646 | -0.067103 | 0.99641 | -0.068045 | 1.0599
108 | -0.0036111 | -0.00090452 | 0.0036113 | 0.00090445 | 1.3308e-07 | -7.3862e-08 | 0.005392 | 0.0053919 | 0.005392 | 0.99652 | -0.065892 | 0.99656 | -0.065118 | 1.4813
109 | -0.0065051 | -0.0016297 | 0.0065062 | 0.00163 | 1.0535e-06 | 2.8618e-07 | 0.0097129 | 0.0097128 | 0.0097129 | 0.99656 | -0.065118 | 0.99674 | -0.061718 | 2.6684
110 | 0.0010198 | 0.00025547 | -0.0010198 | -0.00025559 | 8.5236e-09 | -1.2235e-07 | 0.0015225 | 0.0015225 | 0.0015225 | 0.99674 | -0.061718 | 0.99673 | -0.061893 | 0.41827
111 | -0.007526 | -0.0018855 | 0.0075263 | 0.0018856 | 2.4581e-07 | 8.9632e-08 | 0.011235 | 0.011235 | 0.011235 | 0.99674 | -0.061718 | 0.99678 | -0.061032 | 3.0866
112 | 0.048332 | 0.012139 | -0.048315 | -0.012129 | 1.7577e-05 | 1.0824e-05 | 0.073927 | 0.073927 | 0.073927 | 0.97296 | -0.5211 | 0.97258 | -0.52872 | 10.1548
113 | 0.040368 | 0.010137 | -0.040359 | -0.010131 | 9.4012e-06 | 5.6907e-06 | 0.061769 | 0.061769 | 0.061769 | 0.97258 | -0.52872 | 0.97233 | -0.53361 | 8.4848
114 | 0.0079465 | 0.0019917 | -0.0079457 | -0.0019913 | 8.2772e-07 | 3.4446e-07 | 0.012158 | 0.012158 | 0.012158 | 0.97258 | -0.52872 | 0.97247 | -0.53091 | 3.3401
115 | 0.0087237 | 0.0021866 | -0.0087211 | -0.0021855 | 2.5404e-06 | 1.0986e-06 | 0.012981 | 0.012981 | 0.012981 | 1 | 0 | 0.99968 | -0.0061136 | 3.5663
116 | 0.0071285 | 0.0017863 | -0.0071282 | -0.0017863 | 2.1206e-07 | 6.9865e-08 | 0.010611 | 0.010611 | 0.010611 | 0.99968 | -0.0061136 | 0.99965 | -0.0067381 | 2.915
117 | 0.0041042 | 0.0010283 | -0.0041038 | -0.0010284 | 3.48e-07 | -1.0323e-07 | 0.0061091 | 0.0061092 | 0.0061092 | 0.99965 | -0.0067381 | 0.99956 | -0.0085183 | 1.6784
118 | 0.0030334 | 0.00076016 | -0.0030333 | -0.00076023 | 6.3895e-08 | -6.7487e-08 | 0.0045276 | 0.0045276 | 0.0045276 | 0.99695 | -0.057754 | 0.99692 | -0.058196 | 1.2438
119 | 0.0095751 | 0.0023994 | -0.0095736 | -0.0023987 | 1.4949e-06 | 7.0226e-07 | 0.014291 | 0.014292 | 0.014292 | 0.99695 | -0.057754 | 0.99678 | -0.061032 | 3.9263
120 | 0.0020244 | 0.0005073 | -0.0020244 | -0.00050736 | 1.8325e-08 | -5.8797e-08 | 0.0030137 | 0.0030137 | 0.0030137 | 0.99956 | -0.0085183 | 0.99955 | -0.0087083 | 0.82794
121 | 0.0042122 | 0.0010556 | -0.0042121 | -0.0010557 | 1.0169e-07 | -1.5904e-08 | 0.0064453 | 0.0064453 | 0.0064453 | 0.97247 | -0.53091 | 0.97244 | -0.53142 | 1.7707
122 | 0.0011681 | 0.00029266 | -0.0011681 | -0.00029275 | 9.6467e-09 | -9.3304e-08 | 0.0017892 | 0.0017893 | 0.0017893 | 0.97143 | -0.55147 | 0.97142 | -0.55164 | 0.49156
123 | -0.0052831 | -0.001324 | 0.0052831 | 0.001324 | 6.1889e-08 | 8.5847e-09 | 0.0081039 | 0.0081039 | 0.0081039 | 0.97006 | -0.57861 | 0.97007 | -0.57837 | 2.2264
124 | 0.0045244 | 0.0011339 | -0.0045243 | -0.0011339 | 1.061e-07 | -4.6128e-09 | 0.0069401 | 0.0069402 | 0.0069402 | 0.97006 | -0.57861 | 0.97003 | -0.57911 | 1.9066
125 | 0.0023089 | 0.00057864 | -0.0023089 | -0.00057867 | 1.3337e-08 | -2.6463e-08 | 0.0035418 | 0.0035418 | 0.0035418 | 0.97003 | -0.57911 | 0.97003 | -0.57923 | 0.97304

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26561 | 0.067814

## res_load
| p_mw | q_mvar
0 | 0.00084011 | 0.00021055
1 | 0.0041143 | 0.0010311
2 | 0.001011 | 0.00025338
3 | 0.00055319 | 0.00013864
4 | 0.00072795 | 0.00018244
5 | 0.0035175 | 0.00088156
6 | 0.00064607 | 0.00016192
7 | 0.0015935 | 0.00039936
8 | 0.0075007 | 0.0018798
9 | 0.0011477 | 0.00028764
10 | 0.0015071 | 0.00037772
11 | 0.0033293 | 0.0008344
12 | 0.0022441 | 0.00056241
13 | 0.0021697 | 0.00054377
14 | 0.0030428 | 0.00076261
15 | 0.0017856 | 0.00044751
16 | 0.0019103 | 0.00047876
17 | 0.0022999 | 0.00057642
18 | 0.0020205 | 0.00050639
19 | 0.0020402 | 0.00051132
20 | 0.0022447 | 0.00056257
21 | 0.0066221 | 0.0016597
22 | 0.0021297 | 0.00053376
23 | 0.0015877 | 0.00039791
24 | 0.0014091 | 0.00035314
25 | 0.0019722 | 0.00049427
26 | 0.002157 | 0.0005406
27 | 0.0039766 | 0.00099662
28 | 0.0046497 | 0.0011653
29 | 0.001021 | 0.00025588
30 | 0.004678 | 0.0011724
31 | 0.0033294 | 0.00083442
32 | 0.0045684 | 0.0011449
33 | 0.0018353 | 0.00045996
34 | 0.0012072 | 0.00030255
35 | 0.0015462 | 0.00038752
36 | 0.0019458 | 0.00048767
37 | 0.0070484 | 0.0017665
38 | 0.0036339 | 0.00091075
39 | 0.001376 | 0.00034486
40 | 0.00074016 | 0.0001855
41 | 0.00070356 | 0.00017633
42 | 0.0022537 | 0.00056483
43 | 0.0013712 | 0.00034365
44 | 0.00090981 | 0.00022802
45 | 0.00072067 | 0.00018062
46 | 0.0055285 | 0.0013856
47 | 0.0047349 | 0.0011867
48 | 0.00085235 | 0.00021362
49 | 0.0013355 | 0.00033471
50 | 0.00062689 | 0.00015711
51 | 0.0023273 | 0.00058326
52 | 0.0025532 | 0.00063989
53 | 0.00087117 | 0.00021834
54 | 0.0023575 | 0.00059084
55 | 0.0027096 | 0.00067909
56 | 0.0026219 | 0.0006571
57 | 0.003153 | 0.00079022
58 | 0.0056671 | 0.0014203
59 | 0.002036 | 0.00051027
60 | 0.0025863 | 0.0006482
61 | 0.0077423 | 0.0019404
62 | 0.0020431 | 0.00051205
63 | 0.0020786 | 0.00052094
64 | 0.0022641 | 0.00056745
65 | 0.0033883 | 0.00084918
66 | 0.002706 | 0.00067819
67 | 0.003051 | 0.00076465
68 | 0.0030487 | 0.00076409
69 | 0.002191 | 0.0005491
70 | 0.0024006 | 0.00060164
71 | 0.0025383 | 0.00063616
72 | 0.0028607 | 0.00071695
73 | 0.0029398 | 0.00073679
74 | 0.0032729 | 0.00082027
75 | 0.0023964 | 0.00060058
76 | 0.0026786 | 0.00067131
77 | 0.0036633 | 0.00091811
78 | 0.0010275 | 0.00025753
79 | 0.0025833 | 0.00064744
80 | 0.0028939 | 0.00072527
81 | 0.0040397 | 0.0010124
82 | 0.0025723 | 0.00064469
83 | 0.0063228 | 0.0015846
84 | 0.0030892 | 0.00077423
85 | 0.0015927 | 0.00039917
86 | 0.0030241 | 0.00075791
87 | 0.0020794 | 0.00052114
88 | 0.0030333 | 0.00076023
89 | 0.0020474 | 0.00051312
90 | 0.0020244 | 0.00050736
91 | 0.0024237 | 0.00060742
92 | 0.0010198 | 0.00025559
93 | 0.00093688 | 0.0002348
94 | 0.0037335 | 0.0009357
95 | 0.0042121 | 0.0010557
96 | 0.0012487 | 0.00031295
97 | 0.0011681 | 0.00029275
98 | 0.00075868 | 0.00019014
99 | 0.0024004 | 0.0006016
100 | 0.0022154 | 0.00055522
101 | 0.0023089 | 0.00057867

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1