## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-11_0_9_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-11_0_9_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-11_0_9_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1054-11_0_9_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1054-11_0_9_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1054-11_0_9_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1054-11_0_9_node_135 | 0.4 | n |  | TRUE
7 | bus_LV_1054-11_0_9_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1054-11_0_9_node_131 | 0.4 | n |  | TRUE
9 | bus_LV_1054-11_0_9_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1054-11_0_9_node_132 | 0.4 | n |  | TRUE
11 | bus_LV_1054-11_0_9_node_129 | 0.4 | n |  | TRUE
12 | bus_LV_1054-11_0_9_node_125 | 0.4 | n |  | TRUE
13 | bus_LV_1054-11_0_9_node_126 | 0.4 | n |  | TRUE
14 | bus_LV_1054-11_0_9_node_130 | 0.4 | n |  | TRUE
15 | bus_LV_1054-11_0_9_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1054-11_0_9_node_124 | 0.4 | n |  | TRUE
17 | bus_LV_1054-11_0_9_node_134 | 0.4 | n |  | TRUE
18 | bus_LV_1054-11_0_9_node_133 | 0.4 | n |  | TRUE
19 | bus_LV_1054-11_0_9_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1054-11_0_9_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1054-11_0_9_node_128 | 0.4 | n |  | TRUE
22 | bus_LV_1054-11_0_9_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_1054-11_0_9_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1054-11_0_9_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1054-11_0_9_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1054-11_0_9_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1054-11_0_9_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1054-11_0_9_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1054-11_0_9_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1054-11_0_9_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_1054-11_0_9_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_1054-11_0_9_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1054-11_0_9_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_1054-11_0_9_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1054-11_0_9_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1054-11_0_9_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1054-11_0_9_node_65 | 0.4 | n |  | TRUE
38 | bus_LV_1054-11_0_9_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1054-11_0_9_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1054-11_0_9_node_43 | 0.4 | n |  | TRUE
41 | bus_LV_1054-11_0_9_node_127 | 0.4 | n |  | TRUE
42 | bus_LV_1054-11_0_9_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1054-11_0_9_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_1054-11_0_9_node_63 | 0.4 | n |  | TRUE
45 | bus_LV_1054-11_0_9_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1054-11_0_9_node_59 | 0.4 | n |  | TRUE
47 | bus_LV_1054-11_0_9_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_1054-11_0_9_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1054-11_0_9_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_1054-11_0_9_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_1054-11_0_9_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_1054-11_0_9_node_57 | 0.4 | n |  | TRUE
53 | bus_LV_1054-11_0_9_node_62 | 0.4 | n |  | TRUE
54 | bus_LV_1054-11_0_9_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1054-11_0_9_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_1054-11_0_9_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_1054-11_0_9_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_1054-11_0_9_node_38 | 0.4 | n |  | TRUE
59 | bus_LV_1054-11_0_9_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_1054-11_0_9_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_1054-11_0_9_node_29 | 0.4 | n |  | TRUE
62 | bus_LV_1054-11_0_9_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_1054-11_0_9_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_1054-11_0_9_node_33 | 0.4 | n |  | TRUE
65 | bus_LV_1054-11_0_9_node_36 | 0.4 | n |  | TRUE
66 | bus_LV_1054-11_0_9_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_1054-11_0_9_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1054-11_0_9_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_1054-11_0_9_node_39 | 0.4 | n |  | TRUE
70 | bus_LV_1054-11_0_9_node_40 | 0.4 | n |  | TRUE
71 | bus_LV_1054-11_0_9_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_1054-11_0_9_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_1054-11_0_9_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_1054-11_0_9_node_108 | 0.4 | n |  | TRUE
75 | bus_LV_1054-11_0_9_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_1054-11_0_9_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_1054-11_0_9_node_48 | 0.4 | n |  | TRUE
78 | bus_LV_1054-11_0_9_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_1054-11_0_9_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_1054-11_0_9_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_1054-11_0_9_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_1054-11_0_9_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_1054-11_0_9_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_1054-11_0_9_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_1054-11_0_9_node_93 | 0.4 | n |  | TRUE
86 | bus_LV_1054-11_0_9_node_116 | 0.4 | n |  | TRUE
87 | bus_LV_1054-11_0_9_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_1054-11_0_9_node_91 | 0.4 | n |  | TRUE
89 | bus_LV_1054-11_0_9_node_118 | 0.4 | n |  | TRUE
90 | bus_LV_1054-11_0_9_node_97 | 0.4 | n |  | TRUE
91 | bus_LV_1054-11_0_9_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_1054-11_0_9_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_1054-11_0_9_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_1054-11_0_9_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_1054-11_0_9_node_98 | 0.4 | n |  | TRUE
96 | bus_LV_1054-11_0_9_node_119 | 0.4 | n |  | TRUE
97 | bus_LV_1054-11_0_9_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_1054-11_0_9_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_1054-11_0_9_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_1054-11_0_9_node_80 | 0.4 | n |  | TRUE
101 | bus_LV_1054-11_0_9_node_113 | 0.4 | n |  | TRUE
102 | bus_LV_1054-11_0_9_node_114 | 0.4 | n |  | TRUE
103 | bus_LV_1054-11_0_9_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_1054-11_0_9_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_1054-11_0_9_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_1054-11_0_9_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_1054-11_0_9_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_1054-11_0_9_node_87 | 0.4 | n |  | TRUE
109 | bus_LV_1054-11_0_9_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_1054-11_0_9_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1054-11_0_9_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_1054-11_0_9_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_1054-11_0_9_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1054-11_0_9_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_1054-11_0_9_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_1054-11_0_9_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_1054-11_0_9_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_1054-11_0_9_node_117 | 0.4 | n |  | TRUE
119 | bus_LV_1054-11_0_9_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_1054-11_0_9_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_1054-11_0_9_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_1054-11_0_9_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_1054-11_0_9_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_1054-11_0_9_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_1054-11_0_9_node_111 | 0.4 | n |  | TRUE
126 | bus_LV_1054-11_0_9_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_1054-11_0_9_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_1054-11_0_9_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_1054-11_0_9_node_122 | 0.4 | n |  | TRUE
130 | bus_LV_1054-11_0_9_node_120 | 0.4 | n |  | TRUE
131 | bus_LV_1054-11_0_9_node_121 | 0.4 | n |  | TRUE
132 | bus_LV_1054-11_0_9_node_123 | 0.4 | n |  | TRUE
133 | bus_LV_1054-11_0_9_node_136 | 0.4 | n |  | TRUE
134 | bus_MV_212_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-11_0_9_load_0 | 0 | 0.0072218 | 0.0018099 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-11_0_9_load_4 | 3 | 0.0030343 | 0.00076046 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-11_0_9_load_8 | 4 | 0.00016478 | 4.1298e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-11_0_9_load_7 | 5 | 0.0062705 | 0.0015715 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-11_0_9_load_135 | 6 | 0.0016719 | 0.00041902 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-11_0_9_load_131 | 8 | 0.0016733 | 0.00041937 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-11_0_9_load_132 | 10 | 0.0010683 | 0.00026773 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-11_0_9_load_129 | 11 | 0.0016723 | 0.00041912 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-11_0_9_load_125 | 12 | 0.0046061 | 0.0011544 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-11_0_9_load_126 | 13 | 0.0014815 | 0.00037129 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-11_0_9_load_130 | 14 | 0.0016731 | 0.00041931 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-11_0_9_load_124 | 16 | 0.012253 | 0.003071 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-11_0_9_load_133 | 18 | 0.0025258 | 0.00063302 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-11_0_9_load_128 | 21 | 0.02 | 0.0050125 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-11_0_9_load_9 | 22 | 0.0064462 | 0.0016156 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-11_0_9_load_11 | 23 | 0.0080206 | 0.0020102 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-11_0_9_load_12 | 24 | 0.00361 | 0.00090475 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-11_0_9_load_13 | 27 | 0.0048051 | 0.0012043 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-11_0_9_load_64 | 30 | 0.0065924 | 0.0016522 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-11_0_9_load_66 | 31 | 0.0091437 | 0.0022916 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-11_0_9_load_55 | 33 | 0.013054 | 0.0032717 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-11_0_9_load_25 | 34 | 0.021207 | 0.0053151 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-11_0_9_load_65 | 37 | 0.013497 | 0.0033827 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-11_0_9_load_127 | 41 | 0.0014815 | 0.00037129 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-11_0_9_load_34 | 43 | 0.0086324 | 0.0021635 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-11_0_9_load_63 | 44 | 0.0066167 | 0.0016583 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-11_0_9_load_59 | 46 | 0.0053308 | 0.001336 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-11_0_9_load_52 | 47 | 0.0080897 | 0.0020275 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-11_0_9_load_58 | 50 | 0.01369 | 0.003431 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-11_0_9_load_62 | 53 | 0.011438 | 0.0028666 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-11_0_9_load_41 | 54 | 0.0047864 | 0.0011996 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-11_0_9_load_61 | 55 | 0.0017668 | 0.00044279 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-11_0_9_load_60 | 56 | 0.0038755 | 0.0009713 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-11_0_9_load_51 | 57 | 0.013909 | 0.003486 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-11_0_9_load_56 | 59 | 0.0083571 | 0.0020945 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-11_0_9_load_32 | 60 | 0.00822 | 0.0020601 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-11_0_9_load_29 | 61 | 0.0082199 | 0.0020601 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-11_0_9_load_31 | 63 | 0.0082143 | 0.0020587 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-11_0_9_load_33 | 64 | 0.0048921 | 0.0012261 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-11_0_9_load_36 | 65 | 0.0079927 | 0.0020032 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-11_0_9_load_49 | 66 | 0.002069 | 0.00051853 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-11_0_9_load_54 | 67 | 0.00346 | 0.00086716 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-11_0_9_load_47 | 68 | 0.0020747 | 0.00051997 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-11_0_9_load_39 | 69 | 0.0031295 | 0.00078432 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-11_0_9_load_40 | 70 | 0.0024234 | 0.00060736 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-11_0_9_load_42 | 71 | 0.0024216 | 0.00060691 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-11_0_9_load_44 | 72 | 0.0030191 | 0.00075667 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-11_0_9_load_107 | 73 | 0.0020682 | 0.00051834 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-11_0_9_load_108 | 74 | 0.0028981 | 0.00072634 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-11_0_9_load_45 | 75 | 0.0083045 | 0.0020813 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-11_0_9_load_46 | 76 | 0.0023659 | 0.00059295 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-11_0_9_load_48 | 77 | 0.0085014 | 0.0021306 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-11_0_9_load_73 | 78 | 0.0094175 | 0.0023602 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-11_0_9_load_72 | 79 | 0.0073664 | 0.0018462 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-11_0_9_load_67 | 80 | 0.0020912 | 0.0005241 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-11_0_9_load_68 | 81 | 0.0022314 | 0.00055923 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-11_0_9_load_69 | 82 | 0.0012737 | 0.00031921 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-11_0_9_load_71 | 84 | 0.0017362 | 0.00043513 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-11_0_9_load_93 | 85 | 0.0031922 | 0.00080005 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-11_0_9_load_79 | 87 | 0.001509 | 0.0003782 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-11_0_9_load_91 | 88 | 0.0013469 | 0.00033757 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-11_0_9_load_118 | 89 | 0.0058503 | 0.0014662 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-11_0_9_load_97 | 90 | 0.0032514 | 0.00081489 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-11_0_9_load_77 | 91 | 0.0027252 | 0.00068299 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-11_0_9_load_76 | 94 | 0.0036816 | 0.0009227 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-11_0_9_load_98 | 95 | 0.0018195 | 0.00045601 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-11_0_9_load_119 | 96 | 0.0021105 | 0.00052893 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-11_0_9_load_99 | 97 | 0.0018194 | 0.00045598 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-11_0_9_load_85 | 98 | 0.0030177 | 0.00075631 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-11_0_9_load_78 | 99 | 0.0020315 | 0.00050915 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-11_0_9_load_80 | 100 | 0.00108 | 0.00027066 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-11_0_9_load_113 | 101 | 0.0015177 | 0.00038037 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-11_0_9_load_114 | 102 | 0.0011984 | 0.00030035 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-11_0_9_load_81 | 103 | 0.0040894 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-11_0_9_load_82 | 104 | 0.0082135 | 0.0020585 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-11_0_9_load_83 | 105 | 0.0070273 | 0.0017612 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-11_0_9_load_84 | 106 | 0.0048954 | 0.0012269 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-11_0_9_load_86 | 107 | 0.001325 | 0.00033209 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-11_0_9_load_87 | 108 | 0.0017453 | 0.00043742 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-11_0_9_load_88 | 109 | 0.0012892 | 0.0003231 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-11_0_9_load_89 | 110 | 0.001281 | 0.00032106 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-11_0_9_load_95 | 112 | 0.0013605 | 0.00034097 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-11_0_9_load_96 | 114 | 0.0075758 | 0.0018987 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-11_0_9_load_102 | 115 | 0.0050541 | 0.0012667 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-11_0_9_load_92 | 116 | 0.0012592 | 0.0003156 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-11_0_9_load_94 | 117 | 0.0012592 | 0.0003156 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-11_0_9_load_117 | 118 | 0.0012592 | 0.0003156 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-11_0_9_load_100 | 119 | 0.0012594 | 0.00031564 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-11_0_9_load_101 | 120 | 0.0049443 | 0.0012392 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-11_0_9_load_105 | 122 | 0.0021933 | 0.0005497 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1054-11_0_9_load_106 | 123 | 0.0019302 | 0.00048376 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1054-11_0_9_load_109 | 124 | 0.0018944 | 0.00047479 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1054-11_0_9_load_111 | 125 | 0.0012584 | 0.00031539 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1054-11_0_9_load_110 | 126 | 0.0018876 | 0.00047308 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1054-11_0_9_load_112 | 127 | 0.0056004 | 0.0014036 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1054-11_0_9_load_115 | 128 | 0.00083415 | 0.00020906 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1054-11_0_9_load_122 | 129 | 0.00087125 | 0.00021836 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1054-11_0_9_load_120 | 130 | 0.0023692 | 0.00059377 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1054-11_0_9_load_121 | 131 | 0.00083939 | 0.00021037 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1054-11_0_9_load_123 | 132 | 0.0008951 | 0.00022433 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1054-11_0_9_load_136 | 133 | 0.0025427 | 0.00063726 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-11_0_9_line_0 |  | 0 | 1 | 0.059352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-11_0_9_line_1 |  | 1 | 2 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-11_0_9_line_2 |  | 1 | 3 | 0.05158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-11_0_9_line_3 |  | 2 | 6 | 0.011468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-11_0_9_line_4 |  | 4 | 5 | 0.027344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-11_0_9_line_5 |  | 5 | 22 | 0.0251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-11_0_9_line_6 |  | 6 | 7 | 0.013442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-11_0_9_line_7 |  | 7 | 8 | 0.0093236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-11_0_9_line_8 |  | 8 | 14 | 0.021713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-11_0_9_line_9 |  | 9 | 10 | 0.039915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-11_0_9_line_10 |  | 9 | 11 | 0.0096364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-11_0_9_line_11 |  | 10 | 18 | 0.020109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-11_0_9_line_12 |  | 11 | 14 | 0.021714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-11_0_9_line_13 |  | 12 | 13 | 0.0027155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-11_0_9_line_14 |  | 13 | 41 | 0.019529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-11_0_9_line_15 |  | 15 | 16 | 0.030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-11_0_9_line_16 |  | 15 | 17 | 0.090066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-11_0_9_line_17 |  | 16 | 20 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-11_0_9_line_18 |  | 17 | 18 | 0.02311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-11_0_9_line_19 |  | 17 | 41 | 0.03662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-11_0_9_line_20 |  | 19 | 20 | 0.061815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-11_0_9_line_21 |  | 19 | 21 | 0.037124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-11_0_9_line_22 |  | 20 | 25 | 0.020226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-11_0_9_line_23 |  | 22 | 23 | 0.030704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-11_0_9_line_24 |  | 23 | 24 | 0.020959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-11_0_9_line_25 |  | 24 | 27 | 0.023079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-11_0_9_line_26 |  | 25 | 26 | 0.11667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-11_0_9_line_27 |  | 25 | 27 | 0.0067274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-11_0_9_line_28 |  | 26 | 31 | 0.013033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-11_0_9_line_29 |  | 26 | 32 | 0.1268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-11_0_9_line_30 |  | 26 | 33 | 0.018866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-11_0_9_line_31 |  | 28 | 29 | 0.033134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-11_0_9_line_32 |  | 28 | 30 | 0.031163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-11_0_9_line_33 |  | 29 | 42 | 0.045664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-11_0_9_line_34 |  | 29 | 43 | 0.023535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1054-11_0_9_line_35 |  | 30 | 44 | 0.026339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-11_0_9_line_36 |  | 32 | 34 | 0.020528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1054-11_0_9_line_37 |  | 33 | 51 | 0.022196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1054-11_0_9_line_38 |  | 35 | 36 | 0.030654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1054-11_0_9_line_39 |  | 35 | 37 | 0.011679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1054-11_0_9_line_40 |  | 36 | 47 | 0.014642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-11_0_9_line_41 |  | 36 | 45 | 0.007358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1054-11_0_9_line_42 |  | 37 | 38 | 0.028658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1054-11_0_9_line_43 |  | 38 | 39 | 0.020688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1054-11_0_9_line_44 |  | 39 | 40 | 0.064582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1054-11_0_9_line_45 |  | 40 | 54 | 0.037317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1054-11_0_9_line_46 |  | 42 | 58 | 0.02219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1054-11_0_9_line_47 |  | 42 | 59 | 0.014988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_1054-11_0_9_line_48 |  | 42 | 52 | 0.033003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1054-11_0_9_line_49 |  | 43 | 65 | 0.020647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-11_0_9_line_50 |  | 45 | 46 | 0.023233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1054-11_0_9_line_51 |  | 46 | 50 | 0.013112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1054-11_0_9_line_52 |  | 47 | 57 | 0.0070672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-11_0_9_line_53 |  | 48 | 49 | 0.00446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1054-11_0_9_line_54 |  | 48 | 50 | 0.016876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1054-11_0_9_line_55 |  | 49 | 60 | 0.0077784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-11_0_9_line_56 |  | 49 | 58 | 0.019407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1054-11_0_9_line_57 |  | 51 | 67 | 0.017332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-11_0_9_line_58 |  | 52 | 53 | 0.010641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1054-11_0_9_line_59 |  | 54 | 69 | 0.021482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1054-11_0_9_line_60 |  | 55 | 56 | 0.026329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1054-11_0_9_line_61 |  | 56 | 64 | 0.028866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1054-11_0_9_line_62 |  | 58 | 66 | 0.043171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1054-11_0_9_line_63 |  | 59 | 67 | 0.020228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1054-11_0_9_line_64 |  | 60 | 62 | 0.015683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-11_0_9_line_65 |  | 61 | 62 | 0.015766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1054-11_0_9_line_66 |  | 61 | 63 | 0.019009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1054-11_0_9_line_67 |  | 62 | 64 | 0.030229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1054-11_0_9_line_68 |  | 66 | 68 | 0.0052186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1054-11_0_9_line_69 |  | 68 | 75 | 0.0036428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1054-11_0_9_line_70 |  | 69 | 70 | 0.017103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1054-11_0_9_line_71 |  | 70 | 71 | 0.0083756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1054-11_0_9_line_72 |  | 71 | 72 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1054-11_0_9_line_73 |  | 72 | 73 | 0.016743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1054-11_0_9_line_74 |  | 73 | 74 | 0.012321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1054-11_0_9_line_75 |  | 74 | 106 | 0.030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1054-11_0_9_line_76 |  | 75 | 76 | 0.0019741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-11_0_9_line_77 |  | 76 | 77 | 0.027785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-11_0_9_line_78 |  | 77 | 78 | 0.036646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-11_0_9_line_79 |  | 78 | 79 | 0.029085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-11_0_9_line_80 |  | 80 | 81 | 0.0010888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1054-11_0_9_line_81 |  | 80 | 82 | 0.013454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1054-11_0_9_line_82 |  | 81 | 83 | 0.018944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1054-11_0_9_line_83 |  | 82 | 84 | 0.0084523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-11_0_9_line_84 |  | 83 | 85 | 0.03519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1054-11_0_9_line_85 |  | 83 | 86 | 0.065223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1054-11_0_9_line_86 |  | 84 | 87 | 0.01601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-11_0_9_line_87 |  | 85 | 88 | 0.020684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1054-11_0_9_line_88 |  | 86 | 89 | 0.044304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-11_0_9_line_89 |  | 86 | 90 | 0.018383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1054-11_0_9_line_90 |  | 87 | 91 | 0.019473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-11_0_9_line_91 |  | 88 | 116 | 0.017583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1054-11_0_9_line_92 |  | 90 | 114 | 0.0061477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_1054-11_0_9_line_93 |  | 91 | 99 | 0.019205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1054-11_0_9_line_94 |  | 92 | 93 | 0.003335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_1054-11_0_9_line_95 |  | 92 | 94 | 0.086607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_1054-11_0_9_line_96 |  | 93 | 95 | 0.090674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_1054-11_0_9_line_97 |  | 94 | 96 | 0.024859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_1054-11_0_9_line_98 |  | 95 | 97 | 0.006222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1054-11_0_9_line_99 |  | 96 | 98 | 0.0089236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_1054-11_0_9_line_100 |  | 97 | 119 | 0.013008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_1054-11_0_9_line_101 |  | 98 | 105 | 0.0031443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_1054-11_0_9_line_102 |  | 99 | 100 | 0.0081437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-11_0_9_line_103 |  | 100 | 101 | 0.0026482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-11_0_9_line_104 |  | 101 | 102 | 0.0022423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1054-11_0_9_line_105 |  | 102 | 128 | 0.0055083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1054-11_0_9_line_106 |  | 103 | 104 | 0.0071109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_1054-11_0_9_line_107 |  | 103 | 105 | 0.027085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_1054-11_0_9_line_108 |  | 104 | 106 | 0.023008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_1054-11_0_9_line_109 |  | 107 | 108 | 0.010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_1054-11_0_9_line_110 |  | 107 | 109 | 0.015441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_1054-11_0_9_line_111 |  | 108 | 110 | 0.00028063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_1054-11_0_9_line_112 |  | 109 | 111 | 0.20395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_1054-11_0_9_line_113 |  | 110 | 112 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_1054-11_0_9_line_114 |  | 111 | 113 | 0.21892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1054-11_0_9_line_115 |  | 112 | 114 | 0.013634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_1054-11_0_9_line_116 |  | 113 | 115 | 0.037372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1054-11_0_9_line_117 |  | 115 | 120 | 0.038701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1054-11_0_9_line_118 |  | 116 | 117 | 0.0056389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_1054-11_0_9_line_119 |  | 117 | 118 | 0.0056389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_1054-11_0_9_line_120 |  | 118 | 119 | 0.0056399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_1054-11_0_9_line_121 |  | 120 | 121 | 0.021106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1054-11_0_9_line_122 |  | 121 | 122 | 0.062235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1054-11_0_9_line_123 |  | 121 | 123 | 0.018356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1054-11_0_9_line_124 |  | 122 | 124 | 0.028769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1054-11_0_9_line_125 |  | 123 | 125 | 0.010836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1054-11_0_9_line_126 |  | 124 | 126 | 0.023346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1054-11_0_9_line_127 |  | 125 | 127 | 0.0082914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1054-11_0_9_line_128 |  | 128 | 129 | 0.004862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1054-11_0_9_line_129 |  | 129 | 130 | 0.011348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1054-11_0_9_line_130 |  | 130 | 131 | 0.0020348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1054-11_0_9_line_131 |  | 131 | 132 | 0.0047477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1054-11_0_9_line_132 |  | 132 | 133 | 0.0055899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-11_0_9_trafo_38 | 0.63 MVA 20/0.4 kV | 134 | 58 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2669634.1174 | 1216177.7912 | 2669623.2398 | 1216165.8233 | 2669622.1576 | 1216162.9199 | 2669622.8017 | 1216159.781 | 2669622.3806 | 1216156.8298 | 2669620.7273 | 1216154.0643 | 2669616.6977 | 1216150.6151 | 2669611.7972 | 1216147.6226 | 2669605.7568 | 1216141.4593 | 2669597.8561 | 1216133.8095
1 | 2669634.1174 | 1216177.7912 | 2669639.6868 | 1216183.3264 | 2669645.6268 | 1216188.9772 | 2669648.0514 | 1216186.8152
2 | 2669634.1174 | 1216177.7912 | 2669669.8789 | 1216140.6207
3 | 2669648.0514 | 1216186.8152 | 2669656.0511 | 1216195.0317
4 | 2669806.1753 | 1216075.8457 | 2669791.8696 | 1216063.6968 | 2669785.4888 | 1216057.967
5 | 2669806.1753 | 1216075.8457 | 2669825.3074 | 1216092.0935
6 | 2669665.4281 | 1216204.6629 | 2669656.0511 | 1216195.0317
7 | 2669665.4281 | 1216204.6629 | 2669672.4198 | 1216210.831
8 | 2669672.4198 | 1216210.831 | 2669688.7018 | 1216225.1952
9 | 2669712.2115 | 1216245.9358 | 2669716.8689 | 1216250.2263 | 2669739.5171 | 1216225.4297
10 | 2669712.2115 | 1216245.9358 | 2669704.9852 | 1216239.5607
11 | 2669739.5171 | 1216225.4297 | 2669753.0785 | 1216210.5818
12 | 2669704.9852 | 1216239.5607 | 2669688.7018 | 1216225.1952
13 | 2669726.5721 | 1216152.368 | 2669728.5138 | 1216154.2663
14 | 2669742.4783 | 1216167.9186 | 2669728.5138 | 1216154.2663
15 | 2669828.3302 | 1216126.052 | 2669851.5043 | 1216146.0927
16 | 2669828.3302 | 1216126.052 | 2669768.6635 | 1216193.5185
17 | 2669866.4782 | 1216159.042 | 2669851.5043 | 1216146.0927
18 | 2669768.6635 | 1216193.5185 | 2669753.0785 | 1216210.5818
19 | 2669768.6635 | 1216193.5185 | 2669742.4783 | 1216167.9186
20 | 2669858.7697 | 1216207.1044 | 2669860.5568 | 1216204.9239 | 2669861.5672 | 1216202.2897 | 2669861.714 | 1216199.4785 | 2669860.9715 | 1216196.757 | 2669859.4198 | 1216194.3928 | 2669877.6505 | 1216173.6822 | 2669869.1821 | 1216166.1004 | 2669870.3961 | 1216164.8805 | 2669866.4782 | 1216159.042
21 | 2669858.7697 | 1216207.1044 | 2669860.7964 | 1216218.1685 | 2669868.6422 | 1216228.3335 | 2669877.8935 | 1216237.5159
22 | 2669866.4782 | 1216159.042 | 2669867.2939 | 1216158.1177 | 2669871.9263 | 1216152.8798 | 2669879.8754 | 1216143.8895
23 | 2669849.1063 | 1216111.4889 | 2669833.1152 | 1216098.7241 | 2669825.3074 | 1216092.0935
24 | 2669849.1063 | 1216111.4889 | 2669851.2374 | 1216113.19 | 2669865.5029 | 1216124.5432
25 | 2669883.561 | 1216138.9147 | 2669865.5029 | 1216124.5432
26 | 2669879.8754 | 1216143.8895 | 2669896.2118 | 1216158.4568 | 2669906.0622 | 1216154.3808 | 2669911.1047 | 1216148.4918 | 2669926.1111 | 1216131.457 | 2669938.2581 | 1216118.6802 | 2669924.445 | 1216106.4994 | 2669914.8501 | 1216097.8481 | 2669916.8507 | 1216094.9475 | 2669917.5151 | 1216093.9769
27 | 2669879.8754 | 1216143.8895 | 2669883.3535 | 1216139.9611 | 2669883.9769 | 1216139.2457 | 2669883.561 | 1216138.9147
28 | 2669917.5151 | 1216093.9769 | 2669917.7895 | 1216080.9496
29 | 2669917.5151 | 1216093.9769 | 2669916.8507 | 1216094.9475 | 2669914.8501 | 1216097.8481 | 2669924.445 | 1216106.4994 | 2669938.2581 | 1216118.6802 | 2669943.6389 | 1216123.4353 | 2669953.2556 | 1216132.1647 | 2669974.2355 | 1216150.2446 | 2669967.8212 | 1216157.207 | 2669945.1561 | 1216181.7789
30 | 2669917.5151 | 1216093.9769 | 2669921.5977 | 1216091.601 | 2669931.3911 | 1216081.3983
31 | 2669878.9194 | 1216044.1151 | 2669871.0415 | 1216052.2057 | 2669863.6273 | 1216060.2572 | 2669856.5589 | 1216068.6019
32 | 2669856.5589 | 1216068.6019 | 2669833.0186 | 1216048.1819
33 | 2669910.6954 | 1216017.7042 | 2669907.2551 | 1216014.5174 | 2669878.9194 | 1216044.1151
34 | 2669878.9194 | 1216044.1151 | 2669867.2715 | 1216023.6644
35 | 2669813.1225 | 1216030.923 | 2669833.0186 | 1216048.1819
36 | 2669945.1561 | 1216181.7789 | 2669929.8235 | 1216168.129
37 | 2669928.4467 | 1216059.8946 | 2669928.8465 | 1216073.7081 | 2669931.268 | 1216077.6501 | 2669931.3911 | 1216081.3983
38 | 2669968.6595 | 1216037.9636 | 2669970.2456 | 1216039.3275 | 2669972.7494 | 1216040.1463 | 2669975.3866 | 1216039.9438 | 2669977.7392 | 1216038.7596 | 2669979.4559 | 1216036.7673 | 2669979.8022 | 1216035.7263 | 2669986.5349 | 1216041.1087 | 2669992.9885 | 1216046.3322
39 | 2669992.9885 | 1216046.3322 | 2669994.5741 | 1216044.5052 | 2669998.3452 | 1216040.8583 | 2670000.5818 | 1216039.2057 | 2670001.7593 | 1216038.8409
40 | 2669968.6595 | 1216037.9636 | 2669963.9108 | 1216042.7442 | 2669962.7511 | 1216043.2087 | 2669956.1034 | 1216043.5198
41 | 2669967.3346 | 1216031.166 | 2669966.8541 | 1216032.6391 | 2669967.051 | 1216035.2652 | 2669968.246 | 1216037.6141 | 2669968.6595 | 1216037.9636
42 | 2670027.865 | 1216048.1762 | 2670009.5339 | 1216038.5882 | 2670004.8343 | 1216037.8882 | 2670001.7593 | 1216038.8409
43 | 2670027.865 | 1216048.1762 | 2670038.2299 | 1216035.2453 | 2670040.8113 | 1216032.0403
44 | 2670071.7572 | 1215987.1755 | 2670070.7425 | 1215988.2309 | 2670060.4567 | 1215998.9502 | 2670053.0306 | 1216006.69 | 2670060.5569 | 1216014.3166 | 2670052.9208 | 1216022.4876 | 2670049.6019 | 1216025.7729 | 2670045.2613 | 1216030.0691 | 2670044.5697 | 1216030.7614 | 2670040.8113 | 1216032.0403
45 | 2670071.7572 | 1215987.1755 | 2670056.7121 | 1215972.5672 | 2670045.0499 | 1215961.1123
46 | 2669910.6954 | 1216017.7042 | 2669907.2551 | 1216014.5174 | 2669919.3552 | 1216001.8735
47 | 2669910.6954 | 1216017.7042 | 2669921.7029 | 1216027.8759
48 | 2669887.7733 | 1216041.5061 | 2669910.6954 | 1216017.7042
49 | 2669857.0531 | 1216005.7235 | 2669867.2715 | 1216023.6644
50 | 2669967.3346 | 1216031.166 | 2669950.3735 | 1216015.2884
51 | 2669948.5564 | 1216002.7165 | 2669948.5564 | 1216002.7165 | 2669948.6996 | 1216011.8685 | 2669948.9377 | 1216013.5723 | 2669950.3154 | 1216015.234 | 2669950.3735 | 1216015.2884
52 | 2669951.1038 | 1216048.5148 | 2669956.1034 | 1216043.5198
53 | 2669936.2851 | 1215991.1319 | 2669933.0331 | 1215988.0696
54 | 2669936.2851 | 1215991.1319 | 2669948.5564 | 1216002.7165
55 | 2669933.0331 | 1215988.0696 | 2669938.5056 | 1215982.5419
56 | 2669933.0331 | 1215988.0696 | 2669919.3552 | 1216001.8735
57 | 2669928.4467 | 1216059.8946 | 2669925.315 | 1216056.9449 | 2669925.2146 | 1216046.0924 | 2669924.4217 | 1216044.065
58 | 2669887.7733 | 1216041.5061 | 2669894.6081 | 1216047.2454 | 2669894.588 | 1216048.9608
59 | 2670029.724 | 1215946.0586 | 2670045.0499 | 1215961.1123
60 | 2669997.9639 | 1215991.6496 | 2670016.8431 | 1216010.002
61 | 2669997.9639 | 1215991.6496 | 2669977.2658 | 1215971.529
62 | 2669919.3552 | 1216001.8735 | 2669890.382 | 1215969.8688
63 | 2669924.4217 | 1216044.065 | 2669921.1305 | 1216035.649 | 2669925.441 | 1216031.3302 | 2669921.7029 | 1216027.8759
64 | 2669949.5391 | 1215971.3971 | 2669938.5056 | 1215982.5419
65 | 2669949.5391 | 1215971.3971 | 2669941.304 | 1215957.953
66 | 2669931.3748 | 1215941.7431 | 2669941.304 | 1215957.953
67 | 2669949.5391 | 1215971.3971 | 2669959.5348 | 1215966.6225 | 2669963.7046 | 1215965.8821 | 2669967.4857 | 1215966.5602 | 2669972.485 | 1215968.2533 | 2669977.1781 | 1215971.4437 | 2669977.2658 | 1215971.529
68 | 2669886.8797 | 1215966 | 2669890.382 | 1215969.8688
69 | 2669884.435 | 1215963.2995 | 2669886.8797 | 1215966
70 | 2670029.724 | 1215946.0586 | 2670017.5227 | 1215934.0742
71 | 2670017.5227 | 1215934.0742 | 2670011.5475 | 1215928.2051
72 | 2669995.7261 | 1215913.3103 | 2670004.1505 | 1215920.9395 | 2670011.5475 | 1215928.2051
73 | 2669995.7261 | 1215913.3103 | 2669988.192 | 1215906.4874 | 2669983.1727 | 1215902.2347
74 | 2669983.1727 | 1215902.2347 | 2669973.7722 | 1215894.27
75 | 2669949.4812 | 1215875.608 | 2669950.8276 | 1215876.5189 | 2669971.9444 | 1215892.7213 | 2669973.7722 | 1215894.27
76 | 2669884.435 | 1215963.2995 | 2669883.1101 | 1215961.836
77 | 2669867.3877 | 1215939.0023 | 2669873.8487 | 1215949.4402 | 2669879.5582 | 1215957.9125 | 2669883.1101 | 1215961.836
78 | 2669867.3877 | 1215939.0023 | 2669867.3877 | 1215939.0023 | 2669862.2384 | 1215938.4417 | 2669841.283 | 1215914.9688
79 | 2669821.913 | 1215893.2719 | 2669841.283 | 1215914.9688
80 | 2669976.1546 | 1215867.0397 | 2669975.6834 | 1215868.0212
81 | 2669976.1546 | 1215867.0397 | 2669977.9469 | 1215863.3065 | 2669979.4671 | 1215854.1185 | 2669979.4671 | 1215854.1185
82 | 2669966.0895 | 1215884.3473 | 2669974.81 | 1215869.8405 | 2669975.6834 | 1215868.0212
83 | 2669977.2012 | 1215845.9757 | 2669977.2012 | 1215845.9757 | 2669979.4671 | 1215854.1185
84 | 2669966.0895 | 1215884.3473 | 2669937.5493 | 1215863.7605
85 | 2670016.1534 | 1215926.2949 | 2669991.291 | 1215904.467 | 2669966.0895 | 1215884.3473
86 | 2669977.2012 | 1215845.9757 | 2669973.8383 | 1215840.7218 | 2669969.5189 | 1215834.7896 | 2669968.0854 | 1215832.822
87 | 2669920.3903 | 1215852.259 | 2669925.9941 | 1215855.4254 | 2669937.5493 | 1215863.7605
88 | 2670016.1534 | 1215926.2949 | 2670047.6321 | 1215957.4711
89 | 2670016.1534 | 1215926.2949 | 2670028.0555 | 1215912.2845
90 | 2669956.6185 | 1215817.0831 | 2669968.0854 | 1215832.822
91 | 2669920.3903 | 1215852.259 | 2669905.0817 | 1215843.6089
92 | 2670032.132 | 1215907.6834 | 2670029.143 | 1215911.0044 | 2670028.0555 | 1215912.2845
93 | 2669956.6185 | 1215817.0831 | 2669949.9022 | 1215807.8646 | 2669944.7678 | 1215801.9933
94 | 2669788.1883 | 1215795.1617 | 2669789.3941 | 1215792.0516
95 | 2669788.1883 | 1215795.1617 | 2669853.7898 | 1215822.2581 | 2669867.9748 | 1215828.8219
96 | 2669789.3941 | 1215792.0516 | 2669873.1998 | 1215826.6703
97 | 2669867.9748 | 1215828.8219 | 2669886.5524 | 1215837.4182 | 2669890.3849 | 1215839.5568
98 | 2669873.1998 | 1215826.6703 | 2669878.9504 | 1215829.0458
99 | 2669898.1773 | 1215843.9052 | 2669890.3849 | 1215839.5568
100 | 2669878.9504 | 1215829.0458 | 2669880.2809 | 1215829.5953 | 2669890.3527 | 1215835.2864
101 | 2669900.923 | 1215845.4374 | 2669898.1773 | 1215843.9052
102 | 2669944.7678 | 1215801.9933 | 2669939.4069 | 1215795.863
103 | 2669937.6636 | 1215793.8695 | 2669939.4069 | 1215795.863
104 | 2669937.6636 | 1215793.8695 | 2669936.1876 | 1215792.1816
105 | 2669936.1876 | 1215792.1816 | 2669932.5615 | 1215788.0351
106 | 2669924.3568 | 1215859.004 | 2669930.3848 | 1215862.776
107 | 2669924.3568 | 1215859.004 | 2669917.1209 | 1215854.4763 | 2669900.923 | 1215845.4374
108 | 2669949.4812 | 1215875.608 | 2669932.1141 | 1215863.858 | 2669930.3848 | 1215862.776
109 | 2670064.1355 | 1215894.847 | 2670062.0311 | 1215893.4574 | 2670054.4291 | 1215892.2563
110 | 2670064.1355 | 1215894.847 | 2670069.1968 | 1215898.1891 | 2670076.1308 | 1215904.5005
111 | 2670054.1555 | 1215892.3188 | 2670054.4291 | 1215892.2563 | 2670054.4291 | 1215892.2563
112 | 2670225.5527 | 1216021.1842 | 2670225.5876 | 1216025.3095 | 2670224.5285 | 1216028.1988 | 2670220.8151 | 1216030.1563 | 2670214.3359 | 1216028.4122 | 2670206.8157 | 1216024.1432 | 2670196.9051 | 1216015.888 | 2670184.1207 | 1216004.0633 | 2670131.6079 | 1215955.5036 | 2670079.1214 | 1215907.2225 | 2670076.1308 | 1215904.5005
113 | 2670041.2531 | 1215897.5493 | 2670046.7924 | 1215894.001 | 2670054.1555 | 1215892.3188
114 | 2670225.5527 | 1216021.1842 | 2670223.8461 | 1216015.227 | 2670217.8505 | 1215995.6329 | 2670211.777 | 1215982.0083 | 2670203.9833 | 1215971.3097 | 2670185.2622 | 1215953.567 | 2670178.3687 | 1215945.7253 | 2670173.8286 | 1215935.3542 | 2670164.6646 | 1215910.753 | 2670153.4342 | 1215879.779 | 2670145.2994 | 1215858.0362 | 2670138.5611 | 1215840.8683 | 2670133.825 | 1215825.8364
115 | 2670041.2531 | 1215897.5493 | 2670041.2531 | 1215897.5493 | 2670032.132 | 1215907.6834
116 | 2670133.825 | 1215825.8364 | 2670101.0343 | 1215807.9075
117 | 2670067.0776 | 1215789.341 | 2670101.0343 | 1215807.9075
118 | 2669900.1723 | 1215840.8349 | 2669905.0817 | 1215843.6089
119 | 2669895.263 | 1215838.0609 | 2669900.1723 | 1215840.8349
120 | 2669895.263 | 1215838.0609 | 2669890.3527 | 1215835.2864
121 | 2670048.5594 | 1215779.2158 | 2670067.0776 | 1215789.341
122 | 2670048.5594 | 1215779.2158 | 2669994.9199 | 1215750.023 | 2669993.9107 | 1215749.4394
123 | 2670048.5594 | 1215779.2158 | 2670044.8171 | 1215785.5647 | 2670040.5092 | 1215788.3492 | 2670036.2127 | 1215789.5217 | 2670034.8158 | 1215789.3922
124 | 2669993.9107 | 1215749.4394 | 2669969.0056 | 1215735.0388
125 | 2670034.8158 | 1215789.3922 | 2670031.1305 | 1215789.0506 | 2670025.0449 | 1215786.7443 | 2670024.4896 | 1215786.4523
126 | 2669948.7947 | 1215723.3525 | 2669969.0056 | 1215735.0388
127 | 2670017.1508 | 1215782.5935 | 2670024.4896 | 1215786.4523
128 | 2669929.3609 | 1215784.3752 | 2669932.5615 | 1215788.0351
129 | 2669921.8908 | 1215775.8329 | 2669929.3609 | 1215784.3752
130 | 2669921.8908 | 1215775.8329 | 2669920.5513 | 1215774.3012
131 | 2669920.5513 | 1215774.3012 | 2669917.426 | 1215770.7273
132 | 2669913.7462 | 1215766.5194 | 2669917.426 | 1215770.7273

## bus_geodata
| x | y | coords
0 | 2669597.8561 | 1216133.8095
1 | 2669634.1175 | 1216177.7912
2 | 2669648.0514 | 1216186.8152
3 | 2669669.8789 | 1216140.6207
4 | 2669785.4888 | 1216057.967
5 | 2669806.1753 | 1216075.8457
6 | 2669656.0511 | 1216195.0317
7 | 2669665.4281 | 1216204.6629
8 | 2669672.4198 | 1216210.831
9 | 2669712.2115 | 1216245.9358
10 | 2669739.5171 | 1216225.4297
11 | 2669704.9852 | 1216239.5607
12 | 2669726.5721 | 1216152.368
13 | 2669728.5138 | 1216154.2663
14 | 2669688.7018 | 1216225.1952
15 | 2669828.3302 | 1216126.052
16 | 2669851.5043 | 1216146.0927
17 | 2669768.6635 | 1216193.5185
18 | 2669753.0785 | 1216210.5819
19 | 2669858.7697 | 1216207.1044
20 | 2669866.4782 | 1216159.042
21 | 2669877.8935 | 1216237.5159
22 | 2669825.3074 | 1216092.0935
23 | 2669849.1063 | 1216111.4889
24 | 2669865.5029 | 1216124.5432
25 | 2669879.8754 | 1216143.8895
26 | 2669917.5151 | 1216093.9769
27 | 2669883.561 | 1216138.9147
28 | 2669856.5589 | 1216068.6019
29 | 2669878.9194 | 1216044.1151
30 | 2669833.0186 | 1216048.1819
31 | 2669917.7895 | 1216080.9496
32 | 2669945.1561 | 1216181.7789
33 | 2669931.3911 | 1216081.3983
34 | 2669929.8235 | 1216168.129
35 | 2669992.9885 | 1216046.3322
36 | 2669968.6595 | 1216037.9636
37 | 2670001.7593 | 1216038.8409
38 | 2670027.865 | 1216048.1762
39 | 2670040.8113 | 1216032.0403
40 | 2670071.7572 | 1215987.1755
41 | 2669742.4783 | 1216167.9186
42 | 2669910.6954 | 1216017.7042
43 | 2669867.2715 | 1216023.6644
44 | 2669813.1225 | 1216030.923
45 | 2669967.3346 | 1216031.166
46 | 2669950.3735 | 1216015.2884
47 | 2669956.1034 | 1216043.5198
48 | 2669936.2851 | 1215991.1319
49 | 2669933.0331 | 1215988.0696
50 | 2669948.5564 | 1216002.7165
51 | 2669928.4467 | 1216059.8946
52 | 2669887.7733 | 1216041.5061
53 | 2669894.588 | 1216048.9608
54 | 2670045.0499 | 1215961.1123
55 | 2670016.8431 | 1216010.002
56 | 2669997.9639 | 1215991.6496
57 | 2669951.1038 | 1216048.5148
58 | 2669919.3552 | 1216001.8735
59 | 2669921.7029 | 1216027.8759
60 | 2669938.5056 | 1215982.5419
61 | 2669941.304 | 1215957.953
62 | 2669949.5391 | 1215971.3971
63 | 2669931.3748 | 1215941.7431
64 | 2669977.2658 | 1215971.529
65 | 2669857.0531 | 1216005.7235
66 | 2669890.382 | 1215969.8688
67 | 2669924.4217 | 1216044.065
68 | 2669886.8797 | 1215966
69 | 2670029.724 | 1215946.0586
70 | 2670017.5227 | 1215934.0742
71 | 2670011.5475 | 1215928.2051
72 | 2669995.7261 | 1215913.3103
73 | 2669983.1727 | 1215902.2347
74 | 2669973.7722 | 1215894.27
75 | 2669884.435 | 1215963.2995
76 | 2669883.1101 | 1215961.836
77 | 2669867.3877 | 1215939.0023
78 | 2669841.283 | 1215914.9688
79 | 2669821.913 | 1215893.2719
80 | 2669976.1546 | 1215867.0397
81 | 2669975.6834 | 1215868.0213
82 | 2669979.4671 | 1215854.1185
83 | 2669966.0895 | 1215884.3473
84 | 2669977.2012 | 1215845.9757
85 | 2669937.5493 | 1215863.7605
86 | 2670016.1534 | 1215926.2949
87 | 2669968.0854 | 1215832.822
88 | 2669920.3903 | 1215852.259
89 | 2670047.6321 | 1215957.4711
90 | 2670028.0555 | 1215912.2845
91 | 2669956.6185 | 1215817.0831
92 | 2669788.1883 | 1215795.1617
93 | 2669789.3941 | 1215792.0516
94 | 2669867.9748 | 1215828.8219
95 | 2669873.1998 | 1215826.6703
96 | 2669890.3849 | 1215839.5568
97 | 2669878.9504 | 1215829.0458
98 | 2669898.1773 | 1215843.9052
99 | 2669944.7678 | 1215801.9933
100 | 2669939.4069 | 1215795.863
101 | 2669937.6636 | 1215793.8695
102 | 2669936.1876 | 1215792.1816
103 | 2669924.3568 | 1215859.004
104 | 2669930.3848 | 1215862.776
105 | 2669900.923 | 1215845.4374
106 | 2669949.4812 | 1215875.608
107 | 2670064.1355 | 1215894.847
108 | 2670054.4291 | 1215892.2563
109 | 2670076.1308 | 1215904.5005
110 | 2670054.1555 | 1215892.3188
111 | 2670225.5527 | 1216021.1842
112 | 2670041.2531 | 1215897.5493
113 | 2670133.825 | 1215825.8364
114 | 2670032.132 | 1215907.6834
115 | 2670101.0343 | 1215807.9075
116 | 2669905.0817 | 1215843.6089
117 | 2669900.1723 | 1215840.8349
118 | 2669895.263 | 1215838.0609
119 | 2669890.3527 | 1215835.2864
120 | 2670067.0776 | 1215789.341
121 | 2670048.5594 | 1215779.2158
122 | 2669993.9107 | 1215749.4394
123 | 2670034.8158 | 1215789.3922
124 | 2669969.0056 | 1215735.0388
125 | 2670024.4895 | 1215786.4523
126 | 2669948.7947 | 1215723.3525
127 | 2670017.1508 | 1215782.5935
128 | 2669932.5615 | 1215788.0351
129 | 2669929.3609 | 1215784.3752
130 | 2669921.8908 | 1215775.8329
131 | 2669920.5513 | 1215774.3012
132 | 2669917.426 | 1215770.7273
133 | 2669913.7462 | 1215766.5194
134 | 2669907.2551 | 1216014.5174

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97062 | -0.5676 | 0.0072218 | 0.0018099
1 | 0.97102 | -0.55967 | 0 | 0
2 | 0.97121 | -0.55602 | 0 | 0
3 | 0.97088 | -0.56257 | 0.0030343 | 0.00076046
4 | 0.97713 | -0.43946 | 0.00016478 | 4.1298e-05
5 | 0.97714 | -0.43938 | 0.0062705 | 0.0015715
6 | 0.97132 | -0.55385 | 0.0016719 | 0.00041902
7 | 0.97147 | -0.55088 | 0 | 0
8 | 0.97157 | -0.54883 | 0.0016733 | 0.00041937
9 | 0.97231 | -0.53424 | 0 | 0
10 | 0.97294 | -0.52177 | 0.0010683 | 0.00026773
11 | 0.97216 | -0.53725 | 0.0016723 | 0.00041912
12 | 0.97334 | -0.51388 | 0.0046061 | 0.0011544
13 | 0.97335 | -0.51365 | 0.0014815 | 0.00037129
14 | 0.97185 | -0.54338 | 0.0016731 | 0.00041931
15 | 0.97609 | -0.45992 | 0 | 0
16 | 0.97689 | -0.44417 | 0.012253 | 0.003071
17 | 0.97372 | -0.50637 | 0 | 0
18 | 0.97328 | -0.5151 | 0.0025258 | 0.00063302
19 | 0.97648 | -0.45216 | 0 | 0
20 | 0.97763 | -0.42958 | 0 | 0
21 | 0.97579 | -0.46574 | 0.02 | 0.0050125
22 | 0.97729 | -0.43643 | 0.0064462 | 0.0016156
23 | 0.97766 | -0.42922 | 0.0080206 | 0.0020102
24 | 0.97806 | -0.42123 | 0.00361 | 0.00090475
25 | 0.97877 | -0.40734 | 0 | 0
26 | 0.9885 | -0.2188 | 0 | 0
27 | 0.97859 | -0.41093 | 0.0048051 | 0.0012043
28 | 0.99741 | -0.049514 | 0 | 0
29 | 0.99781 | -0.041847 | 0 | 0
30 | 0.99704 | -0.056729 | 0.0065924 | 0.0016522
31 | 0.98839 | -0.22092 | 0.0091437 | 0.0022916
32 | 0.98603 | -0.26689 | 0 | 0
33 | 0.9906 | -0.17848 | 0.013054 | 0.0032717
34 | 0.98563 | -0.2747 | 0.021207 | 0.0053151
35 | 0.99511 | -0.092871 | 0 | 0
36 | 0.99621 | -0.072007 | 0 | 0
37 | 0.99469 | -0.10083 | 0.013497 | 0.0033827
38 | 0.99376 | -0.11869 | 0 | 0
39 | 0.99308 | -0.1316 | 0 | 0
40 | 0.99097 | -0.17202 | 0 | 0
41 | 0.97346 | -0.51147 | 0.0014815 | 0.00037129
42 | 0.99905 | -0.018023 | 0 | 0
43 | 0.99745 | -0.0487 | 0.0086324 | 0.0021635
44 | 0.99688 | -0.059785 | 0.0066167 | 0.0016583
45 | 0.99651 | -0.066295 | 0 | 0
46 | 0.99746 | -0.048283 | 0.0053308 | 0.001336
47 | 0.99591 | -0.077666 | 0.0080897 | 0.0020275
48 | 0.99877 | -0.023376 | 0 | 0
49 | 0.99897 | -0.019561 | 0 | 0
50 | 0.99801 | -0.037827 | 0.01369 | 0.003431
51 | 0.99334 | -0.12614 | 0 | 0
52 | 0.9987 | -0.024618 | 0 | 0
53 | 0.99859 | -0.026745 | 0.011438 | 0.0028666
54 | 0.98975 | -0.19545 | 0.0047864 | 0.0011996
55 | 0.99786 | -0.040975 | 0.0017668 | 0.00044279
56 | 0.9979 | -0.04016 | 0.0038755 | 0.0009713
57 | 0.99582 | -0.079393 | 0.013909 | 0.003486
58 | 1 | 0 | -0.46451 | -0.11813
59 | 0.99804 | -0.037009 | 0.0083571 | 0.0020945
60 | 0.99872 | -0.024343 | 0.00822 | 0.0020601
61 | 0.9981 | -0.03627 | 0.0082199 | 0.0020601
62 | 0.99834 | -0.031738 | 0 | 0
63 | 0.99796 | -0.039002 | 0.0082143 | 0.0020587
64 | 0.99805 | -0.037309 | 0.0048921 | 0.0012261
65 | 0.9973 | -0.051591 | 0.0079927 | 0.0020032
66 | 0.99843 | -0.030223 | 0.002069 | 0.00051853
67 | 0.99548 | -0.085476 | 0.00346 | 0.00086716
68 | 0.99825 | -0.033694 | 0.0020747 | 0.00051997
69 | 0.98907 | -0.2085 | 0.0031295 | 0.00078432
70 | 0.98854 | -0.21867 | 0.0024234 | 0.00060736
71 | 0.98829 | -0.22356 | 0.0024216 | 0.00060691
72 | 0.98764 | -0.23604 | 0.0030191 | 0.00075667
73 | 0.98715 | -0.24543 | 0.0020682 | 0.00051834
74 | 0.9868 | -0.25224 | 0.0028981 | 0.00072634
75 | 0.99813 | -0.035986 | 0.0083045 | 0.0020813
76 | 0.99808 | -0.036941 | 0.0023659 | 0.00059295
77 | 0.99744 | -0.049242 | 0.0085014 | 0.0021306
78 | 0.99688 | -0.060024 | 0.0094175 | 0.0023602
79 | 0.99668 | -0.063783 | 0.0073664 | 0.0018462
80 | 0.97757 | -0.43193 | 0.0020912 | 0.0005241
81 | 0.9776 | -0.43146 | 0.0022314 | 0.00055923
82 | 0.9773 | -0.43719 | 0.0012737 | 0.00031921
83 | 0.97805 | -0.42257 | 0 | 0
84 | 0.97715 | -0.4403 | 0.0017362 | 0.00043513
85 | 0.97866 | -0.41067 | 0.0031922 | 0.00080005
86 | 0.97731 | -0.437 | 0 | 0
87 | 0.97687 | -0.44568 | 0.001509 | 0.0003782
88 | 0.97903 | -0.40339 | 0.0013469 | 0.00033757
89 | 0.97707 | -0.44173 | 0.0058503 | 0.0014662
90 | 0.97713 | -0.44057 | 0.0032514 | 0.00081489
91 | 0.97657 | -0.4517 | 0.0027252 | 0.00068299
92 | 0.98195 | -0.34623 | 0 | 0
93 | 0.98189 | -0.34754 | 0 | 0
94 | 0.98371 | -0.31204 | 0.0036816 | 0.0009227
95 | 0.98005 | -0.38347 | 0.0018195 | 0.00045601
96 | 0.98424 | -0.30183 | 0.0021105 | 0.00052893
97 | 0.97992 | -0.38589 | 0.0018194 | 0.00045598
98 | 0.98443 | -0.29809 | 0.0030177 | 0.00075631
99 | 0.97631 | -0.45668 | 0.0020315 | 0.00050915
100 | 0.97622 | -0.45849 | 0.00108 | 0.00027066
101 | 0.9762 | -0.45902 | 0.0015177 | 0.00038037
102 | 0.97618 | -0.45941 | 0.0011984 | 0.00030035
103 | 0.98515 | -0.28415 | 0.0040894 | 0.0010249
104 | 0.98533 | -0.28072 | 0.0082135 | 0.0020585
105 | 0.9845 | -0.29673 | 0.0070273 | 0.0017612
106 | 0.98595 | -0.26878 | 0.0048954 | 0.0012269
107 | 0.97681 | -0.44694 | 0.001325 | 0.00033209
108 | 0.97687 | -0.44566 | 0.0017453 | 0.00043742
109 | 0.97671 | -0.44878 | 0.0012892 | 0.0003231
110 | 0.97687 | -0.44563 | 0.001281 | 0.00032106
111 | 0.97554 | -0.47192 | 0 | 0
112 | 0.97697 | -0.44366 | 0.0013605 | 0.00034097
113 | 0.97385 | -0.5051 | 0 | 0
114 | 0.97708 | -0.44168 | 0.0075758 | 0.0018987
115 | 0.97299 | -0.52212 | 0.0050541 | 0.0012667
116 | 0.97935 | -0.39709 | 0.0012592 | 0.0003156
117 | 0.97945 | -0.39504 | 0.0012592 | 0.0003156
118 | 0.97956 | -0.39296 | 0.0012592 | 0.0003156
119 | 0.97967 | -0.39084 | 0.0012594 | 0.00031564
120 | 0.97228 | -0.53618 | 0.0049443 | 0.0012392
121 | 0.97199 | -0.54193 | 0 | 0
122 | 0.97164 | -0.5488 | 0.0021933 | 0.0005497
123 | 0.97183 | -0.54491 | 0.0019302 | 0.00048376
124 | 0.97154 | -0.55081 | 0.0018944 | 0.00047479
125 | 0.97177 | -0.54628 | 0.0012584 | 0.00031539
126 | 0.9715 | -0.55162 | 0.0018876 | 0.00047308
127 | 0.97172 | -0.54714 | 0.0056004 | 0.0014036
128 | 0.97613 | -0.46026 | 0.00083415 | 0.00020906
129 | 0.9761 | -0.46093 | 0.00087125 | 0.00021836
130 | 0.97603 | -0.4623 | 0.0023692 | 0.00059377
131 | 0.97602 | -0.46246 | 0.00083939 | 0.00021037
132 | 0.97601 | -0.46276 | 0.0008951 | 0.00022433
133 | 0.97599 | -0.46302 | 0.0025427 | 0.00063726
134 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0072218 | -0.0018099 | 0.0072245 | 0.001811 | 2.7281e-06 | 1.0121e-06 | 0.011071 | 0.011071 | 0.011071 | 0.97062 | -0.5676 | 0.97102 | -0.55967 | 3.0416
1 | -0.010259 | -0.0025711 | 0.010261 | 0.002572 | 1.7861e-06 | 9.0469e-07 | 0.015721 | 0.015721 | 0.015721 | 0.97102 | -0.55967 | 0.97121 | -0.55602 | 4.319
2 | 0.0030347 | 0.00076009 | -0.0030343 | -0.00076046 | 4.183e-07 | -3.7024e-07 | 0.0046503 | 0.0046505 | 0.0046505 | 0.97102 | -0.55967 | 0.97088 | -0.56257 | 1.2776
3 | -0.010261 | -0.002572 | 0.010262 | 0.0025725 | 1.0629e-06 | 5.3831e-07 | 0.015721 | 0.015721 | 0.015721 | 0.97121 | -0.55602 | 0.97132 | -0.55385 | 4.319
4 | -0.00016478 | -4.1298e-05 | 0.00016478 | 4.0956e-05 | 6.4537e-10 | -3.4211e-07 | 0.00025094 | 0.00025081 | 0.00025094 | 0.97713 | -0.43946 | 0.97714 | -0.43938 | 0.068938
5 | -0.0064353 | -0.0016125 | 0.0064362 | 0.0016128 | 9.0393e-07 | 2.6405e-07 | 0.0097997 | 0.0097996 | 0.0097997 | 0.97714 | -0.43938 | 0.97729 | -0.43643 | 2.6922
6 | -0.011934 | -0.0029915 | 0.011936 | 0.0029924 | 1.6849e-06 | 9.119e-07 | 0.018282 | 0.018282 | 0.018282 | 0.97132 | -0.55385 | 0.97147 | -0.55088 | 5.0227
7 | -0.011936 | -0.0029924 | 0.011937 | 0.0029931 | 1.1686e-06 | 6.3248e-07 | 0.018282 | 0.018282 | 0.018282 | 0.97147 | -0.55088 | 0.97157 | -0.54883 | 5.0226
8 | -0.01361 | -0.0034124 | 0.013614 | 0.0034144 | 3.5379e-06 | 1.9953e-06 | 0.020845 | 0.020845 | 0.020845 | 0.97157 | -0.54883 | 0.97185 | -0.54338 | 5.7267
9 | -0.016966 | -0.0042569 | 0.016976 | 0.0042628 | 1.0092e-05 | 5.9636e-06 | 0.025966 | 0.025966 | 0.025966 | 0.97231 | -0.53424 | 0.97294 | -0.52177 | 7.1336
10 | 0.016966 | 0.0042569 | -0.016963 | -0.0042554 | 2.4365e-06 | 1.4399e-06 | 0.025966 | 0.025966 | 0.025966 | 0.97231 | -0.53424 | 0.97216 | -0.53725 | 7.1336
11 | -0.018044 | -0.0045306 | 0.01805 | 0.004534 | 5.7442e-06 | 3.4265e-06 | 0.0276 | 0.0276 | 0.0276 | 0.97294 | -0.52177 | 0.97328 | -0.5151 | 7.5824
12 | 0.015291 | 0.0038363 | -0.015287 | -0.0038337 | 4.4613e-06 | 2.5861e-06 | 0.023407 | 0.023407 | 0.023407 | 0.97216 | -0.53725 | 0.97185 | -0.54338 | 6.4304
13 | -0.0046061 | -0.0011544 | 0.0046061 | 0.0011544 | 5.0492e-08 | -1.437e-09 | 0.0070416 | 0.0070416 | 0.0070416 | 0.97334 | -0.51388 | 0.97335 | -0.51365 | 1.9345
14 | -0.0060876 | -0.0015257 | 0.0060882 | 0.0015258 | 6.3427e-07 | 1.6317e-07 | 0.0093064 | 0.0093063 | 0.0093064 | 0.97335 | -0.51365 | 0.97346 | -0.51147 | 2.5567
15 | -0.028218 | -0.007109 | 0.02824 | 0.0071222 | 2.1275e-05 | 1.3232e-05 | 0.043032 | 0.043031 | 0.043032 | 0.97609 | -0.45992 | 0.97689 | -0.44417 | 11.8218
16 | 0.028218 | 0.007109 | -0.028156 | -0.0070701 | 6.2542e-05 | 3.8904e-05 | 0.043032 | 0.043032 | 0.043032 | 0.97609 | -0.45992 | 0.97372 | -0.50637 | 11.822
17 | -0.040493 | -0.010193 | 0.040521 | 0.010211 | 2.8257e-05 | 1.7837e-05 | 0.061696 | 0.061696 | 0.061696 | 0.97689 | -0.44417 | 0.97763 | -0.42958 | 16.9494
18 | 0.020584 | 0.0051722 | -0.020576 | -0.005167 | 8.5778e-06 | 5.2025e-06 | 0.031461 | 0.031461 | 0.031461 | 0.97372 | -0.50637 | 0.97328 | -0.5151 | 8.6432
19 | 0.0075715 | 0.0018979 | -0.0075697 | -0.0018971 | 1.8385e-06 | 7.2128e-07 | 0.011571 | 0.011571 | 0.011571 | 0.97372 | -0.50637 | 0.97346 | -0.51147 | 3.1788
20 | -0.020013 | -0.0050203 | 0.020035 | 0.0050334 | 2.1562e-05 | 1.3025e-05 | 0.030499 | 0.030498 | 0.030499 | 0.97648 | -0.45216 | 0.97763 | -0.42958 | 8.3787
21 | 0.020013 | 0.0050203 | -0.02 | -0.0050125 | 1.2949e-05 | 7.8235e-06 | 0.030499 | 0.030499 | 0.030499 | 0.97648 | -0.45216 | 0.97579 | -0.46574 | 8.3788
22 | -0.060556 | -0.015244 | 0.06062 | 0.015285 | 6.4468e-05 | 4.1006e-05 | 0.092194 | 0.092194 | 0.092194 | 0.97763 | -0.42958 | 0.97877 | -0.40734 | 25.3281
23 | -0.012882 | -0.0032283 | 0.012887 | 0.0032308 | 4.4298e-06 | 2.4502e-06 | 0.019615 | 0.019614 | 0.019615 | 0.97729 | -0.43643 | 0.97766 | -0.42922 | 5.3886
24 | -0.020907 | -0.0052409 | 0.020915 | 0.0052458 | 7.9589e-06 | 4.8308e-06 | 0.031822 | 0.031822 | 0.031822 | 0.97766 | -0.42922 | 0.97806 | -0.42123 | 8.7423
25 | -0.024525 | -0.0061505 | 0.024538 | 0.006158 | 1.205e-05 | 7.4223e-06 | 0.037314 | 0.037314 | 0.037314 | 0.97806 | -0.42123 | 0.97859 | -0.41093 | 10.2512
26 | -0.089968 | -0.022651 | 0.090787 | 0.023173 | 0.00081893 | 0.00052264 | 0.13681 | 0.13681 | 0.13681 | 0.97877 | -0.40734 | 0.9885 | -0.2188 | 37.5865
27 | 0.029348 | 0.0073654 | -0.029343 | -0.0073622 | 5.0229e-06 | 3.1301e-06 | 0.044621 | 0.044621 | 0.044621 | 0.97877 | -0.40734 | 0.97859 | -0.41093 | 12.2584
28 | 0.0091446 | 0.0022921 | -0.0091437 | -0.0022916 | 9.2613e-07 | 4.2567e-07 | 0.013766 | 0.013766 | 0.013766 | 0.9885 | -0.2188 | 0.98839 | -0.22092 | 3.7818
29 | 0.021264 | 0.0053494 | -0.021215 | -0.0053198 | 4.874e-05 | 2.9572e-05 | 0.032016 | 0.032017 | 0.032017 | 0.9885 | -0.2188 | 0.98603 | -0.26689 | 8.7958
30 | -0.1212 | -0.030815 | 0.12143 | 0.030966 | 0.00023588 | 0.00015072 | 0.1826 | 0.1826 | 0.1826 | 0.9885 | -0.2188 | 0.9906 | -0.17848 | 50.1637
31 | -0.013215 | -0.0033133 | 0.013219 | 0.003316 | 4.8295e-06 | 2.6583e-06 | 0.019715 | 0.019715 | 0.019715 | 0.99741 | -0.049514 | 0.99781 | -0.041847 | 5.4163
32 | 0.013215 | 0.0033133 | -0.01321 | -0.0033108 | 4.5423e-06 | 2.5005e-06 | 0.019715 | 0.019715 | 0.019715 | 0.99741 | -0.049514 | 0.99704 | -0.056729 | 5.4163
33 | -0.029851 | -0.0074862 | 0.029885 | 0.0075073 | 3.3938e-05 | 2.1123e-05 | 0.044518 | 0.044518 | 0.044518 | 0.99781 | -0.041847 | 0.99905 | -0.018023 | 12.2303
34 | 0.016632 | 0.0041703 | -0.016626 | -0.0041671 | 5.4296e-06 | 3.1676e-06 | 0.024803 | 0.024803 | 0.024803 | 0.99781 | -0.041847 | 0.99745 | -0.0487 | 6.8141
35 | 0.0066177 | 0.0016586 | -0.0066167 | -0.0016583 | 9.6347e-07 | 2.7318e-07 | 0.0098765 | 0.0098766 | 0.0098766 | 0.99704 | -0.056729 | 0.99688 | -0.059785 | 2.7134
36 | 0.021215 | 0.0053198 | -0.021207 | -0.0053151 | 7.8912e-06 | 4.7886e-06 | 0.032017 | 0.032017 | 0.032017 | 0.98603 | -0.26689 | 0.98563 | -0.2747 | 8.7959
37 | -0.13449 | -0.034237 | 0.13483 | 0.034455 | 0.00034032 | 0.00021752 | 0.2022 | 0.2022 | 0.2022 | 0.9906 | -0.17848 | 0.99334 | -0.12614 | 55.5507
38 | -0.15671 | -0.039999 | 0.15687 | 0.040099 | 0.00015815 | 9.9624e-05 | 0.23459 | 0.23459 | 0.23459 | 0.99511 | -0.092871 | 0.99621 | -0.072007 | 16.1119
39 | 0.15671 | 0.039999 | -0.15665 | -0.039961 | 6.0254e-05 | 3.7956e-05 | 0.23459 | 0.23459 | 0.23459 | 0.99511 | -0.092871 | 0.99469 | -0.10083 | 16.112
40 | 0.022006 | 0.0055177 | -0.022 | -0.0055141 | 5.9329e-06 | 3.6065e-06 | 0.032871 | 0.032871 | 0.032871 | 0.99621 | -0.072007 | 0.99591 | -0.077666 | 9.0304
41 | -0.17887 | -0.045617 | 0.17892 | 0.045648 | 4.9346e-05 | 3.1198e-05 | 0.26746 | 0.26746 | 0.26746 | 0.99621 | -0.072007 | 0.99651 | -0.066295 | 18.3695
42 | 0.14315 | 0.036579 | -0.14303 | -0.036501 | 0.0001235 | 7.7553e-05 | 0.2144 | 0.2144 | 0.2144 | 0.99469 | -0.10083 | 0.99376 | -0.11869 | 14.7253
43 | 0.14303 | 0.036501 | -0.14294 | -0.036445 | 8.9151e-05 | 5.5986e-05 | 0.2144 | 0.2144 | 0.2144 | 0.99376 | -0.11869 | 0.99308 | -0.1316 | 14.7253
44 | 0.14294 | 0.036445 | -0.14266 | -0.03627 | 0.00027831 | 0.00017479 | 0.2144 | 0.2144 | 0.2144 | 0.99308 | -0.1316 | 0.99097 | -0.17202 | 14.7254
45 | 0.14266 | 0.03627 | -0.1425 | -0.036169 | 0.00016082 | 0.000101 | 0.2144 | 0.2144 | 0.2144 | 0.99097 | -0.17202 | 0.98975 | -0.19545 | 14.7254
46 | -0.1887 | -0.048258 | 0.18886 | 0.048362 | 0.00016473 | 0.00010426 | 0.2814 | 0.2814 | 0.2814 | 0.99905 | -0.018023 | 1 | 0 | 19.3267
47 | 0.14737 | 0.037881 | -0.14724 | -0.037795 | 0.00013581 | 8.6526e-05 | 0.21984 | 0.21984 | 0.21984 | 0.99905 | -0.018023 | 0.99804 | -0.037009 | 30.1973
48 | 0.011443 | 0.0028691 | -0.011439 | -0.0028672 | 3.5952e-06 | 1.8689e-06 | 0.017044 | 0.017044 | 0.017044 | 0.99905 | -0.018023 | 0.9987 | -0.024618 | 4.6824
49 | 0.0079938 | 0.0020036 | -0.0079927 | -0.0020032 | 1.1011e-06 | 4.3526e-07 | 0.011925 | 0.011925 | 0.011925 | 0.99745 | -0.0487 | 0.9973 | -0.051591 | 3.2762
50 | -0.17892 | -0.045648 | 0.17908 | 0.045746 | 0.00015581 | 9.8506e-05 | 0.26746 | 0.26746 | 0.26746 | 0.99651 | -0.066295 | 0.99746 | -0.048283 | 18.3695
51 | -0.18441 | -0.047082 | 0.1845 | 0.047141 | 9.3238e-05 | 5.8987e-05 | 0.27541 | 0.27541 | 0.27541 | 0.99746 | -0.048283 | 0.99801 | -0.037827 | 18.9156
52 | 0.01391 | 0.0034866 | -0.013909 | -0.003486 | 1.1448e-06 | 6.4073e-07 | 0.020784 | 0.020784 | 0.020784 | 0.99591 | -0.077666 | 0.99582 | -0.079393 | 5.7099
53 | -0.19833 | -0.05066 | 0.19837 | 0.050683 | 3.6591e-05 | 2.3184e-05 | 0.29582 | 0.29582 | 0.29582 | 0.99877 | -0.023376 | 0.99897 | -0.019561 | 20.3175
54 | 0.19833 | 0.05066 | -0.19819 | -0.050573 | 0.00013845 | 8.7726e-05 | 0.29582 | 0.29582 | 0.29582 | 0.99877 | -0.023376 | 0.99801 | -0.037827 | 20.3175
55 | 0.035214 | 0.0088337 | -0.035206 | -0.0088287 | 8.0264e-06 | 5.0351e-06 | 0.052457 | 0.052457 | 0.052457 | 0.99897 | -0.019561 | 0.99872 | -0.024343 | 14.4112
56 | -0.23358 | -0.059517 | 0.2338 | 0.059657 | 0.00022069 | 0.00014022 | 0.34828 | 0.34828 | 0.34828 | 0.99897 | -0.019561 | 1 | 0 | 23.9202
57 | -0.13483 | -0.034455 | 0.13509 | 0.034625 | 0.00026574 | 0.00016985 | 0.2022 | 0.2022 | 0.2022 | 0.99334 | -0.12614 | 0.99548 | -0.085476 | 55.5507
58 | 0.011439 | 0.0028672 | -0.011438 | -0.0028666 | 1.1591e-06 | 6.0263e-07 | 0.017044 | 0.017044 | 0.017044 | 0.9987 | -0.024618 | 0.99859 | -0.026745 | 4.6824
59 | 0.13771 | 0.03497 | -0.13763 | -0.034916 | 8.6469e-05 | 5.4237e-05 | 0.20721 | 0.20721 | 0.20721 | 0.98975 | -0.19545 | 0.98907 | -0.2085 | 14.2312
60 | -0.0017668 | -0.00044279 | 0.0017668 | 0.00044249 | 6.8531e-08 | -3.001e-07 | 0.0026346 | 0.0026345 | 0.0026346 | 0.99786 | -0.040975 | 0.9979 | -0.04016 | 0.72379
61 | -0.0056423 | -0.0014138 | 0.0056431 | 0.0014139 | 7.6624e-07 | 1.1322e-07 | 0.0084135 | 0.0084133 | 0.0084135 | 0.9979 | -0.04016 | 0.99805 | -0.037309 | 2.3114
62 | 0.040194 | 0.010108 | -0.040136 | -0.010072 | 5.7934e-05 | 3.6512e-05 | 0.059821 | 0.059821 | 0.059821 | 1 | 0 | 0.99843 | -0.030223 | 16.4343
63 | 0.13888 | 0.0357 | -0.13855 | -0.035492 | 0.00032622 | 0.00020852 | 0.20738 | 0.20738 | 0.20738 | 0.99804 | -0.037009 | 0.99548 | -0.085476 | 56.9715
64 | 0.026986 | 0.0067686 | -0.026977 | -0.0067627 | 9.5084e-06 | 5.8802e-06 | 0.040209 | 0.040209 | 0.040209 | 0.99872 | -0.024343 | 0.99834 | -0.031738 | 11.0466
65 | -0.016435 | -0.0041192 | 0.016439 | 0.0041213 | 3.5495e-06 | 2.0656e-06 | 0.024503 | 0.024502 | 0.024503 | 0.9981 | -0.03627 | 0.99834 | -0.031738 | 6.7315
66 | 0.0082154 | 0.0020591 | -0.0082143 | -0.0020587 | 1.0694e-06 | 4.3599e-07 | 0.012248 | 0.012248 | 0.012248 | 0.9981 | -0.03627 | 0.99796 | -0.039002 | 3.3649
67 | 0.010538 | 0.0026414 | -0.010535 | -0.00264 | 2.7967e-06 | 1.3947e-06 | 0.015707 | 0.015707 | 0.015707 | 0.99834 | -0.031738 | 0.99805 | -0.037309 | 4.3151
68 | 0.038067 | 0.0095532 | -0.03806 | -0.0095492 | 6.2998e-06 | 3.9636e-06 | 0.056737 | 0.056738 | 0.056738 | 0.99843 | -0.030223 | 0.99825 | -0.033694 | 15.5872
69 | 0.035986 | 0.0090292 | -0.035982 | -0.0090268 | 3.9312e-06 | 2.4683e-06 | 0.053645 | 0.053645 | 0.053645 | 0.99825 | -0.033694 | 0.99813 | -0.035986 | 14.7376
70 | 0.1345 | 0.034131 | -0.13443 | -0.03409 | 6.5747e-05 | 4.1201e-05 | 0.2025 | 0.2025 | 0.2025 | 0.98907 | -0.2085 | 0.98854 | -0.21867 | 13.9079
71 | 0.13201 | 0.033483 | -0.13198 | -0.033463 | 3.1048e-05 | 1.9442e-05 | 0.19885 | 0.19885 | 0.19885 | 0.98854 | -0.21867 | 0.98829 | -0.22356 | 13.6573
72 | 0.12956 | 0.032856 | -0.12948 | -0.032808 | 7.7641e-05 | 4.8577e-05 | 0.1952 | 0.19521 | 0.19521 | 0.98829 | -0.22356 | 0.98764 | -0.23604 | 13.4069
73 | 0.12646 | 0.032051 | -0.1264 | -0.032015 | 5.7057e-05 | 3.566e-05 | 0.19066 | 0.19066 | 0.19066 | 0.98764 | -0.23604 | 0.98715 | -0.24543 | 13.0946
74 | 0.12433 | 0.031497 | -0.12429 | -0.031472 | 4.0625e-05 | 2.537e-05 | 0.18754 | 0.18754 | 0.18754 | 0.98715 | -0.24543 | 0.9868 | -0.25224 | 12.8804
75 | 0.1214 | 0.030745 | -0.1213 | -0.030685 | 9.6369e-05 | 6.0112e-05 | 0.18317 | 0.18317 | 0.18317 | 0.9868 | -0.25224 | 0.98595 | -0.26878 | 12.5803
76 | 0.027677 | 0.0069454 | -0.027676 | -0.0069447 | 1.2605e-06 | 7.8093e-07 | 0.041265 | 0.041265 | 0.041265 | 0.99813 | -0.035986 | 0.99808 | -0.036941 | 11.3364
77 | 0.02531 | 0.0063517 | -0.025295 | -0.0063426 | 1.4838e-05 | 9.1335e-06 | 0.037737 | 0.037737 | 0.037737 | 0.99808 | -0.036941 | 0.99744 | -0.049242 | 10.3674
78 | 0.016794 | 0.0042119 | -0.016785 | -0.0042069 | 8.6265e-06 | 5.0429e-06 | 0.025055 | 0.025055 | 0.025055 | 0.99744 | -0.049242 | 0.99688 | -0.060024 | 6.8832
79 | 0.0073678 | 0.0018467 | -0.0073664 | -0.0018462 | 1.3192e-06 | 4.6517e-07 | 0.010998 | 0.010998 | 0.010998 | 0.99688 | -0.060024 | 0.99668 | -0.063783 | 3.0214
80 | -0.023539 | -0.0059071 | 0.023539 | 0.0059074 | 5.2423e-07 | 3.2186e-07 | 0.035832 | 0.035832 | 0.035832 | 0.97757 | -0.43193 | 0.9776 | -0.43146 | 9.844
81 | 0.021447 | 0.005383 | -0.021442 | -0.0053797 | 5.378e-06 | 3.2733e-06 | 0.032649 | 0.032649 | 0.032649 | 0.97757 | -0.43193 | 0.9773 | -0.43719 | 8.9695
82 | -0.02577 | -0.0064666 | 0.025781 | 0.0064734 | 1.0932e-05 | 6.759e-06 | 0.039228 | 0.039228 | 0.039228 | 0.9776 | -0.43146 | 0.97805 | -0.42257 | 10.777
83 | 0.020168 | 0.0050605 | -0.020165 | -0.0050587 | 2.9892e-06 | 1.8072e-06 | 0.03071 | 0.03071 | 0.03071 | 0.9773 | -0.43719 | 0.97715 | -0.4403 | 8.4368
84 | -0.074385 | -0.018689 | 0.074428 | 0.018714 | 4.2266e-05 | 2.5282e-05 | 0.11319 | 0.11319 | 0.11319 | 0.97805 | -0.42257 | 0.97866 | -0.41067 | 7.7738
85 | 0.048604 | 0.012215 | -0.04857 | -0.012197 | 3.3447e-05 | 1.8135e-05 | 0.073959 | 0.07396 | 0.07396 | 0.97805 | -0.42257 | 0.97731 | -0.437 | 5.0797
86 | 0.018429 | 0.0046236 | -0.018424 | -0.0046207 | 4.7293e-06 | 2.8262e-06 | 0.028066 | 0.028066 | 0.028066 | 0.97715 | -0.4403 | 0.97687 | -0.44568 | 7.7104
87 | -0.07762 | -0.019514 | 0.077647 | 0.01953 | 2.7019e-05 | 1.6252e-05 | 0.11804 | 0.11804 | 0.11804 | 0.97866 | -0.41067 | 0.97903 | -0.40339 | 8.1072
88 | 0.0058516 | 0.0014665 | -0.0058503 | -0.0014662 | 1.3188e-06 | 2.8901e-07 | 0.0089094 | 0.0089096 | 0.0089096 | 0.97731 | -0.437 | 0.97707 | -0.44173 | 2.4477
89 | 0.042719 | 0.010731 | -0.042712 | -0.010727 | 7.293e-06 | 3.7462e-06 | 0.065051 | 0.065051 | 0.065051 | 0.97731 | -0.437 | 0.97713 | -0.44057 | 4.4678
90 | 0.016915 | 0.0042425 | -0.016911 | -0.0042397 | 4.8485e-06 | 2.8593e-06 | 0.025767 | 0.025767 | 0.025767 | 0.97687 | -0.44568 | 0.97657 | -0.4517 | 7.079
91 | -0.078994 | -0.019868 | 0.079017 | 0.019882 | 2.3772e-05 | 1.4329e-05 | 0.12009 | 0.12009 | 0.12009 | 0.97903 | -0.40339 | 0.97935 | -0.39709 | 8.2477
92 | 0.03946 | 0.0099121 | -0.039458 | -0.0099111 | 2.0817e-06 | 1.0243e-06 | 0.0601 | 0.0601 | 0.0601 | 0.97713 | -0.44057 | 0.97708 | -0.44168 | 4.1277
93 | 0.014185 | 0.0035567 | -0.014182 | -0.0035548 | 3.3649e-06 | 1.9133e-06 | 0.021615 | 0.021615 | 0.021615 | 0.97657 | -0.4517 | 0.97631 | -0.45668 | 5.9382
94 | 0.087904 | 0.022185 | -0.087899 | -0.022182 | 5.5524e-06 | 3.3848e-06 | 0.13326 | 0.13326 | 0.13326 | 0.98195 | -0.34623 | 0.98189 | -0.34754 | 9.1526
95 | -0.087904 | -0.022185 | 0.088048 | 0.022273 | 0.00014419 | 8.7891e-05 | 0.13326 | 0.13326 | 0.13326 | 0.98195 | -0.34623 | 0.98371 | -0.31204 | 9.1526
96 | 0.087899 | 0.022182 | -0.087748 | -0.02209 | 0.00015096 | 9.2038e-05 | 0.13326 | 0.13326 | 0.13326 | 0.98189 | -0.34754 | 0.98005 | -0.38347 | 9.1527
97 | -0.09173 | -0.023196 | 0.091775 | 0.023223 | 4.4917e-05 | 2.7484e-05 | 0.13883 | 0.13883 | 0.13883 | 0.98371 | -0.31204 | 0.98424 | -0.30183 | 9.535
98 | 0.085928 | 0.021634 | -0.085918 | -0.021627 | 9.9341e-06 | 6.0442e-06 | 0.1305 | 0.1305 | 0.1305 | 0.98005 | -0.38347 | 0.97992 | -0.38589 | 8.963
99 | -0.093885 | -0.023752 | 0.093902 | 0.023762 | 1.6874e-05 | 1.0345e-05 | 0.14202 | 0.14202 | 0.14202 | 0.98424 | -0.30183 | 0.98443 | -0.29809 | 9.7541
100 | 0.084099 | 0.021171 | -0.084079 | -0.021159 | 1.9899e-05 | 1.208e-05 | 0.12774 | 0.12774 | 0.12774 | 0.97992 | -0.38589 | 0.97967 | -0.39084 | 8.7733
101 | -0.09692 | -0.024519 | 0.096926 | 0.024523 | 6.3336e-06 | 3.8936e-06 | 0.14658 | 0.14658 | 0.14658 | 0.98443 | -0.29809 | 0.9845 | -0.29673 | 10.0674
102 | 0.01215 | 0.0030456 | -0.012149 | -0.0030451 | 1.0473e-06 | 5.6846e-07 | 0.018519 | 0.018519 | 0.018519 | 0.97631 | -0.45668 | 0.97622 | -0.45849 | 5.0876
103 | 0.011069 | 0.0027744 | -0.011069 | -0.0027742 | 2.8272e-07 | 1.4783e-07 | 0.016873 | 0.016873 | 0.016873 | 0.97622 | -0.45849 | 0.9762 | -0.45902 | 4.6354
104 | 0.0095515 | 0.0023939 | -0.0095513 | -0.0023938 | 1.7824e-07 | 8.6041e-08 | 0.014559 | 0.014559 | 0.014559 | 0.9762 | -0.45902 | 0.97618 | -0.45941 | 3.9998
105 | 0.0083529 | 0.0020934 | -0.0083526 | -0.0020933 | 3.3488e-07 | 1.4546e-07 | 0.012733 | 0.012733 | 0.012733 | 0.97618 | -0.45941 | 0.97613 | -0.46026 | 3.498
106 | -0.10811 | -0.027347 | 0.10812 | 0.027358 | 1.7795e-05 | 1.1026e-05 | 0.16338 | 0.16338 | 0.16338 | 0.98515 | -0.28415 | 0.98533 | -0.28072 | 11.221
107 | 0.10402 | 0.026322 | -0.10395 | -0.026284 | 6.275e-05 | 3.8781e-05 | 0.1572 | 0.1572 | 0.1572 | 0.98515 | -0.28415 | 0.9845 | -0.29673 | 10.7968
108 | -0.11634 | -0.029417 | 0.1164 | 0.029458 | 6.6651e-05 | 4.1483e-05 | 0.17578 | 0.17578 | 0.17578 | 0.98533 | -0.28072 | 0.98595 | -0.26878 | 12.0729
109 | -0.027488 | -0.00691 | 0.027489 | 0.0069105 | 1.6803e-06 | 5.6369e-07 | 0.041881 | 0.041881 | 0.041881 | 0.97681 | -0.44694 | 0.97687 | -0.44566 | 2.8764
110 | 0.026163 | 0.0065779 | -0.02616 | -0.0065772 | 2.3003e-06 | 6.9911e-07 | 0.039862 | 0.039863 | 0.039863 | 0.97681 | -0.44694 | 0.97671 | -0.44878 | 2.7378
111 | -0.029235 | -0.007348 | 0.029235 | 0.007348 | 5.2191e-08 | 1.9348e-08 | 0.044539 | 0.044539 | 0.044539 | 0.97687 | -0.44566 | 0.97687 | -0.44563 | 3.059
112 | 0.024871 | 0.0062541 | -0.024844 | -0.0062467 | 2.7466e-05 | 7.3802e-06 | 0.037899 | 0.037902 | 0.037902 | 0.97671 | -0.44878 | 0.97554 | -0.47192 | 2.6032
113 | -0.030516 | -0.007669 | 0.030519 | 0.0076702 | 2.8634e-06 | 1.1248e-06 | 0.046491 | 0.04649 | 0.046491 | 0.97687 | -0.44563 | 0.97697 | -0.44366 | 3.193
114 | 0.024844 | 0.0062467 | -0.024804 | -0.0062297 | 3.9315e-05 | 1.6976e-05 | 0.037902 | 0.037905 | 0.037905 | 0.97554 | -0.47192 | 0.97385 | -0.5051 | 3.4712
115 | -0.031879 | -0.0080111 | 0.031882 | 0.0080124 | 3.0144e-06 | 1.2462e-06 | 0.048563 | 0.048562 | 0.048563 | 0.97697 | -0.44366 | 0.97708 | -0.44168 | 3.3353
116 | 0.024804 | 0.0062297 | -0.024784 | -0.0062173 | 2.0136e-05 | 1.2423e-05 | 0.037905 | 0.037905 | 0.037905 | 0.97385 | -0.5051 | 0.97299 | -0.52212 | 10.4136
117 | 0.01973 | 0.0049507 | -0.019717 | -0.0049427 | 1.3215e-05 | 7.9776e-06 | 0.030176 | 0.030176 | 0.030176 | 0.97299 | -0.52212 | 0.97228 | -0.53618 | 8.2902
118 | -0.080277 | -0.020198 | 0.080285 | 0.020203 | 7.8684e-06 | 4.7519e-06 | 0.122 | 0.122 | 0.122 | 0.97935 | -0.39709 | 0.97945 | -0.39504 | 8.3791
119 | -0.081544 | -0.020518 | 0.081552 | 0.020523 | 8.1171e-06 | 4.911e-06 | 0.12391 | 0.12391 | 0.12391 | 0.97945 | -0.39504 | 0.97956 | -0.39296 | 8.5105
120 | -0.082811 | -0.020839 | 0.08282 | 0.020844 | 8.3711e-06 | 5.0735e-06 | 0.12583 | 0.12583 | 0.12583 | 0.97956 | -0.39296 | 0.97967 | -0.39084 | 8.6419
121 | 0.014773 | 0.0037035 | -0.014769 | -0.0037012 | 4.0458e-06 | 2.3276e-06 | 0.022609 | 0.022609 | 0.022609 | 0.97228 | -0.53618 | 0.97199 | -0.54193 | 6.2114
122 | 0.0059777 | 0.0014977 | -0.0059758 | -0.0014972 | 1.9545e-06 | 4.7976e-07 | 0.0091512 | 0.0091514 | 0.0091514 | 0.97199 | -0.54193 | 0.97164 | -0.5488 | 2.5141
123 | 0.008791 | 0.0022035 | -0.0087897 | -0.0022029 | 1.2468e-06 | 5.7045e-07 | 0.013458 | 0.013458 | 0.013458 | 0.97199 | -0.54193 | 0.97183 | -0.54491 | 3.6973
124 | 0.0037825 | 0.0009475 | -0.0037821 | -0.00094762 | 3.6199e-07 | -1.2461e-07 | 0.0057925 | 0.0057926 | 0.0057926 | 0.97164 | -0.5488 | 0.97154 | -0.55081 | 1.5914
125 | 0.0068595 | 0.0017192 | -0.0068591 | -0.001719 | 4.4827e-07 | 1.5263e-07 | 0.010503 | 0.010503 | 0.010503 | 0.97183 | -0.54491 | 0.97177 | -0.54628 | 2.8854
126 | 0.0018877 | 0.00047284 | -0.0018876 | -0.00047308 | 7.3179e-08 | -2.4225e-07 | 0.0028911 | 0.0028912 | 0.0028912 | 0.97154 | -0.55081 | 0.9715 | -0.55162 | 0.79428
127 | 0.0056007 | 0.0014036 | -0.0056004 | -0.0014036 | 2.2868e-07 | 4.3639e-08 | 0.008576 | 0.008576 | 0.008576 | 0.97177 | -0.54628 | 0.97172 | -0.54714 | 2.3561
128 | 0.0075184 | 0.0018842 | -0.0075182 | -0.0018841 | 2.395e-07 | 9.2502e-08 | 0.011461 | 0.011461 | 0.011461 | 0.97613 | -0.46026 | 0.9761 | -0.46093 | 3.1486
129 | 0.0066469 | 0.0016658 | -0.0066465 | -0.0016657 | 4.3693e-07 | 1.378e-07 | 0.010133 | 0.010133 | 0.010133 | 0.9761 | -0.46093 | 0.97603 | -0.4623 | 2.7838
130 | 0.0042773 | 0.0010719 | -0.0042773 | -0.0010719 | 3.2447e-08 | -4.6639e-09 | 0.006521 | 0.006521 | 0.006521 | 0.97603 | -0.4623 | 0.97602 | -0.46246 | 1.7915
131 | 0.0034379 | 0.00086152 | -0.0034378 | -0.00086155 | 4.891e-08 | -2.8032e-08 | 0.0052413 | 0.0052413 | 0.0052413 | 0.97602 | -0.46246 | 0.97601 | -0.46276 | 1.4399
132 | 0.0025427 | 0.00063721 | -0.0025427 | -0.00063726 | 3.1503e-08 | -4.9696e-08 | 0.0038766 | 0.0038767 | 0.0038767 | 0.97601 | -0.46276 | 0.97599 | -0.46302 | 1.065

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46451 | 0.11813

## res_load
| p_mw | q_mvar
0 | 0.0072218 | 0.0018099
1 | 0.0030343 | 0.00076046
2 | 0.00016478 | 4.1298e-05
3 | 0.0062705 | 0.0015715
4 | 0.0016719 | 0.00041902
5 | 0.0016733 | 0.00041937
6 | 0.0010683 | 0.00026773
7 | 0.0016723 | 0.00041912
8 | 0.0046061 | 0.0011544
9 | 0.0014815 | 0.00037129
10 | 0.0016731 | 0.00041931
11 | 0.012253 | 0.003071
12 | 0.0025258 | 0.00063302
13 | 0.02 | 0.0050125
14 | 0.0064462 | 0.0016156
15 | 0.0080206 | 0.0020102
16 | 0.00361 | 0.00090475
17 | 0.0048051 | 0.0012043
18 | 0.0065924 | 0.0016522
19 | 0.0091437 | 0.0022916
20 | 0.013054 | 0.0032717
21 | 0.021207 | 0.0053151
22 | 0.013497 | 0.0033827
23 | 0.0014815 | 0.00037129
24 | 0.0086324 | 0.0021635
25 | 0.0066167 | 0.0016583
26 | 0.0053308 | 0.001336
27 | 0.0080897 | 0.0020275
28 | 0.01369 | 0.003431
29 | 0.011438 | 0.0028666
30 | 0.0047864 | 0.0011996
31 | 0.0017668 | 0.00044279
32 | 0.0038755 | 0.0009713
33 | 0.013909 | 0.003486
34 | 0.0083571 | 0.0020945
35 | 0.00822 | 0.0020601
36 | 0.0082199 | 0.0020601
37 | 0.0082143 | 0.0020587
38 | 0.0048921 | 0.0012261
39 | 0.0079927 | 0.0020032
40 | 0.002069 | 0.00051853
41 | 0.00346 | 0.00086716
42 | 0.0020747 | 0.00051997
43 | 0.0031295 | 0.00078432
44 | 0.0024234 | 0.00060736
45 | 0.0024216 | 0.00060691
46 | 0.0030191 | 0.00075667
47 | 0.0020682 | 0.00051834
48 | 0.0028981 | 0.00072634
49 | 0.0083045 | 0.0020813
50 | 0.0023659 | 0.00059295
51 | 0.0085014 | 0.0021306
52 | 0.0094175 | 0.0023602
53 | 0.0073664 | 0.0018462
54 | 0.0020912 | 0.0005241
55 | 0.0022314 | 0.00055923
56 | 0.0012737 | 0.00031921
57 | 0.0017362 | 0.00043513
58 | 0.0031922 | 0.00080005
59 | 0.001509 | 0.0003782
60 | 0.0013469 | 0.00033757
61 | 0.0058503 | 0.0014662
62 | 0.0032514 | 0.00081489
63 | 0.0027252 | 0.00068299
64 | 0.0036816 | 0.0009227
65 | 0.0018195 | 0.00045601
66 | 0.0021105 | 0.00052893
67 | 0.0018194 | 0.00045598
68 | 0.0030177 | 0.00075631
69 | 0.0020315 | 0.00050915
70 | 0.00108 | 0.00027066
71 | 0.0015177 | 0.00038037
72 | 0.0011984 | 0.00030035
73 | 0.0040894 | 0.0010249
74 | 0.0082135 | 0.0020585
75 | 0.0070273 | 0.0017612
76 | 0.0048954 | 0.0012269
77 | 0.001325 | 0.00033209
78 | 0.0017453 | 0.00043742
79 | 0.0012892 | 0.0003231
80 | 0.001281 | 0.00032106
81 | 0.0013605 | 0.00034097
82 | 0.0075758 | 0.0018987
83 | 0.0050541 | 0.0012667
84 | 0.0012592 | 0.0003156
85 | 0.0012592 | 0.0003156
86 | 0.0012592 | 0.0003156
87 | 0.0012594 | 0.00031564
88 | 0.0049443 | 0.0012392
89 | 0.0021933 | 0.0005497
90 | 0.0019302 | 0.00048376
91 | 0.0018944 | 0.00047479
92 | 0.0012584 | 0.00031539
93 | 0.0018876 | 0.00047308
94 | 0.0056004 | 0.0014036
95 | 0.00083415 | 0.00020906
96 | 0.00087125 | 0.00021836
97 | 0.0023692 | 0.00059377
98 | 0.00083939 | 0.00021037
99 | 0.0008951 | 0.00022433
100 | 0.0025427 | 0.00063726

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1