## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-27_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-27_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-27_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-27_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1054-27_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1054-27_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1054-27_0_2_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1054-27_0_2_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1054-27_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1054-27_0_2_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1054-27_0_2_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1054-27_0_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1054-27_0_2_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1054-27_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1054-27_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1054-27_0_2_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_1054-27_0_2_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1054-27_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1054-27_0_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1054-27_0_2_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1054-27_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1054-27_0_2_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_1054-27_0_2_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1054-27_0_2_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1054-27_0_2_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1054-27_0_2_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1054-27_0_2_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_1054-27_0_2_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1054-27_0_2_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1054-27_0_2_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1054-27_0_2_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1054-27_0_2_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1054-27_0_2_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1054-27_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_MV_211_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-27_0_2_load_0 | 0 | 0.0033801 | 0.00084713 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-27_0_2_load_1 | 1 | 0.010359 | 0.0025963 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-27_0_2_load_3 | 3 | 0.001954 | 0.00048972 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-27_0_2_load_12 | 6 | 0.0019841 | 0.00049725 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-27_0_2_load_6 | 8 | 0.00085584 | 0.00021449 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-27_0_2_load_20 | 9 | 0.00052862 | 0.00013248 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-27_0_2_load_11 | 10 | 0.0020447 | 0.00051244 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-27_0_2_load_30 | 12 | 0.0094528 | 0.0023691 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-27_0_2_load_7 | 13 | 0.0086249 | 0.0021616 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-27_0_2_load_8 | 14 | 0.0031301 | 0.00078448 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-27_0_2_load_32 | 15 | 0.0067 | 0.0016792 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-27_0_2_load_25 | 16 | 0.0072326 | 0.0018127 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-27_0_2_load_21 | 19 | 0.00085174 | 0.00021347 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-27_0_2_load_34 | 21 | 0.014257 | 0.0035731 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-27_0_2_load_26 | 23 | 0.00067752 | 0.0001698 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-27_0_2_load_33 | 26 | 0.00066272 | 0.00016609 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-27_0_2_load_31 | 27 | 0.0004743 | 0.00011887 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-27_0_2_load_27 | 28 | 0.0014719 | 0.00036889 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-27_0_2_load_29 | 29 | 0.0021076 | 0.00052822 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-27_0_2_load_22 | 30 | 0.00037548 | 9.4103e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-27_0_2_load_24 | 32 | 0.00060996 | 0.00015287 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-27_0_2_load_28 | 33 | 0.00027593 | 6.9153e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-27_0_2_line_0 |  | 0 | 1 | 0.0039137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-27_0_2_line_1 |  | 0 | 2 | 0.087032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-27_0_2_line_2 |  | 1 | 3 | 0.018284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-27_0_2_line_3 |  | 2 | 4 | 0.095703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-27_0_2_line_4 |  | 2 | 5 | 0.27094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-27_0_2_line_5 |  | 3 | 6 | 0.0034072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-27_0_2_line_6 |  | 4 | 7 | 0.39223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-27_0_2_line_7 |  | 4 | 8 | 0.35575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-27_0_2_line_8 |  | 5 | 9 | 0.18672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-27_0_2_line_9 |  | 6 | 10 | 0.10161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-27_0_2_line_10 |  | 7 | 11 | 0.022872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-27_0_2_line_11 |  | 7 | 12 | 0.016611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-27_0_2_line_12 |  | 8 | 13 | 0.028209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-27_0_2_line_13 |  | 11 | 15 | 0.023774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-27_0_2_line_14 |  | 12 | 16 | 0.007001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-27_0_2_line_15 |  | 13 | 14 | 0.18952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-27_0_2_line_16 |  | 15 | 27 | 0.027056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-27_0_2_line_17 |  | 16 | 31 | 0.038576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-27_0_2_line_18 |  | 17 | 18 | 0.16687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-27_0_2_line_19 |  | 17 | 19 | 0.045836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-27_0_2_line_20 |  | 18 | 28 | 0.06484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-27_0_2_line_21 |  | 18 | 24 | 0.064847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-27_0_2_line_22 |  | 20 | 21 | 0.012521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-27_0_2_line_23 |  | 20 | 22 | 0.1644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-27_0_2_line_24 |  | 22 | 23 | 0.016358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-27_0_2_line_25 |  | 23 | 29 | 0.034863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-27_0_2_line_26 |  | 24 | 25 | 0.10038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-27_0_2_line_27 |  | 24 | 26 | 0.051172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-27_0_2_line_28 |  | 25 | 27 | 0.023074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-27_0_2_line_29 |  | 29 | 33 | 0.011321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-27_0_2_line_30 |  | 30 | 31 | 0.037159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-27_0_2_line_31 |  | 31 | 32 | 0.021753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-27_0_2_line_32 |  | 32 | 33 | 0.0050299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-27_0_2_trafo_26 | 0.63 MVA 20/0.4 kV | 34 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2669345.635 | 1214297.4112 | 2669343.4242 | 1214300.6406
1 | 2669368.6733 | 1214214.6488 | 2669362.719 | 1214253.7597 | 2669357.9652 | 1214275.8739 | 2669349.849 | 1214291.2558 | 2669345.635 | 1214297.4112
2 | 2669333.2709 | 1214315.8304 | 2669333.878 | 1214314.5848 | 2669343.4242 | 1214300.6406
3 | 2669289.039 | 1214161.3341 | 2669293.7379 | 1214165.4913 | 2669339.0203 | 1214195.0806 | 2669368.6733 | 1214214.6488
4 | 2669368.6733 | 1214214.6488 | 2669393.8847 | 1214234.0543 | 2669410.949 | 1214252.5534 | 2669421.2128 | 1214268.0047 | 2669433.7144 | 1214296.735 | 2669437.2607 | 1214302.0129 | 2669442.0392 | 1214307.7944 | 2669487.8105 | 1214348.0528 | 2669551.7163 | 1214393.0816 | 2669559.7696 | 1214400.6914
5 | 2669333.2709 | 1214315.8304 | 2669331.7782 | 1214318.8932
6 | 2669289.039 | 1214161.3341 | 2669287.9187 | 1214157.0851 | 2669290.0608 | 1214151.1952 | 2669294.3359 | 1214148.0317 | 2669300.5885 | 1214146.6035 | 2669326.38 | 1214149.4828 | 2669342.9163 | 1214152.677 | 2669360.4836 | 1214159.3188 | 2669373.4668 | 1214158.4582 | 2669378.3959 | 1214155.2357 | 2669381.9545 | 1214150.3296 | 2669385.0207 | 1214139.4473 | 2669385.8573 | 1214132.1747 | 2669386.4313 | 1214127.2338 | 2669386.1706 | 1214114.4005 | 2669384.7762 | 1214090.636 | 2669378.5833 | 1214056.9094 | 2669371.7174 | 1214035.316 | 2669366.2518 | 1214021.3214 | 2669351.5915 | 1213999.1704 | 2669337.1172 | 1213979.9567 | 2669334.7454 | 1213973.5918 | 2669334.4849 | 1213972.477 | 2669334.3578 | 1213969.04 | 2669334.5153 | 1213967.2518 | 2669334.6567 | 1213965.5413 | 2669319.2814 | 1213961.738 | 2669298.0552 | 1213955.5096 | 2669289.1533 | 1213952.2042 | 2669278.6571 | 1213947.5237 | 2669265.0578 | 1213940.5725 | 2669255.2187 | 1213934.8992
7 | 2669289.039 | 1214161.3341 | 2669274.2512 | 1214201.1429 | 2669269.1286 | 1214208.6103 | 2669265.659 | 1214213.0506 | 2669260.5262 | 1214216.1707 | 2669252.6506 | 1214217.3911 | 2669246.5476 | 1214216.4197 | 2669197.8235 | 1214186.2352 | 2669189.9743 | 1214184.532 | 2669180.1439 | 1214184.6847 | 2669167.9213 | 1214190.0463 | 2669137.3369 | 1214212.0722 | 2669105.8175 | 1214232.2196 | 2669094.9248 | 1214243.4227 | 2669085.4901 | 1214256.6328 | 2669079.2517 | 1214260.1294 | 2669072.4261 | 1214259.2387 | 2669061.3581 | 1214256.0863 | 2669047.0468 | 1214252.2849 | 2669034.6721 | 1214249.1508 | 2669024.6081 | 1214249.8125 | 2669011.9366 | 1214251.9783 | 2669006.3897 | 1214256.0718
8 | 2669559.7696 | 1214400.6914 | 2669562.6483 | 1214412.399 | 2669562.643 | 1214427.8198 | 2669552.9811 | 1214531.3722 | 2669550.8515 | 1214573.2849 | 2669549.4973 | 1214586.4849
9 | 2669311.2655 | 1214417.7965 | 2669324.6107 | 1214333.6001 | 2669331.7782 | 1214318.8932
10 | 2669236.5043 | 1213921.6736 | 2669255.2187 | 1213934.8992
11 | 2669255.2187 | 1213934.8992 | 2669254.5913 | 1213935.9481 | 2669252.1317 | 1213939.0882 | 2669243.5898 | 1213946.6382
12 | 2669006.3897 | 1214256.0718 | 2669003.3334 | 1214258.3272 | 2668993.3898 | 1214268.93 | 2668983.5148 | 1214268.884
13 | 2669236.5043 | 1213921.6736 | 2669226.96 | 1213916.1149 | 2669216.3202 | 1213909.1283
14 | 2669243.5898 | 1213946.6382 | 2669237.2626 | 1213949.6348
15 | 2668983.5148 | 1214268.884 | 2668974.0985 | 1214268.8401 | 2668968.7102 | 1214267.7994 | 2668959.2579 | 1214264.1767 | 2668930.9263 | 1214248.4727 | 2668916.4469 | 1214242.1125 | 2668897.3207 | 1214236.2767 | 2668877.0161 | 1214227.9036 | 2668826.2029 | 1214204.8359 | 2668808.8288 | 1214198.4206
16 | 2669195.1156 | 1213892.3569 | 2669195.9989 | 1213893.2413 | 2669213.8432 | 1213907.5017 | 2669216.3202 | 1213909.1283
17 | 2669199.5592 | 1213956.2444 | 2669218.8793 | 1213953.9449 | 2669231.079 | 1213952.5634 | 2669237.2626 | 1213949.6348
18 | 2668897.3471 | 1213829.1773 | 2668896.0861 | 1213833.1319 | 2668941.67 | 1213848.8462 | 2668961.4357 | 1213856.6352 | 2668987.1236 | 1213864.6483 | 2668996.8392 | 1213867.2401 | 2669011.1216 | 1213869.6847 | 2669026.6294 | 1213871.2651 | 2669034.0056 | 1213871.2171 | 2669039.3167 | 1213876.9822 | 2669049.2117 | 1213881.7886
19 | 2668897.3471 | 1213829.1773 | 2668854.1454 | 1213813.8613
20 | 2669049.2117 | 1213881.7886 | 2669053.6225 | 1213895.7707 | 2669058.3627 | 1213904.2642 | 2669084.2245 | 1213911.0012 | 2669091.1633 | 1213899.1567
21 | 2669049.2117 | 1213881.7886 | 2669039.3167 | 1213876.9822 | 2669034.0056 | 1213871.2171 | 2669041.0172 | 1213871.1649 | 2669056.1574 | 1213869.7281 | 2669079.6917 | 1213866.2651
22 | 2669027.239 | 1213957.6819 | 2669039.7403 | 1213956.4925
23 | 2669039.7403 | 1213956.4925 | 2669039.8831 | 1213960.5634 | 2669050.1085 | 1213966.3409 | 2669062.7432 | 1213970.0228 | 2669047.4376 | 1213990.3584 | 2669043.7596 | 1213999.6772 | 2669048.4334 | 1213999.4756 | 2669066.9416 | 1214002.325 | 2669131.9504 | 1214000.6438 | 2669143.3547 | 1213999.075
24 | 2669143.3547 | 1213999.075 | 2669158.7077 | 1214004.7196
25 | 2669158.7077 | 1214004.7196 | 2669165.4628 | 1214007.2031 | 2669169.0906 | 1214007.4564 | 2669172.513 | 1214006.4288 | 2669174.2514 | 1214003.9029 | 2669179.5601 | 1213987.3437
26 | 2669177.3409 | 1213877.7485 | 2669175.0314 | 1213876.4654 | 2669169.2609 | 1213873.6411 | 2669154.0363 | 1213867.9499 | 2669147.2678 | 1213866.0369 | 2669137.0148 | 1213863.9389 | 2669119.8929 | 1213862.6842 | 2669099.9121 | 1213863.6422 | 2669089.0735 | 1213864.884 | 2669079.6917 | 1213866.2651
27 | 2669079.6917 | 1213866.2651 | 2669104.8639 | 1213880.7436 | 2669120.4794 | 1213884.816 | 2669123.2302 | 1213879.4889
28 | 2669177.3409 | 1213877.7485 | 2669189.9936 | 1213887.09 | 2669194.4822 | 1213891.7228 | 2669195.1156 | 1213892.3569
29 | 2669182.8406 | 1213976.5093 | 2669181.1158 | 1213982.4913 | 2669179.5601 | 1213987.3437
30 | 2669199.5592 | 1213956.2444 | 2669197.2561 | 1213953.1046 | 2669177.2673 | 1213946.2684 | 2669169.8139 | 1213945.1257 | 2669165.5714 | 1213946.9007
31 | 2669199.5592 | 1213956.2444 | 2669193.6454 | 1213962.5019 | 2669184.234 | 1213971.6763
32 | 2669182.8406 | 1213976.5093 | 2669184.234 | 1213971.6763 | 2669184.234 | 1213971.6763

## bus_geodata
| x | y | coords
0 | 2669345.635 | 1214297.4112
1 | 2669343.4242 | 1214300.6406
2 | 2669368.6733 | 1214214.6488
3 | 2669333.2709 | 1214315.8304
4 | 2669289.039 | 1214161.3341
5 | 2669559.7696 | 1214400.6914
6 | 2669331.7782 | 1214318.8932
7 | 2669255.2187 | 1213934.8992
8 | 2669006.3897 | 1214256.0718
9 | 2669549.4973 | 1214586.4849
10 | 2669311.2655 | 1214417.7965
11 | 2669236.5043 | 1213921.6736
12 | 2669243.5898 | 1213946.6382
13 | 2668983.5148 | 1214268.884
14 | 2668808.8288 | 1214198.4206
15 | 2669216.3202 | 1213909.1283
16 | 2669237.2626 | 1213949.6348
17 | 2668897.3471 | 1213829.1773
18 | 2669049.2117 | 1213881.7886
19 | 2668854.1454 | 1213813.8613
20 | 2669039.7403 | 1213956.4925
21 | 2669027.239 | 1213957.6819
22 | 2669143.3547 | 1213999.075
23 | 2669158.7077 | 1214004.7196
24 | 2669079.6917 | 1213866.2651
25 | 2669177.3409 | 1213877.7485
26 | 2669123.2302 | 1213879.4889
27 | 2669195.1156 | 1213892.3569
28 | 2669091.1633 | 1213899.1567
29 | 2669179.5601 | 1213987.3437
30 | 2669165.5714 | 1213946.9007
31 | 2669199.5592 | 1213956.2444
32 | 2669184.234 | 1213971.6763
33 | 2669182.8406 | 1213976.5093
34 | 2669143.3547 | 1213999.075

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97736 | -0.43624 | 0.0033801 | 0.00084713
1 | 0.9773 | -0.43741 | 0.010359 | 0.0025963
2 | 0.97896 | -0.40497 | 0 | 0
3 | 0.9772 | -0.43941 | 0.001954 | 0.00048972
4 | 0.98075 | -0.36974 | 0 | 0
5 | 0.97882 | -0.40762 | 0 | 0
6 | 0.97719 | -0.43966 | 0.0019841 | 0.00049725
7 | 0.99273 | -0.13866 | 0 | 0
8 | 0.97659 | -0.45147 | 0.00085584 | 0.00021449
9 | 0.97873 | -0.40943 | 0.00052862 | 0.00013248
10 | 0.977 | -0.44346 | 0.0020447 | 0.00051244
11 | 0.99251 | -0.14278 | 0 | 0
12 | 0.99339 | -0.126 | 0.0094528 | 0.0023691
13 | 0.97628 | -0.45753 | 0.0086249 | 0.0021616
14 | 0.97573 | -0.4684 | 0.0031301 | 0.00078448
15 | 0.99229 | -0.14706 | 0.0067 | 0.0016792
16 | 0.99373 | -0.11951 | 0.0072326 | 0.0018127
17 | 0.9916 | -0.1605 | 0 | 0
18 | 0.99173 | -0.15797 | 0 | 0
19 | 0.99157 | -0.16119 | 0.00085174 | 0.00021347
20 | 0.99766 | -0.045031 | 0 | 0
21 | 0.9975 | -0.048157 | 0.014257 | 0.0035731
22 | 0.99979 | -0.0040673 | 0 | 0
23 | 1 | 0 | -0.079909 | -0.01994
24 | 0.99187 | -0.15529 | 0 | 0
25 | 0.99214 | -0.14995 | 0 | 0
26 | 0.99184 | -0.15589 | 0.00066272 | 0.00016609
27 | 0.99221 | -0.14872 | 0.0004743 | 0.00011887
28 | 0.99165 | -0.15966 | 0.0014719 | 0.00036889
29 | 0.99797 | -0.038455 | 0.0021076 | 0.00052822
30 | 0.99584 | -0.079134 | 0.00037548 | 9.4103e-05
31 | 0.99585 | -0.078889 | 0 | 0
32 | 0.99705 | -0.055916 | 0.00060996 | 0.00015287
33 | 0.99734 | -0.050558 | 0.00027593 | 6.9153e-05
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.016344 | 0.0040953 | -0.016343 | -0.0040948 | 9.087e-07 | 5.3252e-07 | 0.024883 | 0.024883 | 0.024883 | 0.97736 | -0.43624 | 0.9773 | -0.43741 | 6.836
1 | -0.019724 | -0.0049424 | 0.019753 | 0.0049602 | 2.943e-05 | 1.7743e-05 | 0.030029 | 0.030029 | 0.030029 | 0.97736 | -0.43624 | 0.97896 | -0.40497 | 8.2497
2 | 0.0059837 | 0.0014985 | -0.0059831 | -0.0014984 | 5.6908e-07 | 1.3512e-07 | 0.0091102 | 0.0091103 | 0.0091103 | 0.9773 | -0.43741 | 0.9772 | -0.43941 | 2.5028
3 | -0.020282 | -0.005087 | 0.020316 | 0.0051076 | 3.4112e-05 | 2.0626e-05 | 0.03083 | 0.03083 | 0.03083 | 0.97896 | -0.40497 | 0.98075 | -0.36974 | 8.4698
4 | 0.00052873 | 0.0001268 | -0.00052866 | -0.00013017 | 6.5391e-08 | -3.3642e-06 | 0.00080166 | 0.00080285 | 0.00080285 | 0.97896 | -0.40497 | 0.97882 | -0.40762 | 0.22056
5 | 0.0040291 | 0.0010086 | -0.0040291 | -0.0010087 | 4.8088e-08 | -1.1908e-08 | 0.0061349 | 0.0061349 | 0.0061349 | 0.9772 | -0.43941 | 0.97719 | -0.43966 | 1.6854
6 | -0.032981 | -0.0082957 | 0.03335 | 0.0085265 | 0.00036845 | 0.0002308 | 0.050051 | 0.050049 | 0.050051 | 0.98075 | -0.36974 | 0.99273 | -0.13866 | 13.7501
7 | 0.012665 | 0.0031881 | -0.012616 | -0.0031611 | 4.9289e-05 | 2.7075e-05 | 0.019221 | 0.019222 | 0.019222 | 0.98075 | -0.36974 | 0.97659 | -0.45147 | 5.2809
8 | 0.00052866 | 0.00013017 | -0.00052862 | -0.00013248 | 4.5178e-08 | -2.3178e-06 | 0.00080285 | 0.00080368 | 0.00080368 | 0.97882 | -0.40762 | 0.97873 | -0.40943 | 0.22079
9 | 0.002045 | 0.0005114 | -0.0020447 | -0.00051244 | 3.6946e-07 | -1.0362e-06 | 0.0031137 | 0.0031141 | 0.0031141 | 0.97719 | -0.43966 | 0.977 | -0.44346 | 0.85553
10 | 0.010166 | 0.0025426 | -0.010164 | -0.0025416 | 1.9913e-06 | 9.7875e-07 | 0.015237 | 0.015237 | 0.015237 | 0.99273 | -0.13866 | 0.99251 | -0.14278 | 4.186
11 | -0.043516 | -0.011069 | 0.043543 | 0.011086 | 2.655e-05 | 1.6777e-05 | 0.065285 | 0.065285 | 0.065285 | 0.99273 | -0.13866 | 0.99339 | -0.126 | 17.9355
12 | 0.01176 | 0.0029466 | -0.011757 | -0.0029447 | 3.3964e-06 | 1.8209e-06 | 0.017918 | 0.017918 | 0.017918 | 0.97659 | -0.45147 | 0.97628 | -0.45753 | 4.9226
13 | 0.010164 | 0.0025416 | -0.010162 | -0.0025406 | 2.0698e-06 | 1.0175e-06 | 0.015237 | 0.015237 | 0.015237 | 0.99251 | -0.14278 | 0.99229 | -0.14706 | 4.186
14 | -0.052996 | -0.013455 | 0.053012 | 0.013466 | 1.657e-05 | 1.0514e-05 | 0.079445 | 0.079445 | 0.079445 | 0.99339 | -0.126 | 0.99373 | -0.11951 | 21.8255
15 | 0.0031317 | 0.00078315 | -0.0031301 | -0.00078448 | 1.6191e-06 | -1.3322e-06 | 0.0047727 | 0.0047735 | 0.0047735 | 0.97628 | -0.45753 | 0.97573 | -0.4684 | 1.3114
16 | 0.0034624 | 0.00086143 | -0.0034622 | -0.00086161 | 2.7329e-07 | -1.7456e-07 | 0.0051899 | 0.0051901 | 0.0051901 | 0.99229 | -0.14706 | 0.99221 | -0.14872 | 1.4258
17 | -0.060245 | -0.015278 | 0.060363 | 0.015353 | 0.00011789 | 7.495e-05 | 0.090275 | 0.090275 | 0.090275 | 0.99373 | -0.11951 | 0.99585 | -0.078889 | 24.8008
18 | -0.00085177 | -0.00021289 | 0.00085187 | 0.00021081 | 1.0214e-07 | -2.0875e-06 | 0.001278 | 0.0012772 | 0.001278 | 0.9916 | -0.1605 | 0.99173 | -0.15797 | 0.35109
19 | 0.00085177 | 0.00021289 | -0.00085174 | -0.00021347 | 2.8078e-08 | -5.7329e-07 | 0.001278 | 0.0012782 | 0.0012782 | 0.9916 | -0.1605 | 0.99157 | -0.16119 | 0.35115
20 | 0.001472 | 0.00036813 | -0.0014719 | -0.00036889 | 1.186e-07 | -7.6067e-07 | 0.0022084 | 0.0022087 | 0.0022087 | 0.99173 | -0.15797 | 0.99165 | -0.15966 | 0.60678
21 | -0.0023239 | -0.00057894 | 0.0023242 | 0.00057829 | 2.9542e-07 | -6.4779e-07 | 0.0034856 | 0.0034853 | 0.0034856 | 0.99173 | -0.15797 | 0.99187 | -0.15529 | 0.95758
22 | 0.014259 | 0.0035742 | -0.014257 | -0.0035731 | 2.1237e-06 | 1.1957e-06 | 0.021267 | 0.021267 | 0.021267 | 0.99766 | -0.045031 | 0.9975 | -0.048157 | 5.8427
23 | -0.014259 | -0.0035742 | 0.014287 | 0.0035899 | 2.7882e-05 | 1.5694e-05 | 0.021267 | 0.021267 | 0.021267 | 0.99766 | -0.045031 | 0.99979 | -0.0040673 | 5.8427
24 | -0.014287 | -0.0035899 | 0.014289 | 0.0035915 | 2.7743e-06 | 1.561e-06 | 0.021267 | 0.021266 | 0.021267 | 0.99979 | -0.0040673 | 1 | 0 | 5.8425
25 | 0.06397 | 0.016348 | -0.063851 | -0.016273 | 0.00011873 | 7.5534e-05 | 0.0953 | 0.0953 | 0.0953 | 1 | 0 | 0.99797 | -0.038455 | 26.1813
26 | -0.0029869 | -0.00074374 | 0.0029877 | 0.00074292 | 7.5522e-07 | -8.1265e-07 | 0.0044793 | 0.0044789 | 0.0044793 | 0.99187 | -0.15529 | 0.99214 | -0.14995 | 1.2306
27 | 0.00066274 | 0.00016544 | -0.00066272 | -0.00016609 | 1.8965e-08 | -6.4831e-07 | 0.00099402 | 0.00099425 | 0.00099425 | 0.99187 | -0.15529 | 0.99184 | -0.15589 | 0.27315
28 | -0.0029877 | -0.00074292 | 0.0029879 | 0.00074274 | 1.7357e-07 | -1.8691e-07 | 0.0044789 | 0.0044788 | 0.0044789 | 0.99214 | -0.14995 | 0.99221 | -0.14872 | 1.2305
29 | 0.061743 | 0.015745 | -0.061707 | -0.015722 | 3.6057e-05 | 2.2929e-05 | 0.092157 | 0.092158 | 0.092158 | 0.99797 | -0.038455 | 0.99734 | -0.050558 | 25.318
30 | -0.00037548 | -9.4103e-05 | 0.00037548 | 9.3622e-05 | 4.3849e-09 | -4.8065e-07 | 0.00056105 | 0.00056088 | 0.00056105 | 0.99584 | -0.079134 | 0.99585 | -0.078889 | 0.15413
31 | -0.060738 | -0.015447 | 0.060805 | 0.01549 | 6.7308e-05 | 4.2793e-05 | 0.090836 | 0.090836 | 0.090836 | 0.99585 | -0.078889 | 0.99705 | -0.055916 | 24.9549
32 | -0.061415 | -0.015642 | 0.061431 | 0.015653 | 1.5877e-05 | 1.0095e-05 | 0.091746 | 0.091746 | 0.091746 | 0.99705 | -0.055916 | 0.99734 | -0.050558 | 25.2049

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.080587 | 0.02011

## res_load
| p_mw | q_mvar
0 | 0.0033801 | 0.00084713
1 | 0.010359 | 0.0025963
2 | 0.001954 | 0.00048972
3 | 0.0019841 | 0.00049725
4 | 0.00085584 | 0.00021449
5 | 0.00052862 | 0.00013248
6 | 0.0020447 | 0.00051244
7 | 0.0094528 | 0.0023691
8 | 0.0086249 | 0.0021616
9 | 0.0031301 | 0.00078448
10 | 0.0067 | 0.0016792
11 | 0.0072326 | 0.0018127
12 | 0.00085174 | 0.00021347
13 | 0.014257 | 0.0035731
14 | 0.00067752 | 0.0001698
15 | 0.00066272 | 0.00016609
16 | 0.0004743 | 0.00011887
17 | 0.0014719 | 0.00036889
18 | 0.0021076 | 0.00052822
19 | 0.00037548 | 9.4103e-05
20 | 0.00060996 | 0.00015287
21 | 0.00027593 | 6.9153e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1