## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-29_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-29_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-29_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-29_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1054-29_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1054-29_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1054-29_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1054-29_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1054-29_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1054-29_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1054-29_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1054-29_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1054-29_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1054-29_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1054-29_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1054-29_0_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1054-29_0_4_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1054-29_0_4_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1054-29_0_4_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1054-29_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1054-29_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1054-29_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1054-29_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1054-29_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1054-29_0_4_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1054-29_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1054-29_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1054-29_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1054-29_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1054-29_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1054-29_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1054-29_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1054-29_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1054-29_0_4_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_1054-29_0_4_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_1054-29_0_4_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_1054-29_0_4_node_54 | 0.4 | n |  | TRUE
37 | bus_LV_1054-29_0_4_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_1054-29_0_4_node_35 | 0.4 | n |  | TRUE
39 | bus_LV_1054-29_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_1054-29_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1054-29_0_4_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1054-29_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1054-29_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1054-29_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_1054-29_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1054-29_0_4_node_68 | 0.4 | n |  | TRUE
47 | bus_LV_1054-29_0_4_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_1054-29_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_1054-29_0_4_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_1054-29_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_1054-29_0_4_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1054-29_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1054-29_0_4_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1054-29_0_4_node_116 | 0.4 | n |  | TRUE
55 | bus_LV_1054-29_0_4_node_117 | 0.4 | n |  | TRUE
56 | bus_LV_1054-29_0_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_1054-29_0_4_node_118 | 0.4 | n |  | TRUE
58 | bus_LV_1054-29_0_4_node_67 | 0.4 | n |  | TRUE
59 | bus_LV_1054-29_0_4_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_1054-29_0_4_node_57 | 0.4 | n |  | TRUE
61 | bus_LV_1054-29_0_4_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_1054-29_0_4_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_1054-29_0_4_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_1054-29_0_4_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_1054-29_0_4_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_1054-29_0_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1054-29_0_4_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_1054-29_0_4_node_76 | 0.4 | n |  | TRUE
69 | bus_LV_1054-29_0_4_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1054-29_0_4_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_1054-29_0_4_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_1054-29_0_4_node_79 | 0.4 | n |  | TRUE
73 | bus_LV_1054-29_0_4_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_1054-29_0_4_node_120 | 0.4 | n |  | TRUE
75 | bus_LV_1054-29_0_4_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_1054-29_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1054-29_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_1054-29_0_4_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_1054-29_0_4_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_1054-29_0_4_node_81 | 0.4 | n |  | TRUE
81 | bus_LV_1054-29_0_4_node_83 | 0.4 | n |  | TRUE
82 | bus_LV_1054-29_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_1054-29_0_4_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_1054-29_0_4_node_86 | 0.4 | n |  | TRUE
85 | bus_LV_1054-29_0_4_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_1054-29_0_4_node_88 | 0.4 | n |  | TRUE
87 | bus_LV_1054-29_0_4_node_89 | 0.4 | n |  | TRUE
88 | bus_LV_1054-29_0_4_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_1054-29_0_4_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_1054-29_0_4_node_102 | 0.4 | n |  | TRUE
91 | bus_LV_1054-29_0_4_node_111 | 0.4 | n |  | TRUE
92 | bus_LV_1054-29_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_1054-29_0_4_node_99 | 0.4 | n |  | TRUE
94 | bus_LV_1054-29_0_4_node_124 | 0.4 | n |  | TRUE
95 | bus_LV_1054-29_0_4_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_1054-29_0_4_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_1054-29_0_4_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_1054-29_0_4_node_129 | 0.4 | n |  | TRUE
99 | bus_LV_1054-29_0_4_node_110 | 0.4 | n |  | TRUE
100 | bus_LV_1054-29_0_4_node_130 | 0.4 | n |  | TRUE
101 | bus_LV_1054-29_0_4_node_126 | 0.4 | n |  | TRUE
102 | bus_LV_1054-29_0_4_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_1054-29_0_4_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_1054-29_0_4_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1054-29_0_4_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_1054-29_0_4_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_1054-29_0_4_node_101 | 0.4 | n |  | TRUE
108 | bus_LV_1054-29_0_4_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_1054-29_0_4_node_112 | 0.4 | n |  | TRUE
110 | bus_LV_1054-29_0_4_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_1054-29_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_1054-29_0_4_node_106 | 0.4 | n |  | TRUE
113 | bus_LV_1054-29_0_4_node_108 | 0.4 | n |  | TRUE
114 | bus_LV_1054-29_0_4_node_109 | 0.4 | n |  | TRUE
115 | bus_LV_1054-29_0_4_node_123 | 0.4 | n |  | TRUE
116 | bus_LV_1054-29_0_4_node_113 | 0.4 | n |  | TRUE
117 | bus_LV_1054-29_0_4_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_1054-29_0_4_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_1054-29_0_4_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_1054-29_0_4_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_1054-29_0_4_node_125 | 0.4 | n |  | TRUE
122 | bus_LV_1054-29_0_4_node_127 | 0.4 | n |  | TRUE
123 | bus_LV_1054-29_0_4_node_128 | 0.4 | n |  | TRUE
124 | bus_MV_212_1_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-29_0_4_load_0 | 0 | 0.0077995 | 0.0019547 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-29_0_4_load_1 | 1 | 0.0033921 | 0.00085014 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-29_0_4_load_6 | 5 | 0.003025 | 0.00075814 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-29_0_4_load_8 | 7 | 0.0069191 | 0.0017341 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-29_0_4_load_18 | 8 | 0.0019879 | 0.00049821 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-29_0_4_load_15 | 9 | 0.0026879 | 0.00067366 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-29_0_4_load_30 | 10 | 0.0041195 | 0.0010325 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-29_0_4_load_10 | 11 | 0.0027687 | 0.0006939 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-29_0_4_load_24 | 12 | 0.0020156 | 0.00050515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-29_0_4_load_20 | 13 | 0.0019977 | 0.00050068 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-29_0_4_load_16 | 14 | 0.0023654 | 0.00059284 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-29_0_4_load_31 | 15 | 0.0046238 | 0.0011588 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-29_0_4_load_26 | 16 | 0.0017021 | 0.00042659 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-29_0_4_load_22 | 18 | 0.0042673 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-29_0_4_load_11 | 19 | 0.0042749 | 0.0010714 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-29_0_4_load_12 | 20 | 0.0033415 | 0.00083745 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-29_0_4_load_13 | 21 | 0.0017019 | 0.00042654 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-29_0_4_load_14 | 22 | 0.0017019 | 0.00042654 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-29_0_4_load_17 | 25 | 0.0040337 | 0.0010109 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-29_0_4_load_19 | 26 | 0.0020097 | 0.00050368 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-29_0_4_load_34 | 27 | 0.0035896 | 0.00089964 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-29_0_4_load_33 | 28 | 0.003009 | 0.00075412 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-29_0_4_load_28 | 29 | 0.0036832 | 0.0009231 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-29_0_4_load_21 | 30 | 0.0041884 | 0.0010497 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-29_0_4_load_29 | 31 | 0.0020883 | 0.00052338 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-29_0_4_load_43 | 32 | 0.0022071 | 0.00055316 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-29_0_4_load_44 | 33 | 0.0020712 | 0.00051909 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-29_0_4_load_45 | 34 | 0.0017563 | 0.00044016 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-29_0_4_load_54 | 36 | 0.0053824 | 0.0013489 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-29_0_4_load_55 | 37 | 0.029389 | 0.0073655 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-29_0_4_load_35 | 38 | 0.003343 | 0.00083784 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-29_0_4_load_36 | 39 | 0.0019156 | 0.0004801 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-29_0_4_load_39 | 42 | 0.0016802 | 0.0004211 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-29_0_4_load_40 | 43 | 0.0018678 | 0.00046811 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-29_0_4_load_41 | 44 | 0.0055805 | 0.0013986 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-29_0_4_load_42 | 45 | 0.0017148 | 0.00042978 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-29_0_4_load_68 | 46 | 0.0016069 | 0.00040273 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-29_0_4_load_69 | 47 | 0.030359 | 0.0076086 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-29_0_4_load_52 | 48 | 0.0018108 | 0.00045383 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-29_0_4_load_50 | 50 | 0.001689 | 0.00042329 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-29_0_4_load_51 | 53 | 0.0024234 | 0.00060736 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-29_0_4_load_116 | 54 | 0.0021689 | 0.00054359 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-29_0_4_load_117 | 55 | 0.0035427 | 0.00088789 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-29_0_4_load_53 | 56 | 0.0034361 | 0.00086117 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-29_0_4_load_118 | 57 | 0.0017432 | 0.00043688 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-29_0_4_load_67 | 58 | 0.0049978 | 0.0012526 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-29_0_4_load_63 | 59 | 0.0034159 | 0.00085611 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-29_0_4_load_57 | 60 | 0.0022783 | 0.000571 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-29_0_4_load_58 | 61 | 0.003276 | 0.00082103 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-29_0_4_load_60 | 63 | 0.0022035 | 0.00055226 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-29_0_4_load_62 | 65 | 0.0017253 | 0.00043241 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-29_0_4_load_64 | 66 | 0.0041935 | 0.001051 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-29_0_4_load_66 | 67 | 0.0017725 | 0.00044424 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-29_0_4_load_65 | 69 | 0.0059449 | 0.0014899 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-29_0_4_load_119 | 71 | 0.0014223 | 0.00035646 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-29_0_4_load_79 | 72 | 0.0027845 | 0.00069785 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-29_0_4_load_72 | 73 | 0.0045254 | 0.0011342 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-29_0_4_load_120 | 74 | 0.0012467 | 0.00031245 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-29_0_4_load_74 | 75 | 0.0065981 | 0.0016536 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-29_0_4_load_73 | 76 | 0.0059746 | 0.0014974 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-29_0_4_load_80 | 79 | 0.0088725 | 0.0022237 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-29_0_4_load_83 | 81 | 0.0085199 | 0.0021353 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-29_0_4_load_84 | 82 | 0.0058197 | 0.0014586 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-29_0_4_load_85 | 83 | 0.0040515 | 0.0010154 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-29_0_4_load_86 | 84 | 0.0050679 | 0.0012701 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-29_0_4_load_88 | 86 | 0.0040422 | 0.0010131 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-29_0_4_load_89 | 87 | 0.0028648 | 0.00071798 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-29_0_4_load_90 | 88 | 0.0030807 | 0.00077211 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-29_0_4_load_91 | 89 | 0.0059302 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-29_0_4_load_102 | 90 | 0.00040366 | 0.00010117 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-29_0_4_load_111 | 91 | 0.0032055 | 0.00080336 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-29_0_4_load_92 | 92 | 0.0052083 | 0.0013053 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-29_0_4_load_124 | 94 | 0.0019302 | 0.00048376 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-29_0_4_load_94 | 96 | 0.0033082 | 0.00082911 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-29_0_4_load_95 | 97 | 0.0023015 | 0.00057681 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-29_0_4_load_110 | 99 | 0.0040443 | 0.0010136 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-29_0_4_load_130 | 100 | 0.0049541 | 0.0012416 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-29_0_4_load_107 | 102 | 0.0034582 | 0.0008667 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-29_0_4_load_96 | 103 | 0.003597 | 0.00090151 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-29_0_4_load_97 | 104 | 0.00090539 | 0.00022691 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-29_0_4_load_98 | 105 | 0.0065713 | 0.0016469 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-29_0_4_load_100 | 106 | 0.0034612 | 0.00086746 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-29_0_4_load_101 | 107 | 0.0023813 | 0.0005968 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-29_0_4_load_103 | 108 | 0.0039597 | 0.0009924 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-29_0_4_load_112 | 109 | 0.0026353 | 0.00066048 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-29_0_4_load_104 | 110 | 0.0069586 | 0.001744 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-29_0_4_load_105 | 111 | 0.0039597 | 0.0009924 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-29_0_4_load_108 | 113 | 0.0039596 | 0.00099237 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-29_0_4_load_109 | 114 | 0.01247 | 0.0031254 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-29_0_4_load_123 | 115 | 0.0017158 | 0.00043001 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1054-29_0_4_load_115 | 118 | 0.0018518 | 0.00046411 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1054-29_0_4_load_121 | 119 | 0.0013144 | 0.00032943 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1054-29_0_4_load_122 | 120 | 0.0016078 | 0.00040294 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1054-29_0_4_load_125 | 121 | 0.0034082 | 0.00085418 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1054-29_0_4_load_127 | 122 | 0.0026553 | 0.00066548 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1054-29_0_4_load_128 | 123 | 0.0027249 | 0.00068291 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-29_0_4_line_0 |  | 0 | 1 | 0.0011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-29_0_4_line_1 |  | 0 | 2 | 0.01377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-29_0_4_line_2 |  | 1 | 3 | 0.019364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-29_0_4_line_3 |  | 2 | 4 | 0.022636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-29_0_4_line_4 |  | 3 | 5 | 0.030447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-29_0_4_line_5 |  | 4 | 6 | 0.021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-29_0_4_line_6 |  | 4 | 7 | 0.031869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-29_0_4_line_7 |  | 6 | 8 | 0.013863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-29_0_4_line_8 |  | 6 | 9 | 0.018528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-29_0_4_line_9 |  | 7 | 10 | 0.027354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-29_0_4_line_10 |  | 8 | 13 | 0.02575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-29_0_4_line_11 |  | 9 | 14 | 0.013466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-29_0_4_line_12 |  | 10 | 15 | 0.026156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-29_0_4_line_13 |  | 11 | 12 | 0.0030838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-29_0_4_line_14 |  | 12 | 18 | 0.0011951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-29_0_4_line_15 |  | 13 | 24 | 0.016452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-29_0_4_line_16 |  | 14 | 25 | 0.0087737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-29_0_4_line_17 |  | 16 | 17 | 0.0048691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-29_0_4_line_18 |  | 17 | 23 | 0.026425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-29_0_4_line_19 |  | 17 | 30 | 0.03539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-29_0_4_line_20 |  | 18 | 30 | 0.0083349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-29_0_4_line_21 |  | 19 | 20 | 0.026703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-29_0_4_line_22 |  | 20 | 21 | 0.0081076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-29_0_4_line_23 |  | 21 | 22 | 0.0061921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-29_0_4_line_24 |  | 22 | 23 | 0.030349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-29_0_4_line_25 |  | 23 | 24 | 0.02203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-29_0_4_line_26 |  | 24 | 29 | 0.0072542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-29_0_4_line_27 |  | 25 | 26 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-29_0_4_line_28 |  | 26 | 27 | 0.0088956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-29_0_4_line_29 |  | 27 | 28 | 0.010731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-29_0_4_line_30 |  | 28 | 38 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-29_0_4_line_31 |  | 31 | 32 | 0.025488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-29_0_4_line_32 |  | 32 | 33 | 0.023381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-29_0_4_line_33 |  | 32 | 34 | 0.015944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-29_0_4_line_34 |  | 33 | 51 | 0.01661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1054-29_0_4_line_35 |  | 34 | 52 | 0.0075193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-29_0_4_line_36 |  | 35 | 36 | 0.016779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1054-29_0_4_line_37 |  | 35 | 37 | 0.033101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1054-29_0_4_line_38 |  | 36 | 46 | 0.022515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1054-29_0_4_line_39 |  | 38 | 39 | 0.0073511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1054-29_0_4_line_40 |  | 39 | 40 | 0.013783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-29_0_4_line_41 |  | 40 | 41 | 0.002688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1054-29_0_4_line_42 |  | 40 | 42 | 0.012188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1054-29_0_4_line_43 |  | 41 | 43 | 0.0092752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1054-29_0_4_line_44 |  | 41 | 44 | 0.037953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-29_0_4_line_45 |  | 42 | 45 | 0.0078986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1054-29_0_4_line_46 |  | 43 | 46 | 0.0078831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1054-29_0_4_line_47 |  | 44 | 47 | 0.037978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1054-29_0_4_line_48 |  | 45 | 48 | 0.0082446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_1054-29_0_4_line_49 |  | 47 | 49 | 0.034886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-29_0_4_line_50 |  | 48 | 50 | 0.0081522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1054-29_0_4_line_51 |  | 49 | 70 | 0.017111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1054-29_0_4_line_52 |  | 50 | 51 | 0.016085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1054-29_0_4_line_53 |  | 51 | 53 | 0.0059563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1054-29_0_4_line_54 |  | 52 | 54 | 0.014249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1054-29_0_4_line_55 |  | 52 | 55 | 0.004648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-29_0_4_line_56 |  | 53 | 56 | 0.02265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1054-29_0_4_line_57 |  | 54 | 57 | 0.014244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-29_0_4_line_58 |  | 56 | 58 | 0.010751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1054-29_0_4_line_59 |  | 58 | 59 | 0.013557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1054-29_0_4_line_60 |  | 59 | 63 | 0.017316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1054-29_0_4_line_61 |  | 60 | 61 | 0.0077081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1054-29_0_4_line_62 |  | 60 | 62 | 0.017836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1054-29_0_4_line_63 |  | 61 | 63 | 0.0051674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_1054-29_0_4_line_64 |  | 62 | 64 | 0.014995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-29_0_4_line_65 |  | 62 | 65 | 0.066622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_1054-29_0_4_line_66 |  | 64 | 66 | 0.040554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1054-29_0_4_line_67 |  | 65 | 67 | 0.0017489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1054-29_0_4_line_68 |  | 66 | 68 | 0.033992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1054-29_0_4_line_69 |  | 67 | 71 | 0.043602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1054-29_0_4_line_70 |  | 68 | 72 | 0.012787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1054-29_0_4_line_71 |  | 69 | 70 | 0.024983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-29_0_4_line_72 |  | 70 | 73 | 0.035211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1054-29_0_4_line_73 |  | 71 | 74 | 0.012705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1054-29_0_4_line_74 |  | 73 | 75 | 0.018065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1054-29_0_4_line_75 |  | 74 | 117 | 0.017429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_1054-29_0_4_line_76 |  | 75 | 76 | 0.01652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-29_0_4_line_77 |  | 76 | 77 | 0.042941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-29_0_4_line_78 |  | 77 | 78 | 0.099867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-29_0_4_line_79 |  | 78 | 79 | 0.090081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-29_0_4_line_80 |  | 79 | 80 | 0.028466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1054-29_0_4_line_81 |  | 80 | 81 | 0.015862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1054-29_0_4_line_82 |  | 82 | 83 | 0.0062141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1054-29_0_4_line_83 |  | 82 | 84 | 0.000334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-29_0_4_line_84 |  | 83 | 85 | 0.019087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1054-29_0_4_line_85 |  | 84 | 86 | 0.020064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1054-29_0_4_line_86 |  | 85 | 87 | 0.014167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-29_0_4_line_87 |  | 85 | 88 | 0.011054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1054-29_0_4_line_88 |  | 86 | 89 | 0.017052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-29_0_4_line_89 |  | 87 | 90 | 0.0073491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1054-29_0_4_line_90 |  | 88 | 91 | 0.00024812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-29_0_4_line_91 |  | 89 | 92 | 0.00084251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1054-29_0_4_line_92 |  | 90 | 93 | 0.011615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1054-29_0_4_line_93 |  | 91 | 94 | 0.033062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_1054-29_0_4_line_94 |  | 93 | 107 | 0.039351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1054-29_0_4_line_95 |  | 93 | 104 | 0.008898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1054-29_0_4_line_96 |  | 94 | 115 | 0.00023761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1054-29_0_4_line_97 |  | 95 | 96 | 0.0070186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1054-29_0_4_line_98 |  | 95 | 97 | 0.016428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1054-29_0_4_line_99 |  | 96 | 98 | 0.016352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1054-29_0_4_line_100 |  | 97 | 99 | 0.0015246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1054-29_0_4_line_101 |  | 98 | 100 | 0.018433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1054-29_0_4_line_102 |  | 98 | 101 | 0.029118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-29_0_4_line_103 |  | 99 | 102 | 0.0056315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-29_0_4_line_104 |  | 101 | 123 | 0.004288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1054-29_0_4_line_105 |  | 101 | 121 | 0.015341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1054-29_0_4_line_106 |  | 102 | 112 | 0.015799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1054-29_0_4_line_107 |  | 103 | 104 | 0.0081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1054-29_0_4_line_108 |  | 103 | 105 | 0.018909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1054-29_0_4_line_109 |  | 105 | 106 | 0.011442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1054-29_0_4_line_110 |  | 106 | 108 | 0.0018193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1054-29_0_4_line_111 |  | 107 | 109 | 0.029518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1054-29_0_4_line_112 |  | 108 | 110 | 0.016006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1054-29_0_4_line_113 |  | 110 | 111 | 0.014337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1054-29_0_4_line_114 |  | 111 | 112 | 0.010671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1054-29_0_4_line_115 |  | 112 | 113 | 0.002458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1054-29_0_4_line_116 |  | 113 | 114 | 0.01406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1054-29_0_4_line_117 |  | 115 | 119 | 0.027254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_1054-29_0_4_line_118 |  | 116 | 117 | 0.011333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1054-29_0_4_line_119 |  | 116 | 118 | 0.012755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1054-29_0_4_line_120 |  | 117 | 119 | 0.014929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_1054-29_0_4_line_121 |  | 118 | 120 | 0.0023875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1054-29_0_4_line_122 |  | 121 | 122 | 0.0042218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-29_0_4_trafo_51 | 0.63 MVA 20/0.4 kV | 124 | 53 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2669318.9043 | 1215278.1946 | 2669318.1267 | 1215279.0645
1 | 2669328.0816 | 1215267.9285 | 2669321.6877 | 1215275.0809 | 2669318.9043 | 1215278.1946
2 | 2669305.222 | 1215293.5011 | 2669318.1267 | 1215279.0645
3 | 2669314.244 | 1215252.3467 | 2669312.9422 | 1215253.9325 | 2669328.0816 | 1215267.9285
4 | 2669305.222 | 1215293.5011 | 2669285.0525 | 1215270.6924
5 | 2669328.0894 | 1215235.2746 | 2669314.244 | 1215252.3467
6 | 2669314.244 | 1215252.3467 | 2669299.6084 | 1215240.7359 | 2669289.5895 | 1215232.1609
7 | 2669328.0894 | 1215235.2746 | 2669334.9428 | 1215223.2245
8 | 2669328.0894 | 1215235.2746 | 2669314.8165 | 1215222.3468
9 | 2669269.3819 | 1215213.7512 | 2669277.6293 | 1215221.9243 | 2669289.5895 | 1215232.1609
10 | 2669334.9428 | 1215223.2245 | 2669334.9428 | 1215223.2245 | 2669343.4608 | 1215217.5867 | 2669354.3521 | 1215206.5093
11 | 2669305.1697 | 1215212.9508 | 2669314.8165 | 1215222.3468
12 | 2669269.3819 | 1215213.7512 | 2669250.8035 | 1215195.34
13 | 2669368.2867 | 1215234.128 | 2669366.327 | 1215236.509 | 2669366.327 | 1215236.509
14 | 2669369.0462 | 1215233.2052 | 2669369.0462 | 1215233.2052 | 2669368.2867 | 1215234.128
15 | 2669365.8862 | 1215194.7775 | 2669362.6661 | 1215198.0533 | 2669354.3521 | 1215206.5093
16 | 2669298.6629 | 1215208.7922 | 2669303.472 | 1215213.4636 | 2669304.8336 | 1215212.6234 | 2669305.1697 | 1215212.9508
17 | 2669403.2999 | 1215225.699 | 2669407.0537 | 1215228.8002
18 | 2669403.2999 | 1215225.699 | 2669382.8931 | 1215208.8398
19 | 2669403.2999 | 1215225.699 | 2669400.378 | 1215228.8003 | 2669387.7827 | 1215242.1955 | 2669378.5317 | 1215239.6974 | 2669375.9243 | 1215237.9128
20 | 2669375.9243 | 1215237.9128 | 2669369.0462 | 1215233.2052
21 | 2669418.6969 | 1215178.3937 | 2669414.6384 | 1215174.154 | 2669410.9853 | 1215174.8342 | 2669412.8304 | 1215183.3388 | 2669410.5489 | 1215191.4396 | 2669410.5489 | 1215191.4396
22 | 2669410.5489 | 1215191.4396 | 2669413.7939 | 1215194.5015 | 2669411.1615 | 1215197.0242
23 | 2669411.1615 | 1215197.0242 | 2669406.6909 | 1215201.3086
24 | 2669382.8931 | 1215208.8398 | 2669387.6743 | 1215203.8923 | 2669389.5983 | 1215205.6158 | 2669398.5492 | 1215209.111 | 2669406.6909 | 1215201.3086
25 | 2669365.8862 | 1215194.7775 | 2669382.8931 | 1215208.8398
26 | 2669365.8862 | 1215194.7775 | 2669360.2953 | 1215190.1552
27 | 2669298.6629 | 1215208.7922 | 2669289.6074 | 1215199.9959
28 | 2669289.6074 | 1215199.9959 | 2669283.2266 | 1215193.7977
29 | 2669275.5293 | 1215186.3208 | 2669283.2266 | 1215193.7977
30 | 2669266.7839 | 1215179.0534 | 2669272.7118 | 1215185.0328 | 2669273.4568 | 1215184.3076 | 2669275.5293 | 1215186.3208
31 | 2669319.3998 | 1215154.4672 | 2669338.2793 | 1215171.5909
32 | 2669319.3998 | 1215154.4672 | 2669302.084 | 1215138.7559
33 | 2669319.3998 | 1215154.4672 | 2669323.1213 | 1215150.5302 | 2669330.3556 | 1215142.8837
34 | 2669289.7831 | 1215127.5949 | 2669302.084 | 1215138.7559
35 | 2669335.5234 | 1215137.4216 | 2669330.3556 | 1215142.8837
36 | 2669208.4071 | 1215203.0419 | 2669218.4428 | 1215198.8002 | 2669222.5341 | 1215194.572
37 | 2669208.4071 | 1215203.0419 | 2669200.0352 | 1215198.7309 | 2669184.3506 | 1215191.7446 | 2669178.08 | 1215189.9807
38 | 2669222.5341 | 1215194.572 | 2669230.4645 | 1215186.3763 | 2669233.9393 | 1215182.7477 | 2669237.1063 | 1215179.4602 | 2669238.1663 | 1215178.3685
39 | 2669266.7839 | 1215179.0534 | 2669261.6084 | 1215173.8329
40 | 2669251.9044 | 1215164.0446 | 2669261.6084 | 1215173.8329
41 | 2669251.9044 | 1215164.0446 | 2669250.1191 | 1215166.0584
42 | 2669251.9044 | 1215164.0446 | 2669253.8551 | 1215162.166 | 2669257.1423 | 1215159.0022 | 2669260.6857 | 1215155.5933
43 | 2669250.1191 | 1215166.0584 | 2669243.6578 | 1215172.7128
44 | 2669250.1191 | 1215166.0584 | 2669241.1122 | 1215156.9147 | 2669237.5683 | 1215154.0718 | 2669228.4735 | 1215151.1866 | 2669219.4019 | 1215144.9061
45 | 2669266.3778 | 1215150.1172 | 2669260.6857 | 1215155.5933
46 | 2669243.6578 | 1215172.7128 | 2669238.1663 | 1215178.3685
47 | 2669188.1774 | 1215123.2884 | 2669219.4019 | 1215144.9061
48 | 2669266.3778 | 1215150.1172 | 2669272.3193 | 1215144.4013
49 | 2669157.1305 | 1215108.8322 | 2669164.4868 | 1215109.718 | 2669173.8236 | 1215113.3509 | 2669188.1774 | 1215123.2884
50 | 2669278.1943 | 1215138.7494 | 2669272.3193 | 1215144.4013
51 | 2669153.0849 | 1215092.286 | 2669155.7762 | 1215099.8886 | 2669157.1305 | 1215108.8322
52 | 2669289.7831 | 1215127.5949 | 2669287.3869 | 1215129.9019 | 2669283.9538 | 1215133.2085 | 2669278.1943 | 1215138.7494
53 | 2669289.7831 | 1215127.5949 | 2669286.2435 | 1215124.3851 | 2669285.3497 | 1215123.6177
54 | 2669335.5234 | 1215137.4216 | 2669345.9919 | 1215147.088
55 | 2669338.7144 | 1215134.0344 | 2669335.5234 | 1215137.4216
56 | 2669268.1649 | 1215108.8629 | 2669285.3497 | 1215123.6177
57 | 2669356.2694 | 1215149.3148 | 2669349.7701 | 1215143.3132 | 2669346.0349 | 1215147.1278 | 2669345.9919 | 1215147.088
58 | 2669260.0357 | 1215101.8292 | 2669260.6854 | 1215102.4411 | 2669268.1649 | 1215108.8629
59 | 2669260.0357 | 1215101.8292 | 2669250.1666 | 1215092.5348
60 | 2669250.1666 | 1215092.5348 | 2669237.5609 | 1215080.6633
61 | 2669227.9156 | 1215072.1509 | 2669231.7109 | 1215075.1541 | 2669233.7991 | 1215077.1206
62 | 2669213.9288 | 1215061.0833 | 2669227.9156 | 1215072.1509
63 | 2669233.7991 | 1215077.1206 | 2669237.5609 | 1215080.6633
64 | 2669201.5655 | 1215052.5455 | 2669213.9288 | 1215061.0833
65 | 2669213.9288 | 1215061.0833 | 2669217.5594 | 1215055.811 | 2669215.758 | 1215046.7844 | 2669213.9209 | 1215034.9556 | 2669228.0025 | 1215032.8622 | 2669240.9344 | 1215032.9902 | 2669244.0678 | 1215032.6041 | 2669245.5852 | 1215031.421 | 2669244.9798 | 1215028.6233 | 2669243.1239 | 1215025.1557
66 | 2669201.5655 | 1215052.5455 | 2669177.8305 | 1215038.3612 | 2669166.821 | 1215031.6318
67 | 2669243.1239 | 1215025.1557 | 2669242.2986 | 1215023.6138
68 | 2669137.8181 | 1215013.9041 | 2669166.821 | 1215031.6318
69 | 2669229.2018 | 1214984.5346 | 2669229.2018 | 1214984.5346 | 2669226.7414 | 1214988.4418 | 2669226.8056 | 1214994.0239 | 2669233.7706 | 1215007.68 | 2669242.2986 | 1215023.6138
70 | 2669137.8181 | 1215013.9041 | 2669140.8119 | 1215007.8794 | 2669141.6182 | 1215001.8739
71 | 2669153.0849 | 1215092.286 | 2669156.9355 | 1215090.952 | 2669163.9292 | 1215093.6348 | 2669169.0172 | 1215081.2193
72 | 2669153.0849 | 1215092.286 | 2669149.1148 | 1215084.9353 | 2669141.0503 | 1215072.4339 | 2669133.9826 | 1215062.7607
73 | 2669229.2018 | 1214984.5346 | 2669233.3193 | 1214981.158 | 2669238.8959 | 1214976.3242
74 | 2669133.9826 | 1215062.7607 | 2669123.3249 | 1215048.174
75 | 2669250.9503 | 1214963.8074 | 2669247.6361 | 1214967.9826 | 2669243.8373 | 1214972.0411 | 2669238.8959 | 1214976.3242
76 | 2669113.5788 | 1215034.8349 | 2669123.3249 | 1215048.174
77 | 2669094.8331 | 1214998.2071 | 2669093.595 | 1215002.1619 | 2669094.3412 | 1215007.2293 | 2669098.3412 | 1215013.9799 | 2669113.5788 | 1215034.8349
78 | 2669008.5053 | 1215008.8142 | 2669012.9075 | 1215000.5155 | 2669017.9395 | 1214997.5051 | 2669035.0459 | 1214995.2239 | 2669059.0999 | 1214981.2714 | 2669089.0703 | 1214995.4719 | 2669094.8331 | 1214998.2071
79 | 2669008.5053 | 1215008.8142 | 2669010.6941 | 1215012.6086 | 2669038.418 | 1215060.7709 | 2669054.1846 | 1215086.4453
80 | 2669069.0828 | 1215110.7018 | 2669062.926 | 1215100.6798 | 2669054.1846 | 1215086.4453
81 | 2669069.0828 | 1215110.7018 | 2669082.7323 | 1215102.6215
82 | 2669333.9872 | 1215039.0169 | 2669329.6048 | 1215034.6112
83 | 2669334.2227 | 1215039.2537 | 2669333.9872 | 1215039.0169
84 | 2669316.144 | 1215021.0786 | 2669329.6048 | 1215034.6112
85 | 2669348.372 | 1215053.4785 | 2669334.2227 | 1215039.2537
86 | 2669316.144 | 1215021.0786 | 2669323.4085 | 1215013.5361 | 2669325.9826 | 1215010.8859
87 | 2669316.144 | 1215021.0786 | 2669307.94 | 1215013.6695
88 | 2669360.2362 | 1215065.7193 | 2669357.9335 | 1215063.091 | 2669348.372 | 1215053.4785
89 | 2669325.9826 | 1215010.8859 | 2669331.103 | 1215005.6141
90 | 2669307.94 | 1215013.6695 | 2669307.7559 | 1215013.5032
91 | 2669360.7914 | 1215066.353 | 2669360.2362 | 1215065.7193
92 | 2669339.1892 | 1214997.276 | 2669337.0445 | 1214999.4969 | 2669331.103 | 1215005.6141
93 | 2669307.7559 | 1215013.5032 | 2669283.4062 | 1214991.5129 | 2669283.214 | 1214991.3488
94 | 2669339.1892 | 1214997.276 | 2669325.0337 | 1214985.4706 | 2669309.1737 | 1214971.8297
95 | 2669339.1892 | 1214997.276 | 2669346.0217 | 1215002.976
96 | 2669283.214 | 1214991.3488 | 2669283.0333 | 1214991.1946
97 | 2669376.858 | 1215084.6914 | 2669381.647 | 1215089.8223
98 | 2669376.858 | 1215084.6914 | 2669384.1955 | 1215078.0503 | 2669385.6587 | 1215078.2675 | 2669389.5766 | 1215075.0777
99 | 2669392.8047 | 1215101.7766 | 2669381.647 | 1215089.8223
100 | 2669389.526 | 1215073.554 | 2669389.5766 | 1215075.0777 | 2669389.5766 | 1215075.0777
101 | 2669392.8047 | 1215101.7766 | 2669405.3678 | 1215115.2979
102 | 2669392.8047 | 1215101.7766 | 2669382.1427 | 1215111.5142 | 2669375.7389 | 1215117.5435 | 2669371.3636 | 1215121.5396
103 | 2669393.6118 | 1215069.6785 | 2669389.526 | 1215073.554 | 2669389.526 | 1215073.554
104 | 2669368.3616 | 1215118.4694 | 2669371.3636 | 1215121.5396
105 | 2669371.3636 | 1215121.5396 | 2669382.1047 | 1215132.4933
106 | 2669405.0613 | 1215058.7921 | 2669401.9509 | 1215061.7689 | 2669393.6118 | 1215069.6785
107 | 2669352.2416 | 1215008.1648 | 2669346.0217 | 1215002.976
108 | 2669352.2416 | 1215008.1648 | 2669357.8951 | 1215012.8811 | 2669366.169 | 1215020.9348
109 | 2669374.3678 | 1215028.9154 | 2669366.169 | 1215020.9348
110 | 2669375.6714 | 1215030.1844 | 2669374.3678 | 1215028.9154
111 | 2669309.1737 | 1214971.8297 | 2669295.3925 | 1214959.9768 | 2669290.4305 | 1214956.2946 | 2669285.7767 | 1214954.0606
112 | 2669387.1407 | 1215041.3484 | 2669375.6714 | 1215030.1844
113 | 2669387.1407 | 1215041.3484 | 2669397.4144 | 1215051.3487
114 | 2669405.0613 | 1215058.7921 | 2669397.4144 | 1215051.3487
115 | 2669405.0613 | 1215058.7921 | 2669406.8225 | 1215060.5069
116 | 2669416.8959 | 1215070.3149 | 2669406.8225 | 1215060.5069
117 | 2669283.0333 | 1214991.1946 | 2669262.3047 | 1214973.4999
118 | 2669250.9503 | 1214963.8074 | 2669242.3174 | 1214956.4358
119 | 2669242.3174 | 1214956.4358 | 2669232.0777 | 1214948.8299
120 | 2669250.9503 | 1214963.8074 | 2669262.3047 | 1214973.4999
121 | 2669230.1611 | 1214947.4062 | 2669232.0777 | 1214948.8299
122 | 2669385.0606 | 1215135.5077 | 2669382.1047 | 1215132.4933

## bus_geodata
| x | y | coords
0 | 2669318.9043 | 1215278.1946
1 | 2669318.1268 | 1215279.0645
2 | 2669328.0816 | 1215267.9285
3 | 2669305.222 | 1215293.5011
4 | 2669314.244 | 1215252.3467
5 | 2669285.0525 | 1215270.6924
6 | 2669328.0894 | 1215235.2746
7 | 2669289.5895 | 1215232.1609
8 | 2669334.9428 | 1215223.2245
9 | 2669314.8165 | 1215222.3468
10 | 2669269.3819 | 1215213.7512
11 | 2669366.327 | 1215236.509
12 | 2669368.2867 | 1215234.128
13 | 2669354.3521 | 1215206.5093
14 | 2669305.1697 | 1215212.9508
15 | 2669250.8035 | 1215195.34
16 | 2669407.0537 | 1215228.8002
17 | 2669403.2999 | 1215225.699
18 | 2669369.0462 | 1215233.2052
19 | 2669418.6969 | 1215178.3937
20 | 2669410.5489 | 1215191.4396
21 | 2669411.1615 | 1215197.0242
22 | 2669406.6909 | 1215201.3086
23 | 2669382.8931 | 1215208.8398
24 | 2669365.8862 | 1215194.7775
25 | 2669298.6629 | 1215208.7922
26 | 2669289.6074 | 1215199.9959
27 | 2669283.2266 | 1215193.7977
28 | 2669275.5293 | 1215186.3208
29 | 2669360.2953 | 1215190.1552
30 | 2669375.9243 | 1215237.9128
31 | 2669338.2793 | 1215171.5909
32 | 2669319.3998 | 1215154.4672
33 | 2669302.084 | 1215138.7559
34 | 2669330.3556 | 1215142.8837
35 | 2669208.4071 | 1215203.0419
36 | 2669222.5341 | 1215194.572
37 | 2669178.08 | 1215189.9807
38 | 2669266.7839 | 1215179.0534
39 | 2669261.6084 | 1215173.8329
40 | 2669251.9044 | 1215164.0446
41 | 2669250.1191 | 1215166.0584
42 | 2669260.6857 | 1215155.5933
43 | 2669243.6578 | 1215172.7128
44 | 2669219.4019 | 1215144.9061
45 | 2669266.3778 | 1215150.1172
46 | 2669238.1663 | 1215178.3685
47 | 2669188.1774 | 1215123.2884
48 | 2669272.3193 | 1215144.4013
49 | 2669157.1305 | 1215108.8322
50 | 2669278.1943 | 1215138.7494
51 | 2669289.7831 | 1215127.5949
52 | 2669335.5234 | 1215137.4216
53 | 2669285.3497 | 1215123.6177
54 | 2669345.9919 | 1215147.088
55 | 2669338.7144 | 1215134.0344
56 | 2669268.1649 | 1215108.8629
57 | 2669356.2694 | 1215149.3148
58 | 2669260.0357 | 1215101.8292
59 | 2669250.1666 | 1215092.5348
60 | 2669227.9156 | 1215072.1509
61 | 2669233.7991 | 1215077.1206
62 | 2669213.9288 | 1215061.0833
63 | 2669237.5609 | 1215080.6633
64 | 2669201.5655 | 1215052.5455
65 | 2669243.1239 | 1215025.1557
66 | 2669166.821 | 1215031.6318
67 | 2669242.2986 | 1215023.6138
68 | 2669137.8181 | 1215013.904
69 | 2669169.0172 | 1215081.2193
70 | 2669153.0849 | 1215092.286
71 | 2669229.2018 | 1214984.5346
72 | 2669141.6182 | 1215001.8739
73 | 2669133.9826 | 1215062.7607
74 | 2669238.8959 | 1214976.3242
75 | 2669123.3249 | 1215048.174
76 | 2669113.5788 | 1215034.8349
77 | 2669094.8331 | 1214998.2071
78 | 2669008.5053 | 1215008.8142
79 | 2669054.1846 | 1215086.4453
80 | 2669069.0828 | 1215110.7018
81 | 2669082.7323 | 1215102.6215
82 | 2669333.9872 | 1215039.0169
83 | 2669329.6048 | 1215034.6112
84 | 2669334.2227 | 1215039.2537
85 | 2669316.144 | 1215021.0786
86 | 2669348.372 | 1215053.4785
87 | 2669325.9826 | 1215010.8859
88 | 2669307.94 | 1215013.6695
89 | 2669360.2362 | 1215065.7193
90 | 2669331.103 | 1215005.6141
91 | 2669307.7559 | 1215013.5032
92 | 2669360.7914 | 1215066.353
93 | 2669339.1892 | 1214997.276
94 | 2669283.214 | 1214991.3488
95 | 2669376.858 | 1215084.6914
96 | 2669381.647 | 1215089.8223
97 | 2669389.5766 | 1215075.0777
98 | 2669392.8047 | 1215101.7766
99 | 2669389.526 | 1215073.554
100 | 2669405.3678 | 1215115.2979
101 | 2669371.3636 | 1215121.5396
102 | 2669393.6118 | 1215069.6785
103 | 2669352.2416 | 1215008.1648
104 | 2669346.0217 | 1215002.976
105 | 2669366.169 | 1215020.9348
106 | 2669374.3678 | 1215028.9154
107 | 2669309.1737 | 1214971.8297
108 | 2669375.6714 | 1215030.1844
109 | 2669285.7767 | 1214954.0606
110 | 2669387.1408 | 1215041.3484
111 | 2669397.4144 | 1215051.3487
112 | 2669405.0613 | 1215058.7921
113 | 2669406.8225 | 1215060.5069
114 | 2669416.8959 | 1215070.3149
115 | 2669283.0333 | 1214991.1946
116 | 2669242.3174 | 1214956.4358
117 | 2669250.9503 | 1214963.8074
118 | 2669232.0777 | 1214948.8299
119 | 2669262.3047 | 1214973.4999
120 | 2669230.1611 | 1214947.4062
121 | 2669382.1047 | 1215132.4933
122 | 2669385.0606 | 1215135.5077
123 | 2669368.3616 | 1215118.4694
124 | 2669289.7831 | 1215127.5949

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98609 | -0.26743 | 0.0077995 | 0.0019547
1 | 0.98609 | -0.26756 | 0.0033921 | 0.00085014
2 | 0.98627 | -0.26392 | 0 | 0
3 | 0.98603 | -0.26861 | 0 | 0
4 | 0.98657 | -0.25815 | 0 | 0
5 | 0.98595 | -0.27026 | 0.003025 | 0.00075814
6 | 0.98717 | -0.24641 | 0 | 0
7 | 0.98611 | -0.2671 | 0.0069191 | 0.0017341
8 | 0.98674 | -0.25475 | 0.0019879 | 0.00049821
9 | 0.98825 | -0.22538 | 0.0026879 | 0.00067366
10 | 0.98589 | -0.27139 | 0.0041195 | 0.0010325
11 | 0.98414 | -0.30551 | 0.0027687 | 0.0006939
12 | 0.98415 | -0.30536 | 0.0020156 | 0.00050515
13 | 0.98599 | -0.26935 | 0.0019977 | 0.00050068
14 | 0.98908 | -0.20948 | 0.0023654 | 0.00059284
15 | 0.98578 | -0.27356 | 0.0046238 | 0.0011588
16 | 0.98465 | -0.29562 | 0.0017021 | 0.00042659
17 | 0.98465 | -0.29547 | 0 | 0
18 | 0.98415 | -0.30526 | 0.0042673 | 0.0010695
19 | 0.98449 | -0.29859 | 0.0042749 | 0.0010714
20 | 0.9846 | -0.29653 | 0.0033415 | 0.00083745
21 | 0.98466 | -0.29542 | 0.0017019 | 0.00042654
22 | 0.98471 | -0.29439 | 0.0017019 | 0.00042654
23 | 0.98502 | -0.28837 | 0 | 0
24 | 0.98554 | -0.2781 | 0 | 0
25 | 0.98963 | -0.19877 | 0.0040337 | 0.0010109
26 | 0.99047 | -0.18247 | 0.0020097 | 0.00050368
27 | 0.99108 | -0.17068 | 0.0035896 | 0.00089964
28 | 0.99185 | -0.1558 | 0.003009 | 0.00075412
29 | 0.98552 | -0.27858 | 0.0036832 | 0.0009231
30 | 0.98422 | -0.3039 | 0.0041884 | 0.0010497
31 | 0.99882 | -0.022578 | 0.0020883 | 0.00052338
32 | 0.99887 | -0.021648 | 0.0022071 | 0.00055316
33 | 0.99915 | -0.016131 | 0.0020712 | 0.00051909
34 | 0.99873 | -0.024214 | 0.0017563 | 0.00044016
35 | 0.99241 | -0.14534 | 0 | 0
36 | 0.99286 | -0.13661 | 0.0053824 | 0.0013489
37 | 0.99152 | -0.16257 | 0.029389 | 0.0073655
38 | 0.99278 | -0.13805 | 0.003343 | 0.00083784
39 | 0.99335 | -0.12706 | 0.0019156 | 0.0004801
40 | 0.99444 | -0.10603 | 0 | 0
41 | 0.99416 | -0.11146 | 0 | 0
42 | 0.99557 | -0.084453 | 0.0016802 | 0.0004211
43 | 0.99384 | -0.11772 | 0.0018678 | 0.00046811
44 | 0.9915 | -0.16273 | 0.0055805 | 0.0013986
45 | 0.99631 | -0.070379 | 0.0017148 | 0.00042978
46 | 0.99357 | -0.12278 | 0.0016069 | 0.00040273
47 | 0.98902 | -0.21052 | 0.030359 | 0.0076086
48 | 0.99708 | -0.055587 | 0.0018108 | 0.00045383
49 | 0.98772 | -0.2357 | 0 | 0
50 | 0.99785 | -0.040854 | 0.001689 | 0.00042329
51 | 0.99939 | -0.011614 | 0 | 0
52 | 0.99868 | -0.025194 | 0 | 0
53 | 1 | 0 | -0.38919 | -0.099206
54 | 0.99863 | -0.026168 | 0.0021689 | 0.00054359
55 | 0.99867 | -0.025481 | 0.0035427 | 0.00088789
56 | 0.99833 | -0.031358 | 0.0034361 | 0.00086117
57 | 0.99861 | -0.026602 | 0.0017432 | 0.00043688
58 | 0.99756 | -0.045954 | 0.0049978 | 0.0012526
59 | 0.99661 | -0.063799 | 0.0034159 | 0.00085611
60 | 0.99458 | -0.10228 | 0.0022783 | 0.000571
61 | 0.99509 | -0.092691 | 0.003276 | 0.00082103
62 | 0.99343 | -0.12414 | 0 | 0
63 | 0.99543 | -0.08612 | 0.0022035 | 0.00055226
64 | 0.99333 | -0.12599 | 0 | 0
65 | 0.98934 | -0.20212 | 0.0017253 | 0.00043241
66 | 0.99308 | -0.13099 | 0.0041935 | 0.001051
67 | 0.98923 | -0.20415 | 0.0017725 | 0.00044424
68 | 0.99299 | -0.13267 | 0 | 0
69 | 0.98695 | -0.25073 | 0.0059449 | 0.0014899
70 | 0.98708 | -0.24807 | 0 | 0
71 | 0.98663 | -0.25418 | 0.0014223 | 0.00035646
72 | 0.99296 | -0.1333 | 0.0027845 | 0.00069785
73 | 0.98596 | -0.26983 | 0.0045254 | 0.0011342
74 | 0.98588 | -0.26864 | 0.0012467 | 0.00031245
75 | 0.98546 | -0.27954 | 0.0065981 | 0.0016536
76 | 0.98511 | -0.28648 | 0.0059746 | 0.0014974
77 | 0.98442 | -0.29991 | 0 | 0
78 | 0.98281 | -0.33121 | 0 | 0
79 | 0.98137 | -0.35952 | 0.0088725 | 0.0022237
80 | 0.98114 | -0.36391 | 0 | 0
81 | 0.98102 | -0.36636 | 0.0085199 | 0.0021353
82 | 0.9788 | -0.40606 | 0.0058197 | 0.0014586
83 | 0.97895 | -0.40311 | 0.0040515 | 0.0010154
84 | 0.97879 | -0.40618 | 0.0050679 | 0.0012701
85 | 0.97948 | -0.39266 | 0 | 0
86 | 0.97851 | -0.41173 | 0.0040422 | 0.0010131
87 | 0.97841 | -0.41353 | 0.0028648 | 0.00071798
88 | 0.98063 | -0.37037 | 0.0030807 | 0.00077211
89 | 0.97834 | -0.41518 | 0.0059302 | 0.0014862
90 | 0.97788 | -0.42399 | 0.00040366 | 0.00010117
91 | 0.98065 | -0.36986 | 0.0032055 | 0.00080336
92 | 0.97833 | -0.41526 | 0.0052083 | 0.0013053
93 | 0.97704 | -0.44046 | 0 | 0
94 | 0.98246 | -0.33475 | 0.0019302 | 0.00048376
95 | 0.97125 | -0.55437 | 0 | 0
96 | 0.97114 | -0.55658 | 0.0033082 | 0.00082911
97 | 0.97151 | -0.5492 | 0.0023015 | 0.00057681
98 | 0.97093 | -0.56074 | 0 | 0
99 | 0.97154 | -0.54865 | 0.0040443 | 0.0010136
100 | 0.97084 | -0.56243 | 0.0049541 | 0.0012416
101 | 0.97069 | -0.56547 | 0 | 0
102 | 0.97166 | -0.54622 | 0.0034582 | 0.0008667
103 | 0.97589 | -0.46292 | 0.003597 | 0.00090151
104 | 0.97643 | -0.45228 | 0.00090539 | 0.00022691
105 | 0.97469 | -0.48655 | 0.0065713 | 0.0016469
106 | 0.97403 | -0.49949 | 0.0034612 | 0.00086746
107 | 0.97685 | -0.44407 | 0.0023813 | 0.0005968
108 | 0.97393 | -0.50144 | 0.0039597 | 0.0009924
109 | 0.97678 | -0.44549 | 0.0026353 | 0.00066048
110 | 0.97312 | -0.51739 | 0.0069586 | 0.001744
111 | 0.97249 | -0.52987 | 0.0039597 | 0.0009924
112 | 0.97206 | -0.53839 | 0 | 0
113 | 0.97202 | -0.53913 | 0.0039596 | 0.00099237
114 | 0.97186 | -0.54237 | 0.01247 | 0.0031254
115 | 0.98247 | -0.33449 | 0.0017158 | 0.00043001
116 | 0.98482 | -0.28903 | 0 | 0
117 | 0.98486 | -0.28833 | 0 | 0
118 | 0.98478 | -0.28982 | 0.0018518 | 0.00046411
119 | 0.98401 | -0.30475 | 0.0013144 | 0.00032943
120 | 0.98478 | -0.28989 | 0.0016078 | 0.00040294
121 | 0.9706 | -0.56719 | 0.0034082 | 0.00085418
122 | 0.97059 | -0.5674 | 0.0026553 | 0.00066548
123 | 0.97068 | -0.56569 | 0.0027249 | 0.00068291
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0064176 | 0.0016079 | -0.0064175 | -0.0016079 | 4.1032e-08 | 1.1376e-08 | 0.0096839 | 0.0096839 | 0.0096839 | 0.98609 | -0.26743 | 0.98609 | -0.26756 | 2.6604
1 | -0.014217 | -0.0035627 | 0.014219 | 0.003564 | 2.3766e-06 | 1.3453e-06 | 0.021453 | 0.021453 | 0.021453 | 0.98609 | -0.26743 | 0.98627 | -0.26392 | 5.8938
2 | 0.0030254 | 0.00075775 | -0.0030252 | -0.0007579 | 1.5134e-07 | -1.5015e-07 | 0.0045652 | 0.0045653 | 0.0045653 | 0.98609 | -0.26756 | 0.98603 | -0.26861 | 1.2542
3 | -0.014219 | -0.003564 | 0.014223 | 0.0035662 | 3.9068e-06 | 2.2114e-06 | 0.021453 | 0.021453 | 0.021453 | 0.98627 | -0.26392 | 0.98657 | -0.25815 | 5.8938
4 | 0.0030252 | 0.0007579 | -0.003025 | -0.00075814 | 2.3797e-07 | -2.3603e-07 | 0.0045653 | 0.0045654 | 0.0045654 | 0.98603 | -0.26861 | 0.98595 | -0.27026 | 1.2542
5 | -0.029895 | -0.0074962 | 0.029911 | 0.0075066 | 1.6742e-05 | 1.0434e-05 | 0.045091 | 0.045091 | 0.045091 | 0.98657 | -0.25815 | 0.98717 | -0.24641 | 12.3876
6 | 0.015671 | 0.00393 | -0.015665 | -0.0039261 | 6.6774e-06 | 3.8668e-06 | 0.023637 | 0.023638 | 0.023638 | 0.98657 | -0.25815 | 0.98611 | -0.2671 | 6.4938
7 | 0.033707 | 0.0084745 | -0.033694 | -0.0084661 | 1.3425e-05 | 8.4149e-06 | 0.050818 | 0.050818 | 0.050818 | 0.98717 | -0.24641 | 0.98674 | -0.25475 | 13.9611
8 | -0.063619 | -0.015981 | 0.063683 | 0.016022 | 6.3912e-05 | 4.0667e-05 | 0.095909 | 0.095909 | 0.095909 | 0.98717 | -0.24641 | 0.98825 | -0.22538 | 26.3486
9 | 0.0087455 | 0.002192 | -0.0087438 | -0.0021912 | 1.7865e-06 | 7.9446e-07 | 0.013197 | 0.013197 | 0.013197 | 0.98611 | -0.2671 | 0.98589 | -0.27139 | 3.6256
10 | 0.031706 | 0.0079679 | -0.031684 | -0.0079541 | 2.2082e-05 | 1.3804e-05 | 0.047821 | 0.047821 | 0.047821 | 0.98674 | -0.25475 | 0.98599 | -0.26935 | 13.1375
11 | -0.06637 | -0.016695 | 0.066421 | 0.016728 | 5.0455e-05 | 3.2118e-05 | 0.099956 | 0.099956 | 0.099956 | 0.98825 | -0.22538 | 0.98908 | -0.20948 | 27.4604
12 | 0.0046242 | 0.0011588 | -0.0046238 | -0.0011588 | 4.7779e-07 | -2.7707e-08 | 0.0069794 | 0.0069795 | 0.0069795 | 0.98589 | -0.27139 | 0.98578 | -0.27356 | 1.9174
13 | -0.0027687 | -0.0006939 | 0.0027687 | 0.00069387 | 2.0266e-08 | -2.6214e-08 | 0.0041862 | 0.0041862 | 0.0041862 | 0.98414 | -0.30551 | 0.98415 | -0.30536 | 1.1501
14 | -0.0047843 | -0.001199 | 0.0047843 | 0.001199 | 2.3452e-08 | -1.7713e-10 | 0.0072337 | 0.0072337 | 0.0072337 | 0.98415 | -0.30536 | 0.98415 | -0.30526 | 1.9873
15 | 0.029686 | 0.0074534 | -0.029674 | -0.0074457 | 1.2386e-05 | 7.7171e-06 | 0.044806 | 0.044806 | 0.044806 | 0.98599 | -0.26935 | 0.98554 | -0.2781 | 12.3093
16 | -0.068786 | -0.01732 | 0.068822 | 0.017343 | 3.5255e-05 | 2.245e-05 | 0.10351 | 0.10351 | 0.10351 | 0.98908 | -0.20948 | 0.98963 | -0.19877 | 28.4381
17 | -0.0017021 | -0.00042659 | 0.0017021 | 0.00042654 | 1.2081e-08 | -5.4201e-08 | 0.0025723 | 0.0025723 | 0.0025723 | 0.98465 | -0.29562 | 0.98465 | -0.29547 | 0.70667
18 | -0.014948 | -0.003748 | 0.014953 | 0.0037509 | 5.0569e-06 | 2.9002e-06 | 0.02259 | 0.02259 | 0.02259 | 0.98465 | -0.29547 | 0.98502 | -0.28837 | 6.2061
19 | 0.013246 | 0.0033214 | -0.013241 | -0.0033185 | 5.318e-06 | 2.9536e-06 | 0.020018 | 0.020018 | 0.020018 | 0.98465 | -0.29547 | 0.98422 | -0.3039 | 5.4995
20 | -0.0090516 | -0.0022685 | 0.0090522 | 0.0022688 | 5.8543e-07 | 2.6876e-07 | 0.013686 | 0.013686 | 0.013686 | 0.98415 | -0.30526 | 0.98422 | -0.3039 | 3.7598
21 | -0.0042749 | -0.0010714 | 0.0042754 | 0.0010713 | 4.1806e-07 | -7.2026e-08 | 0.0064614 | 0.0064613 | 0.0064614 | 0.98449 | -0.29859 | 0.9846 | -0.29653 | 1.7751
22 | -0.0076168 | -0.0019088 | 0.0076172 | 0.0019089 | 4.0287e-07 | 1.5472e-07 | 0.011511 | 0.011511 | 0.011511 | 0.9846 | -0.29653 | 0.98466 | -0.29542 | 3.1624
23 | -0.0093191 | -0.0023355 | 0.0093196 | 0.0023357 | 4.6054e-07 | 2.1598e-07 | 0.014083 | 0.014083 | 0.014083 | 0.98466 | -0.29542 | 0.98471 | -0.29439 | 3.869
24 | -0.011022 | -0.0027622 | 0.011025 | 0.0027639 | 3.1569e-06 | 1.6342e-06 | 0.016655 | 0.016655 | 0.016655 | 0.98471 | -0.29439 | 0.98502 | -0.28837 | 4.5755
25 | -0.025978 | -0.0065147 | 0.02599 | 0.0065226 | 1.2724e-05 | 7.8625e-06 | 0.039245 | 0.039245 | 0.039245 | 0.98502 | -0.28837 | 0.98554 | -0.2781 | 10.7815
26 | 0.0036833 | 0.00092306 | -0.0036832 | -0.0009231 | 8.4131e-08 | -3.8592e-08 | 0.0055612 | 0.0055612 | 0.0055612 | 0.98554 | -0.2781 | 0.98552 | -0.27858 | 1.5278
27 | -0.072855 | -0.018354 | 0.072912 | 0.01839 | 5.6847e-05 | 3.622e-05 | 0.10958 | 0.10958 | 0.10958 | 0.98963 | -0.19877 | 0.99047 | -0.18247 | 30.1043
28 | -0.074922 | -0.018894 | 0.074964 | 0.018921 | 4.2293e-05 | 2.6953e-05 | 0.1126 | 0.1126 | 0.1126 | 0.99047 | -0.18247 | 0.99108 | -0.17068 | 30.9337
29 | -0.078554 | -0.01982 | 0.07861 | 0.019856 | 5.602e-05 | 3.5715e-05 | 0.11799 | 0.11799 | 0.11799 | 0.99108 | -0.17068 | 0.99185 | -0.1558 | 32.4144
30 | -0.081619 | -0.02061 | 0.081688 | 0.020654 | 6.9493e-05 | 4.4316e-05 | 0.1225 | 0.1225 | 0.1225 | 0.99185 | -0.1558 | 0.99278 | -0.13805 | 33.6545
31 | -0.0020883 | -0.00052338 | 0.0020884 | 0.00052311 | 9.251e-08 | -2.7441e-07 | 0.0031111 | 0.003111 | 0.0031111 | 0.99882 | -0.022578 | 0.99887 | -0.021648 | 0.8547
32 | -0.013508 | -0.0033852 | 0.013512 | 0.0033871 | 3.5506e-06 | 1.9662e-06 | 0.020123 | 0.020123 | 0.020123 | 0.99887 | -0.021648 | 0.99915 | -0.016131 | 5.5284
33 | 0.0092129 | 0.0023089 | -0.0092117 | -0.0023084 | 1.1262e-06 | 5.1209e-07 | 0.013724 | 0.013724 | 0.013724 | 0.99887 | -0.021648 | 0.99873 | -0.024214 | 3.7705
34 | -0.015583 | -0.0039062 | 0.015586 | 0.0039081 | 3.3547e-06 | 1.9294e-06 | 0.023208 | 0.023208 | 0.023208 | 0.99915 | -0.016131 | 0.99939 | -0.011614 | 6.3758
35 | 0.0074555 | 0.0018682 | -0.0074551 | -0.0018681 | 3.4791e-07 | 1.2427e-07 | 0.011108 | 0.011108 | 0.011108 | 0.99873 | -0.024214 | 0.99868 | -0.025194 | 3.0516
36 | -0.029413 | -0.0073806 | 0.029425 | 0.0073882 | 1.224e-05 | 7.6165e-06 | 0.044105 | 0.044105 | 0.044105 | 0.99241 | -0.14534 | 0.99286 | -0.13661 | 12.1168
37 | 0.029413 | 0.0073806 | -0.029389 | -0.0073655 | 2.4146e-05 | 1.5026e-05 | 0.044105 | 0.044105 | 0.044105 | 0.99241 | -0.14534 | 0.99152 | -0.16257 | 12.1168
38 | -0.034808 | -0.0087371 | 0.034831 | 0.0087516 | 2.2981e-05 | 1.4417e-05 | 0.052172 | 0.052172 | 0.052172 | 0.99286 | -0.13661 | 0.99357 | -0.12278 | 14.3329
39 | -0.085031 | -0.021492 | 0.085076 | 0.021521 | 4.4822e-05 | 2.8591e-05 | 0.12751 | 0.12751 | 0.12751 | 0.99278 | -0.13805 | 0.99335 | -0.12706 | 35.031
40 | -0.086992 | -0.022001 | 0.08708 | 0.022057 | 8.7867e-05 | 5.6056e-05 | 0.13038 | 0.13038 | 0.13038 | 0.99335 | -0.12706 | 0.99444 | -0.10603 | 35.8194
41 | 0.11528 | 0.029139 | -0.11525 | -0.02912 | 3.0022e-05 | 1.9179e-05 | 0.17258 | 0.17258 | 0.17258 | 0.99444 | -0.10603 | 0.99416 | -0.11146 | 47.4119
42 | -0.20236 | -0.051196 | 0.20257 | 0.05133 | 0.00020975 | 0.00013392 | 0.30296 | 0.30296 | 0.30296 | 0.99444 | -0.10603 | 0.99557 | -0.084453 | 41.6156
43 | 0.038326 | 0.0096351 | -0.038314 | -0.0096279 | 1.145e-05 | 7.2075e-06 | 0.057375 | 0.057375 | 0.057375 | 0.99416 | -0.11146 | 0.99384 | -0.11772 | 15.7623
44 | 0.076921 | 0.019485 | -0.076732 | -0.019364 | 0.0001889 | 0.0001204 | 0.1152 | 0.11521 | 0.11521 | 0.99416 | -0.11146 | 0.9915 | -0.16273 | 31.6497
45 | -0.20425 | -0.051751 | 0.20438 | 0.051839 | 0.0001382 | 8.824e-05 | 0.30547 | 0.30547 | 0.30547 | 0.99557 | -0.084453 | 0.99631 | -0.070379 | 41.9606
46 | 0.036446 | 0.0091598 | -0.036438 | -0.0091543 | 8.8057e-06 | 5.5336e-06 | 0.054578 | 0.054578 | 0.054578 | 0.99384 | -0.11772 | 0.99357 | -0.12278 | 14.994
47 | 0.071152 | 0.017966 | -0.070989 | -0.017862 | 0.00016253 | 0.00010353 | 0.10683 | 0.10683 | 0.10683 | 0.9915 | -0.16273 | 0.98902 | -0.21052 | 29.349
48 | -0.2061 | -0.052269 | 0.20625 | 0.052363 | 0.00014668 | 9.366e-05 | 0.30803 | 0.30803 | 0.30803 | 0.99631 | -0.070379 | 0.99708 | -0.055587 | 42.3124
49 | 0.04063 | 0.010253 | -0.040581 | -0.010223 | 4.8927e-05 | 3.0866e-05 | 0.061155 | 0.061155 | 0.061155 | 0.98902 | -0.21052 | 0.98772 | -0.2357 | 16.8008
50 | -0.20806 | -0.052816 | 0.2082 | 0.052911 | 0.00014759 | 9.4246e-05 | 0.31074 | 0.31074 | 0.31074 | 0.99708 | -0.055587 | 0.99785 | -0.040854 | 42.6836
51 | 0.040581 | 0.010223 | -0.040557 | -0.010207 | 2.3998e-05 | 1.514e-05 | 0.061155 | 0.061155 | 0.061155 | 0.98772 | -0.2357 | 0.98708 | -0.24807 | 16.8008
52 | -0.20989 | -0.053334 | 0.21019 | 0.053523 | 0.00029595 | 0.00018899 | 0.31325 | 0.31325 | 0.31325 | 0.99785 | -0.040854 | 0.99939 | -0.011614 | 43.0295
53 | -0.22578 | -0.057431 | 0.2259 | 0.057512 | 0.00012643 | 8.076e-05 | 0.33646 | 0.33646 | 0.33646 | 0.99939 | -0.011614 | 1 | 0 | 46.2174
54 | 0.0039123 | 0.00098024 | -0.0039122 | -0.00098031 | 1.8156e-07 | -7.0231e-08 | 0.0058292 | 0.0058293 | 0.0058293 | 0.99868 | -0.025194 | 0.99863 | -0.026168 | 1.6014
55 | 0.0035428 | 0.00088786 | -0.0035427 | -0.00088789 | 4.8568e-08 | -2.9734e-08 | 0.0052787 | 0.0052787 | 0.0052787 | 0.99868 | -0.025194 | 0.99867 | -0.025481 | 1.4502
56 | 0.16164 | 0.041694 | -0.16139 | -0.041537 | 0.00024655 | 0.0001572 | 0.24094 | 0.24094 | 0.24094 | 1 | 0 | 0.99833 | -0.031358 | 33.0965
57 | 0.0017432 | 0.00043672 | -0.0017432 | -0.00043688 | 3.6037e-08 | -1.6329e-07 | 0.0025974 | 0.0025975 | 0.0025975 | 0.99863 | -0.026168 | 0.99861 | -0.026602 | 0.71359
58 | 0.15796 | 0.040676 | -0.15784 | -0.040604 | 0.0001121 | 7.1462e-05 | 0.23582 | 0.23582 | 0.23582 | 0.99833 | -0.031358 | 0.99756 | -0.045954 | 32.3931
59 | 0.15285 | 0.039352 | -0.15271 | -0.039267 | 0.00013256 | 8.4487e-05 | 0.22837 | 0.22837 | 0.22837 | 0.99756 | -0.045954 | 0.99661 | -0.063799 | 31.369
60 | 0.1493 | 0.038411 | -0.14914 | -0.038308 | 0.00016184 | 0.00010313 | 0.22327 | 0.22327 | 0.22327 | 0.99661 | -0.063799 | 0.99543 | -0.08612 | 30.6685
61 | -0.14354 | -0.036862 | 0.14361 | 0.036905 | 6.6854e-05 | 4.2586e-05 | 0.21507 | 0.21507 | 0.21507 | 0.99458 | -0.10228 | 0.99509 | -0.092691 | 29.5432
62 | 0.14126 | 0.036291 | -0.14111 | -0.036196 | 0.00014983 | 9.5429e-05 | 0.21167 | 0.21167 | 0.21167 | 0.99458 | -0.10228 | 0.99343 | -0.12414 | 29.075
63 | -0.14689 | -0.037726 | 0.14693 | 0.037756 | 4.6882e-05 | 2.987e-05 | 0.21997 | 0.21997 | 0.21997 | 0.99509 | -0.092691 | 0.99543 | -0.08612 | 30.2161
64 | 0.0069806 | 0.0017492 | -0.00698 | -0.001749 | 6.1475e-07 | 1.9931e-07 | 0.010456 | 0.010456 | 0.010456 | 0.99343 | -0.12414 | 0.99333 | -0.12599 | 2.8725
65 | 0.13413 | 0.034447 | -0.13363 | -0.034125 | 0.00050573 | 0.00032195 | 0.20121 | 0.20121 | 0.20121 | 0.99343 | -0.12414 | 0.98934 | -0.20212 | 27.6389
66 | 0.00698 | 0.001749 | -0.0069783 | -0.0017484 | 1.6626e-06 | 5.3924e-07 | 0.010456 | 0.010456 | 0.010456 | 0.99333 | -0.12599 | 0.99308 | -0.13099 | 2.8725
67 | 0.1319 | 0.033692 | -0.13189 | -0.033684 | 1.2936e-05 | 8.2341e-06 | 0.19862 | 0.19862 | 0.19862 | 0.98934 | -0.20212 | 0.98923 | -0.20415 | 27.2824
68 | 0.0027848 | 0.00069745 | -0.0027846 | -0.00069774 | 2.2193e-07 | -2.9772e-07 | 0.0041725 | 0.0041727 | 0.0041727 | 0.99308 | -0.13099 | 0.99299 | -0.13267 | 1.1463
69 | 0.13012 | 0.03324 | -0.1298 | -0.03304 | 0.0003139 | 0.00019978 | 0.19595 | 0.19595 | 0.19595 | 0.98923 | -0.20415 | 0.98663 | -0.25418 | 26.9162
70 | 0.0027846 | 0.00069774 | -0.0027845 | -0.00069785 | 8.3489e-08 | -1.1197e-07 | 0.0041727 | 0.0041727 | 0.0041727 | 0.99299 | -0.13267 | 0.99296 | -0.1333 | 1.1464
71 | -0.0059449 | -0.0014899 | 0.0059456 | 0.0014901 | 7.5265e-07 | 1.6239e-07 | 0.0089631 | 0.008963 | 0.0089631 | 0.98695 | -0.25073 | 0.98708 | -0.24807 | 2.4624
72 | 0.034612 | 0.0087173 | -0.034576 | -0.0086947 | 3.5968e-05 | 2.257e-05 | 0.052192 | 0.052192 | 0.052192 | 0.98708 | -0.24807 | 0.98596 | -0.26983 | 14.3385
73 | 0.12838 | 0.032684 | -0.12829 | -0.032627 | 8.9475e-05 | 5.694e-05 | 0.19381 | 0.19381 | 0.19381 | 0.98663 | -0.25418 | 0.98588 | -0.26864 | 26.6216
74 | 0.03005 | 0.0075606 | -0.030036 | -0.0075519 | 1.394e-05 | 8.6914e-06 | 0.045362 | 0.045362 | 0.045362 | 0.98596 | -0.26983 | 0.98546 | -0.27954 | 12.4622
75 | 0.12705 | 0.032314 | -0.12692 | -0.032238 | 0.00012037 | 7.6595e-05 | 0.19192 | 0.19192 | 0.19192 | 0.98588 | -0.26864 | 0.98486 | -0.28833 | 26.3631
76 | 0.023438 | 0.0058982 | -0.023431 | -0.0058935 | 7.7633e-06 | 4.7581e-06 | 0.0354 | 0.0354 | 0.0354 | 0.98546 | -0.27954 | 0.98511 | -0.28648 | 9.7252
77 | 0.017456 | 0.0043961 | -0.017445 | -0.0043895 | 1.1202e-05 | 6.6229e-06 | 0.026375 | 0.026375 | 0.026375 | 0.98511 | -0.28648 | 0.98442 | -0.29991 | 7.2459
78 | 0.017445 | 0.0043895 | -0.017419 | -0.0043741 | 2.6053e-05 | 1.5406e-05 | 0.026375 | 0.026376 | 0.026376 | 0.98442 | -0.29991 | 0.98281 | -0.33121 | 7.246
79 | 0.017419 | 0.0043741 | -0.017395 | -0.0043602 | 2.3501e-05 | 1.39e-05 | 0.026376 | 0.026376 | 0.026376 | 0.98281 | -0.33121 | 0.98137 | -0.35952 | 7.2462
80 | 0.0085227 | 0.0021365 | -0.0085209 | -0.0021357 | 1.7827e-06 | 7.8136e-07 | 0.012923 | 0.012923 | 0.012923 | 0.98137 | -0.35952 | 0.98114 | -0.36391 | 3.5503
81 | 0.0085209 | 0.0021357 | -0.0085199 | -0.0021353 | 9.9338e-07 | 4.3547e-07 | 0.012923 | 0.012923 | 0.012923 | 0.98114 | -0.36391 | 0.98102 | -0.36636 | 3.5503
82 | -0.026074 | -0.0065367 | 0.026078 | 0.006539 | 3.6617e-06 | 2.2653e-06 | 0.03964 | 0.03964 | 0.03964 | 0.9788 | -0.40606 | 0.97895 | -0.40311 | 10.8901
83 | 0.020255 | 0.0050781 | -0.020254 | -0.0050781 | 1.1876e-07 | 7.1807e-08 | 0.030793 | 0.030793 | 0.030793 | 0.9788 | -0.40606 | 0.97879 | -0.40618 | 8.4595
84 | -0.030129 | -0.0075544 | 0.030144 | 0.0075637 | 1.5013e-05 | 9.3683e-06 | 0.045798 | 0.045798 | 0.045798 | 0.97895 | -0.40311 | 0.97948 | -0.39266 | 12.582
85 | 0.015187 | 0.0038079 | -0.015183 | -0.0038056 | 4.0107e-06 | 2.3147e-06 | 0.023088 | 0.023088 | 0.023088 | 0.97879 | -0.40618 | 0.97851 | -0.41173 | 6.3429
86 | 0.081479 | 0.02061 | -0.081398 | -0.020558 | 8.1488e-05 | 5.1974e-05 | 0.12385 | 0.12385 | 0.12385 | 0.97948 | -0.39266 | 0.97841 | -0.41353 | 34.0249
87 | -0.11162 | -0.028174 | 0.11174 | 0.02825 | 0.00011931 | 7.6217e-05 | 0.16965 | 0.16965 | 0.16965 | 0.97948 | -0.39266 | 0.98063 | -0.37037 | 46.6068
88 | 0.01114 | 0.0027925 | -0.011138 | -0.0027916 | 1.8353e-06 | 9.6043e-07 | 0.016941 | 0.016941 | 0.016941 | 0.97851 | -0.41173 | 0.97834 | -0.41518 | 4.6542
89 | 0.078533 | 0.01984 | -0.078494 | -0.019815 | 3.9351e-05 | 2.5092e-05 | 0.11949 | 0.11949 | 0.11949 | 0.97841 | -0.41353 | 0.97788 | -0.42399 | 32.8279
90 | -0.11482 | -0.029022 | 0.11483 | 0.029024 | 2.8275e-06 | 1.8065e-06 | 0.17432 | 0.17432 | 0.17432 | 0.98063 | -0.37037 | 0.98065 | -0.36986 | 47.891
91 | 0.0052083 | 0.0013053 | -0.0052083 | -0.0013053 | 1.9826e-08 | 2.1096e-09 | 0.0079217 | 0.0079217 | 0.0079217 | 0.97834 | -0.41518 | 0.97833 | -0.41526 | 2.1763
92 | 0.07809 | 0.019714 | -0.078029 | -0.019674 | 6.1556e-05 | 3.925e-05 | 0.11888 | 0.11888 | 0.11888 | 0.97788 | -0.42399 | 0.97704 | -0.44046 | 32.6592
93 | -0.11803 | -0.029827 | 0.11823 | 0.029954 | 0.00019904 | 0.00012655 | 0.17919 | 0.17919 | 0.17919 | 0.98065 | -0.36986 | 0.98246 | -0.33475 | 24.6136
94 | 0.0050177 | 0.0012571 | -0.0050168 | -0.001257 | 8.6175e-07 | 5.8787e-08 | 0.0076417 | 0.0076419 | 0.0076419 | 0.97704 | -0.44046 | 0.97685 | -0.44407 | 2.0994
95 | 0.073011 | 0.018417 | -0.07297 | -0.018391 | 4.1288e-05 | 2.6313e-05 | 0.11124 | 0.11124 | 0.11124 | 0.97704 | -0.44046 | 0.97643 | -0.45228 | 30.5599
96 | -0.12016 | -0.030437 | 0.12016 | 0.030438 | 1.4775e-06 | 9.396e-07 | 0.18211 | 0.18211 | 0.18211 | 0.98246 | -0.33475 | 0.98247 | -0.33449 | 25.0152
97 | 0.017058 | 0.0042769 | -0.017056 | -0.0042758 | 1.7977e-06 | 1.0637e-06 | 0.026135 | 0.026135 | 0.026135 | 0.97125 | -0.55437 | 0.97114 | -0.55658 | 7.1799
98 | -0.017058 | -0.0042769 | 0.017062 | 0.0042794 | 4.2077e-06 | 2.4896e-06 | 0.026135 | 0.026135 | 0.026135 | 0.97125 | -0.55437 | 0.97151 | -0.5492 | 7.1799
99 | 0.013748 | 0.0034467 | -0.013745 | -0.0034452 | 2.7212e-06 | 1.5393e-06 | 0.021066 | 0.021066 | 0.021066 | 0.97114 | -0.55658 | 0.97093 | -0.56074 | 5.7873
100 | -0.019364 | -0.0048562 | 0.019364 | 0.0048565 | 5.0295e-07 | 3.0301e-07 | 0.02966 | 0.02966 | 0.02966 | 0.97151 | -0.5492 | 0.97154 | -0.54865 | 8.1483
101 | 0.0049545 | 0.0012416 | -0.0049541 | -0.0012416 | 3.9854e-07 | 2.7112e-08 | 0.0075931 | 0.0075932 | 0.0075932 | 0.97093 | -0.56074 | 0.97084 | -0.56243 | 2.086
102 | 0.0087909 | 0.0022035 | -0.0087889 | -0.0022026 | 1.982e-06 | 9.0848e-07 | 0.013473 | 0.013473 | 0.013473 | 0.97093 | -0.56074 | 0.97069 | -0.56547 | 3.7014
103 | -0.023409 | -0.0058701 | 0.023411 | 0.0058718 | 2.7147e-06 | 1.6677e-06 | 0.035854 | 0.035854 | 0.035854 | 0.97154 | -0.54865 | 0.97166 | -0.54622 | 9.85
104 | 0.0027249 | 0.00068288 | -0.0027249 | -0.00068291 | 2.8057e-08 | -3.5049e-08 | 0.0041771 | 0.0041771 | 0.0041771 | 0.97069 | -0.56547 | 0.97068 | -0.56569 | 1.1476
105 | 0.006064 | 0.0015198 | -0.0060635 | -0.0015196 | 4.9714e-07 | 1.2854e-07 | 0.0092958 | 0.0092959 | 0.0092959 | 0.97069 | -0.56547 | 0.9706 | -0.56719 | 2.5538
106 | -0.026869 | -0.0067385 | 0.026879 | 0.0067447 | 1.0032e-05 | 6.2248e-06 | 0.04115 | 0.04115 | 0.04115 | 0.97166 | -0.54622 | 0.97206 | -0.53839 | 11.3049
107 | -0.072028 | -0.018141 | 0.072064 | 0.018164 | 3.6659e-05 | 2.3361e-05 | 0.10986 | 0.10986 | 0.10986 | 0.97589 | -0.46292 | 0.97643 | -0.45228 | 30.1808
108 | 0.068431 | 0.017239 | -0.068353 | -0.01719 | 7.7246e-05 | 4.9202e-05 | 0.10437 | 0.10437 | 0.10437 | 0.97589 | -0.46292 | 0.97469 | -0.48655 | 28.6741
109 | 0.061782 | 0.015543 | -0.061744 | -0.015519 | 3.8188e-05 | 2.4298e-05 | 0.094341 | 0.094341 | 0.094341 | 0.97469 | -0.48655 | 0.97403 | -0.49949 | 25.918
110 | 0.058283 | 0.014651 | -0.058277 | -0.014648 | 5.4105e-06 | 3.4401e-06 | 0.089054 | 0.089054 | 0.089054 | 0.97403 | -0.49949 | 0.97393 | -0.50144 | 24.4653
111 | 0.0026355 | 0.00066022 | -0.0026353 | -0.00066048 | 1.784e-07 | -2.5533e-07 | 0.0040145 | 0.0040146 | 0.0040146 | 0.97685 | -0.44407 | 0.97678 | -0.44549 | 1.1029
112 | 0.054317 | 0.013655 | -0.054276 | -0.013629 | 4.1353e-05 | 2.6267e-05 | 0.083004 | 0.083004 | 0.083004 | 0.97393 | -0.50144 | 0.97312 | -0.51739 | 22.8033
113 | 0.047317 | 0.011885 | -0.047289 | -0.011867 | 2.8153e-05 | 1.784e-05 | 0.072363 | 0.072364 | 0.072364 | 0.97312 | -0.51739 | 0.97249 | -0.52987 | 19.8801
114 | 0.04333 | 0.010875 | -0.043312 | -0.010864 | 1.7593e-05 | 1.1127e-05 | 0.066305 | 0.066305 | 0.066305 | 0.97249 | -0.52987 | 0.97206 | -0.53839 | 18.2156
115 | 0.016433 | 0.0041192 | -0.016432 | -0.0041188 | 5.8327e-07 | 3.4282e-07 | 0.025155 | 0.025155 | 0.025155 | 0.97206 | -0.53839 | 0.97202 | -0.53913 | 6.9107
116 | 0.012472 | 0.0031264 | -0.01247 | -0.0031254 | 1.9221e-06 | 1.0559e-06 | 0.019093 | 0.019094 | 0.019094 | 0.97202 | -0.53913 | 0.97186 | -0.54237 | 5.2455
117 | -0.12188 | -0.030868 | 0.12205 | 0.030979 | 0.00017434 | 0.00011089 | 0.18471 | 0.18471 | 0.18471 | 0.98247 | -0.33449 | 0.98401 | -0.30475 | 25.3721
118 | -0.0034597 | -0.00086695 | 0.0034598 | 0.00086688 | 1.1613e-07 | -6.9883e-08 | 0.0052274 | 0.0052274 | 0.0052274 | 0.98482 | -0.28903 | 0.98486 | -0.28833 | 1.4361
119 | 0.0034597 | 0.00086695 | -0.0034596 | -0.00086702 | 1.3071e-07 | -7.864e-08 | 0.0052274 | 0.0052275 | 0.0052275 | 0.98482 | -0.28903 | 0.98478 | -0.28982 | 1.4361
120 | 0.12347 | 0.031371 | -0.12337 | -0.031309 | 9.7565e-05 | 6.2062e-05 | 0.1867 | 0.1867 | 0.1867 | 0.98486 | -0.28833 | 0.98401 | -0.30475 | 25.6451
121 | 0.0016078 | 0.00040291 | -0.0016078 | -0.00040294 | 5.2839e-09 | -2.6994e-08 | 0.0024293 | 0.0024293 | 0.0024293 | 0.98478 | -0.28982 | 0.98478 | -0.28989 | 0.6674
122 | 0.0026553 | 0.00066544 | -0.0026553 | -0.00066548 | 2.6236e-08 | -3.5387e-08 | 0.0040708 | 0.0040708 | 0.0040708 | 0.9706 | -0.56719 | 0.97059 | -0.5674 | 1.1184

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39161 | 0.099813

## res_load
| p_mw | q_mvar
0 | 0.0077995 | 0.0019547
1 | 0.0033921 | 0.00085014
2 | 0.003025 | 0.00075814
3 | 0.0069191 | 0.0017341
4 | 0.0019879 | 0.00049821
5 | 0.0026879 | 0.00067366
6 | 0.0041195 | 0.0010325
7 | 0.0027687 | 0.0006939
8 | 0.0020156 | 0.00050515
9 | 0.0019977 | 0.00050068
10 | 0.0023654 | 0.00059284
11 | 0.0046238 | 0.0011588
12 | 0.0017021 | 0.00042659
13 | 0.0042673 | 0.0010695
14 | 0.0042749 | 0.0010714
15 | 0.0033415 | 0.00083745
16 | 0.0017019 | 0.00042654
17 | 0.0017019 | 0.00042654
18 | 0.0040337 | 0.0010109
19 | 0.0020097 | 0.00050368
20 | 0.0035896 | 0.00089964
21 | 0.003009 | 0.00075412
22 | 0.0036832 | 0.0009231
23 | 0.0041884 | 0.0010497
24 | 0.0020883 | 0.00052338
25 | 0.0022071 | 0.00055316
26 | 0.0020712 | 0.00051909
27 | 0.0017563 | 0.00044016
28 | 0.0053824 | 0.0013489
29 | 0.029389 | 0.0073655
30 | 0.003343 | 0.00083784
31 | 0.0019156 | 0.0004801
32 | 0.0016802 | 0.0004211
33 | 0.0018678 | 0.00046811
34 | 0.0055805 | 0.0013986
35 | 0.0017148 | 0.00042978
36 | 0.0016069 | 0.00040273
37 | 0.030359 | 0.0076086
38 | 0.0018108 | 0.00045383
39 | 0.001689 | 0.00042329
40 | 0.0024234 | 0.00060736
41 | 0.0021689 | 0.00054359
42 | 0.0035427 | 0.00088789
43 | 0.0034361 | 0.00086117
44 | 0.0017432 | 0.00043688
45 | 0.0049978 | 0.0012526
46 | 0.0034159 | 0.00085611
47 | 0.0022783 | 0.000571
48 | 0.003276 | 0.00082103
49 | 0.0022035 | 0.00055226
50 | 0.0017253 | 0.00043241
51 | 0.0041935 | 0.001051
52 | 0.0017725 | 0.00044424
53 | 0.0059449 | 0.0014899
54 | 0.0014223 | 0.00035646
55 | 0.0027845 | 0.00069785
56 | 0.0045254 | 0.0011342
57 | 0.0012467 | 0.00031245
58 | 0.0065981 | 0.0016536
59 | 0.0059746 | 0.0014974
60 | 0.0088725 | 0.0022237
61 | 0.0085199 | 0.0021353
62 | 0.0058197 | 0.0014586
63 | 0.0040515 | 0.0010154
64 | 0.0050679 | 0.0012701
65 | 0.0040422 | 0.0010131
66 | 0.0028648 | 0.00071798
67 | 0.0030807 | 0.00077211
68 | 0.0059302 | 0.0014862
69 | 0.00040366 | 0.00010117
70 | 0.0032055 | 0.00080336
71 | 0.0052083 | 0.0013053
72 | 0.0019302 | 0.00048376
73 | 0.0033082 | 0.00082911
74 | 0.0023015 | 0.00057681
75 | 0.0040443 | 0.0010136
76 | 0.0049541 | 0.0012416
77 | 0.0034582 | 0.0008667
78 | 0.003597 | 0.00090151
79 | 0.00090539 | 0.00022691
80 | 0.0065713 | 0.0016469
81 | 0.0034612 | 0.00086746
82 | 0.0023813 | 0.0005968
83 | 0.0039597 | 0.0009924
84 | 0.0026353 | 0.00066048
85 | 0.0069586 | 0.001744
86 | 0.0039597 | 0.0009924
87 | 0.0039596 | 0.00099237
88 | 0.01247 | 0.0031254
89 | 0.0017158 | 0.00043001
90 | 0.0018518 | 0.00046411
91 | 0.0013144 | 0.00032943
92 | 0.0016078 | 0.00040294
93 | 0.0034082 | 0.00085418
94 | 0.0026553 | 0.00066548
95 | 0.0027249 | 0.00068291

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1