## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-30_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-30_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-30_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-30_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1054-30_0_4_node_134 | 0.4 | n |  | TRUE
5 | bus_LV_1054-30_0_4_node_91 | 0.4 | n |  | TRUE
6 | bus_LV_1054-30_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1054-30_0_4_node_90 | 0.4 | n |  | TRUE
8 | bus_LV_1054-30_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1054-30_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1054-30_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1054-30_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1054-30_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1054-30_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1054-30_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_1054-30_0_4_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1054-30_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1054-30_0_4_node_130 | 0.4 | n |  | TRUE
18 | bus_LV_1054-30_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1054-30_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1054-30_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1054-30_0_4_node_129 | 0.4 | n |  | TRUE
22 | bus_LV_1054-30_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1054-30_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1054-30_0_4_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1054-30_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1054-30_0_4_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_1054-30_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_1054-30_0_4_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_1054-30_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1054-30_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1054-30_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1054-30_0_4_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_1054-30_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1054-30_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1054-30_0_4_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_1054-30_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_1054-30_0_4_node_20 | 0.4 | n |  | TRUE
38 | bus_LV_1054-30_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1054-30_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1054-30_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1054-30_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1054-30_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1054-30_0_4_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1054-30_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1054-30_0_4_node_63 | 0.4 | n |  | TRUE
46 | bus_LV_1054-30_0_4_node_66 | 0.4 | n |  | TRUE
47 | bus_LV_1054-30_0_4_node_77 | 0.4 | n |  | TRUE
48 | bus_LV_1054-30_0_4_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_1054-30_0_4_node_86 | 0.4 | n |  | TRUE
50 | bus_LV_1054-30_0_4_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_1054-30_0_4_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_1054-30_0_4_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1054-30_0_4_node_67 | 0.4 | n |  | TRUE
54 | bus_LV_1054-30_0_4_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_1054-30_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_1054-30_0_4_node_55 | 0.4 | n |  | TRUE
57 | bus_LV_1054-30_0_4_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_1054-30_0_4_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_1054-30_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_1054-30_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_1054-30_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_1054-30_0_4_node_41 | 0.4 | n |  | TRUE
63 | bus_LV_1054-30_0_4_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_1054-30_0_4_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_1054-30_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_1054-30_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_1054-30_0_4_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_1054-30_0_4_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_1054-30_0_4_node_93 | 0.4 | n |  | TRUE
70 | bus_LV_1054-30_0_4_node_97 | 0.4 | n |  | TRUE
71 | bus_LV_1054-30_0_4_node_92 | 0.4 | n |  | TRUE
72 | bus_LV_1054-30_0_4_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_1054-30_0_4_node_48 | 0.4 | n |  | TRUE
74 | bus_LV_1054-30_0_4_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_1054-30_0_4_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_1054-30_0_4_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_1054-30_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_1054-30_0_4_node_96 | 0.4 | n |  | TRUE
79 | bus_LV_1054-30_0_4_node_88 | 0.4 | n |  | TRUE
80 | bus_LV_1054-30_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_1054-30_0_4_node_89 | 0.4 | n |  | TRUE
82 | bus_LV_1054-30_0_4_node_125 | 0.4 | n |  | TRUE
83 | bus_LV_1054-30_0_4_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_1054-30_0_4_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_1054-30_0_4_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_1054-30_0_4_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_1054-30_0_4_node_95 | 0.4 | n |  | TRUE
88 | bus_LV_1054-30_0_4_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_1054-30_0_4_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_1054-30_0_4_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_1054-30_0_4_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_1054-30_0_4_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_1054-30_0_4_node_71 | 0.4 | n |  | TRUE
94 | bus_LV_1054-30_0_4_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_1054-30_0_4_node_124 | 0.4 | n |  | TRUE
96 | bus_LV_1054-30_0_4_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_1054-30_0_4_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_1054-30_0_4_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_1054-30_0_4_node_133 | 0.4 | n |  | TRUE
100 | bus_LV_1054-30_0_4_node_132 | 0.4 | n |  | TRUE
101 | bus_LV_1054-30_0_4_node_81 | 0.4 | n |  | TRUE
102 | bus_LV_1054-30_0_4_node_82 | 0.4 | n |  | TRUE
103 | bus_LV_1054-30_0_4_node_83 | 0.4 | n |  | TRUE
104 | bus_LV_1054-30_0_4_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_1054-30_0_4_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_1054-30_0_4_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_1054-30_0_4_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_1054-30_0_4_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_1054-30_0_4_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_1054-30_0_4_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_1054-30_0_4_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_1054-30_0_4_node_119 | 0.4 | n |  | TRUE
113 | bus_LV_1054-30_0_4_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1054-30_0_4_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_1054-30_0_4_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_1054-30_0_4_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_1054-30_0_4_node_106 | 0.4 | n |  | TRUE
118 | bus_LV_1054-30_0_4_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_1054-30_0_4_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_1054-30_0_4_node_109 | 0.4 | n |  | TRUE
121 | bus_LV_1054-30_0_4_node_127 | 0.4 | n |  | TRUE
122 | bus_LV_1054-30_0_4_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_1054-30_0_4_node_123 | 0.4 | n |  | TRUE
124 | bus_LV_1054-30_0_4_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_1054-30_0_4_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_1054-30_0_4_node_113 | 0.4 | n |  | TRUE
127 | bus_LV_1054-30_0_4_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_1054-30_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_1054-30_0_4_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_1054-30_0_4_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_1054-30_0_4_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_1054-30_0_4_node_131 | 0.4 | n |  | TRUE
133 | bus_MV_212_0_node_73 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-30_0_4_load_0 | 0 | 0.02458 | 0.0061604 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-30_0_4_load_1 | 1 | 0.019159 | 0.0048017 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-30_0_4_load_134 | 4 | 0.0074087 | 0.0018568 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-30_0_4_load_90 | 7 | 0.0088468 | 0.0022172 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-30_0_4_load_4 | 9 | 0.016399 | 0.0041099 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-30_0_4_load_10 | 10 | 0.0077562 | 0.0019439 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-30_0_4_load_5 | 11 | 0.016398 | 0.0041098 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-30_0_4_load_7 | 12 | 0.010144 | 0.0025424 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-30_0_4_load_31 | 14 | 0.010133 | 0.0025396 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-30_0_4_load_11 | 16 | 0.001965 | 0.00049247 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-30_0_4_load_130 | 17 | 0.0021045 | 0.00052743 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-30_0_4_load_25 | 19 | 0.0024827 | 0.00062222 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-30_0_4_load_19 | 20 | 0.0037033 | 0.00092813 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-30_0_4_load_129 | 21 | 0.0021439 | 0.0005373 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-30_0_4_load_12 | 22 | 0.0014909 | 0.00037365 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-30_0_4_load_13 | 23 | 0.0016583 | 0.00041561 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-30_0_4_load_14 | 24 | 0.0014507 | 0.00036359 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-30_0_4_load_33 | 25 | 0.0037472 | 0.00093914 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-30_0_4_load_35 | 26 | 0.003915 | 0.0009812 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-30_0_4_load_32 | 27 | 0.0039569 | 0.00099168 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-30_0_4_load_15 | 28 | 0.00099052 | 0.00024825 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-30_0_4_load_17 | 29 | 0.0017203 | 0.00043115 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-30_0_4_load_16 | 30 | 0.0015303 | 0.00038352 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-30_0_4_load_18 | 31 | 0.0013851 | 0.00034713 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-30_0_4_load_54 | 32 | 0.0016705 | 0.00041866 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-30_0_4_load_34 | 33 | 0.0027633 | 0.00069255 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-30_0_4_load_36 | 34 | 0.0026724 | 0.00066978 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-30_0_4_load_57 | 35 | 0.0013279 | 0.00033281 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-30_0_4_load_37 | 36 | 0.0038677 | 0.00096934 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-30_0_4_load_23 | 39 | 0.0040029 | 0.0010032 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-30_0_4_load_26 | 40 | 0.0021778 | 0.00054581 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-30_0_4_load_27 | 41 | 0.0019394 | 0.00048607 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-30_0_4_load_28 | 42 | 0.0031155 | 0.00078081 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-30_0_4_load_29 | 43 | 0.0019293 | 0.00048352 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-30_0_4_load_30 | 44 | 0.0034787 | 0.00087186 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-30_0_4_load_63 | 45 | 0.0020877 | 0.00052321 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-30_0_4_load_66 | 46 | 0.0027073 | 0.00067852 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-30_0_4_load_77 | 47 | 0.0019068 | 0.00047789 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-30_0_4_load_46 | 48 | 0.0024883 | 0.00062363 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-30_0_4_load_86 | 49 | 0.0021475 | 0.00053821 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-30_0_4_load_61 | 51 | 0.0010424 | 0.00026125 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-30_0_4_load_62 | 52 | 0.0011002 | 0.00027573 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-30_0_4_load_67 | 53 | 0.0016941 | 0.00042457 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-30_0_4_load_78 | 54 | 0.001871 | 0.00046891 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-30_0_4_load_38 | 55 | 0.0025315 | 0.00063445 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-30_0_4_load_55 | 56 | 0.0014044 | 0.00035197 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-30_0_4_load_56 | 57 | 0.001407 | 0.00035263 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-30_0_4_load_69 | 58 | 0.0031603 | 0.00079204 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-30_0_4_load_39 | 60 | 0.0022688 | 0.00056861 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-30_0_4_load_40 | 61 | 0.0015929 | 0.00039921 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-30_0_4_load_41 | 62 | 0.0014064 | 0.00035248 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-30_0_4_load_53 | 64 | 0.0014028 | 0.00035157 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-30_0_4_load_58 | 66 | 0.0037538 | 0.00094079 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-30_0_4_load_59 | 67 | 0.0036572 | 0.00091657 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-30_0_4_load_42 | 68 | 0.0017453 | 0.00043741 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-30_0_4_load_93 | 69 | 0.005063 | 0.0012689 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-30_0_4_load_97 | 70 | 0.0014153 | 0.00035471 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-30_0_4_load_47 | 72 | 0.0015494 | 0.00038832 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-30_0_4_load_48 | 73 | 0.0017929 | 0.00044933 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-30_0_4_load_49 | 74 | 0.00068276 | 0.00017112 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-30_0_4_load_51 | 76 | 0.0022625 | 0.00056703 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-30_0_4_load_88 | 79 | 0.0019255 | 0.00048257 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-30_0_4_load_89 | 81 | 0.0079899 | 0.0020025 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-30_0_4_load_125 | 82 | 0.0019521 | 0.00048925 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-30_0_4_load_70 | 83 | 0.0016472 | 0.00041282 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-30_0_4_load_64 | 84 | 0.0010706 | 0.00026832 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-30_0_4_load_87 | 85 | 0.00097628 | 0.00024468 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-30_0_4_load_65 | 86 | 0.0010821 | 0.00027119 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-30_0_4_load_95 | 87 | 0.0017429 | 0.00043682 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-30_0_4_load_84 | 88 | 0.0019102 | 0.00047874 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-30_0_4_load_85 | 89 | 0.002085 | 0.00052254 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-30_0_4_load_68 | 90 | 0.0013324 | 0.00033392 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-30_0_4_load_73 | 92 | 0.0017597 | 0.00044103 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-30_0_4_load_71 | 93 | 0.0017187 | 0.00043075 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-30_0_4_load_124 | 95 | 0.003838 | 0.00096189 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-30_0_4_load_72 | 96 | 0.0026625 | 0.0006673 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-30_0_4_load_79 | 97 | 0.0017481 | 0.00043811 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-30_0_4_load_80 | 98 | 0.0019291 | 0.00048347 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-30_0_4_load_133 | 99 | 0.0021432 | 0.00053713 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-30_0_4_load_132 | 100 | 0.0021048 | 0.00052752 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-30_0_4_load_81 | 101 | 0.0021146 | 0.00052997 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-30_0_4_load_82 | 102 | 0.0019597 | 0.00049114 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-30_0_4_load_94 | 104 | 0.0022745 | 0.00057005 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-30_0_4_load_102 | 105 | 0.0020468 | 0.00051298 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-30_0_4_load_98 | 106 | 0.001384 | 0.00034687 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-30_0_4_load_103 | 107 | 0.0021614 | 0.0005417 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-30_0_4_load_99 | 108 | 0.0031796 | 0.00079689 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-30_0_4_load_100 | 109 | 0.0011683 | 0.00029281 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-30_0_4_load_101 | 110 | 0.004476 | 0.0011218 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-30_0_4_load_120 | 111 | 0.0026094 | 0.00065397 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1054-30_0_4_load_119 | 112 | 0.0021331 | 0.00053461 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1054-30_0_4_load_104 | 113 | 0.0015032 | 0.00037675 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1054-30_0_4_load_105 | 114 | 0.0021579 | 0.00054082 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1054-30_0_4_load_121 | 115 | 0.0013925 | 0.00034899 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1054-30_0_4_load_122 | 116 | 0.001628 | 0.00040801 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1054-30_0_4_load_106 | 117 | 0.0072824 | 0.0018251 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1054-30_0_4_load_107 | 118 | 0.0083958 | 0.0021042 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1054-30_0_4_load_127 | 121 | 0.0016605 | 0.00041615 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1054-30_0_4_load_110 | 122 | 0.0059836 | 0.0014996 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1054-30_0_4_load_123 | 123 | 0.0031256 | 0.00078336 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1054-30_0_4_load_111 | 124 | 0.0035842 | 0.0008983 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1054-30_0_4_load_112 | 125 | 0.001431 | 0.00035863 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1054-30_0_4_load_113 | 126 | 0.0013751 | 0.00034464 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1054-30_0_4_load_114 | 127 | 0.0013386 | 0.00033548 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1054-30_0_4_load_115 | 128 | 0.0042293 | 0.00106 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1054-30_0_4_load_116 | 129 | 0.0016305 | 0.00040863 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1054-30_0_4_load_117 | 130 | 0.0015376 | 0.00038535 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1054-30_0_4_load_118 | 131 | 0.0012413 | 0.00031109 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1054-30_0_4_load_131 | 132 | 0.0019638 | 0.00049218 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-30_0_4_line_0 |  | 0 | 1 | 0.044293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-30_0_4_line_1 |  | 0 | 2 | 0.032461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-30_0_4_line_2 |  | 2 | 3 | 0.051268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-30_0_4_line_3 |  | 3 | 4 | 0.00682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-30_0_4_line_4 |  | 3 | 5 | 0.032113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-30_0_4_line_5 |  | 3 | 6 | 0.046226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-30_0_4_line_6 |  | 5 | 7 | 0.032715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-30_0_4_line_7 |  | 6 | 10 | 0.025772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-30_0_4_line_8 |  | 6 | 8 | 0.003635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-30_0_4_line_9 |  | 7 | 77 | 0.01256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-30_0_4_line_10 |  | 8 | 9 | 0.042483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-30_0_4_line_11 |  | 9 | 11 | 0.03664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-30_0_4_line_12 |  | 11 | 12 | 0.038588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-30_0_4_line_13 |  | 13 | 14 | 0.015929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-30_0_4_line_14 |  | 13 | 15 | 0.023516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-30_0_4_line_15 |  | 15 | 18 | 0.003806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-30_0_4_line_16 |  | 15 | 19 | 0.019282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_1054-30_0_4_line_17 |  | 15 | 20 | 0.01085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1054-30_0_4_line_18 |  | 16 | 17 | 0.0077141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-30_0_4_line_19 |  | 17 | 21 | 0.0074535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-30_0_4_line_20 |  | 18 | 43 | 0.029123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-30_0_4_line_21 |  | 19 | 44 | 0.024808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1054-30_0_4_line_22 |  | 20 | 37 | 0.017014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1054-30_0_4_line_23 |  | 21 | 132 | 0.016195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-30_0_4_line_24 |  | 22 | 23 | 0.0011728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-30_0_4_line_25 |  | 22 | 24 | 0.0015753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-30_0_4_line_26 |  | 24 | 25 | 0.0028967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-30_0_4_line_27 |  | 25 | 26 | 0.025029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-30_0_4_line_28 |  | 25 | 27 | 0.025983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-30_0_4_line_29 |  | 26 | 36 | 0.023824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-30_0_4_line_30 |  | 26 | 30 | 0.0049545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-30_0_4_line_31 |  | 27 | 33 | 0.027674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-30_0_4_line_32 |  | 28 | 29 | 0.0010989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-30_0_4_line_33 |  | 29 | 32 | 0.0010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-30_0_4_line_34 |  | 30 | 31 | 0.0010962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1054-30_0_4_line_35 |  | 31 | 35 | 0.0011868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-30_0_4_line_36 |  | 32 | 33 | 0.010954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1054-30_0_4_line_37 |  | 33 | 34 | 0.023593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1054-30_0_4_line_38 |  | 34 | 56 | 0.0064141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1054-30_0_4_line_39 |  | 34 | 57 | 0.020653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1054-30_0_4_line_40 |  | 36 | 58 | 0.023271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-30_0_4_line_41 |  | 37 | 38 | 0.00398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1054-30_0_4_line_42 |  | 37 | 39 | 0.0091404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1054-30_0_4_line_43 |  | 38 | 40 | 0.028276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1054-30_0_4_line_44 |  | 38 | 41 | 0.023009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-30_0_4_line_45 |  | 39 | 42 | 0.023085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1054-30_0_4_line_46 |  | 40 | 45 | 0.0075562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1054-30_0_4_line_47 |  | 42 | 46 | 0.031058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_1054-30_0_4_line_48 |  | 43 | 47 | 0.0075886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1054-30_0_4_line_49 |  | 44 | 48 | 0.038048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1054-30_0_4_line_50 |  | 45 | 49 | 0.0075854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1054-30_0_4_line_51 |  | 46 | 53 | 0.02273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_1054-30_0_4_line_52 |  | 47 | 54 | 0.0074533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-30_0_4_line_53 |  | 48 | 55 | 0.031486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1054-30_0_4_line_54 |  | 49 | 88 | 0.029912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1054-30_0_4_line_55 |  | 50 | 51 | 0.016826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-30_0_4_line_56 |  | 50 | 52 | 0.011788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1054-30_0_4_line_57 |  | 51 | 84 | 0.007578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-30_0_4_line_58 |  | 53 | 90 | 0.024309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1054-30_0_4_line_59 |  | 54 | 97 | 0.0071984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1054-30_0_4_line_60 |  | 55 | 59 | 0.019184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1054-30_0_4_line_61 |  | 56 | 64 | 0.00020163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1054-30_0_4_line_62 |  | 57 | 65 | 0.020314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1054-30_0_4_line_63 |  | 58 | 66 | 0.011408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1054-30_0_4_line_64 |  | 58 | 67 | 0.013751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-30_0_4_line_65 |  | 59 | 65 | 0.005596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_1054-30_0_4_line_66 |  | 60 | 61 | 0.028519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_1054-30_0_4_line_67 |  | 60 | 62 | 0.033629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1054-30_0_4_line_68 |  | 61 | 68 | 0.0013212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1054-30_0_4_line_69 |  | 62 | 63 | 0.038862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1054-30_0_4_line_70 |  | 63 | 65 | 0.015881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_1054-30_0_4_line_71 |  | 67 | 82 | 0.024909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-30_0_4_line_72 |  | 68 | 69 | 0.056764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_1054-30_0_4_line_73 |  | 69 | 70 | 0.023912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1054-30_0_4_line_74 |  | 69 | 71 | 0.0114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_1054-30_0_4_line_75 |  | 70 | 106 | 0.0016298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1054-30_0_4_line_76 |  | 71 | 104 | 0.044977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-30_0_4_line_77 |  | 72 | 73 | 5.437e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-30_0_4_line_78 |  | 72 | 74 | 0.010002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-30_0_4_line_79 |  | 73 | 75 | 0.016002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-30_0_4_line_80 |  | 75 | 76 | 0.022823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1054-30_0_4_line_81 |  | 75 | 77 | 0.035733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1054-30_0_4_line_82 |  | 76 | 78 | 0.0043198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1054-30_0_4_line_83 |  | 77 | 79 | 0.016455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-30_0_4_line_84 |  | 78 | 80 | 0.016556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1054-30_0_4_line_85 |  | 79 | 81 | 0.007622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1054-30_0_4_line_86 |  | 80 | 87 | 0.01318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-30_0_4_line_87 |  | 80 | 91 | 0.004111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1054-30_0_4_line_88 |  | 82 | 83 | 0.010682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-30_0_4_line_89 |  | 83 | 93 | 0.028494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1054-30_0_4_line_90 |  | 84 | 85 | 0.0073179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-30_0_4_line_91 |  | 85 | 89 | 0.01564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1054-30_0_4_line_92 |  | 86 | 87 | 0.018573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1054-30_0_4_line_93 |  | 88 | 103 | 0.018597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1054-30_0_4_line_94 |  | 89 | 103 | 0.0023864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1054-30_0_4_line_95 |  | 90 | 91 | 0.021925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_1054-30_0_4_line_96 |  | 91 | 92 | 0.01392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1054-30_0_4_line_97 |  | 93 | 94 | 0.015302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1054-30_0_4_line_98 |  | 94 | 95 | 0.017058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1054-30_0_4_line_99 |  | 94 | 96 | 0.012054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1054-30_0_4_line_100 |  | 97 | 98 | 0.015588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1054-30_0_4_line_101 |  | 98 | 99 | 0.0075898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1054-30_0_4_line_102 |  | 99 | 100 | 0.0074539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-30_0_4_line_103 |  | 100 | 132 | 0.0071982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-30_0_4_line_104 |  | 101 | 102 | 0.0072924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1054-30_0_4_line_105 |  | 101 | 103 | 0.0056271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1054-30_0_4_line_106 |  | 104 | 105 | 0.01436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1054-30_0_4_line_107 |  | 105 | 107 | 0.0047657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1054-30_0_4_line_108 |  | 106 | 108 | 0.0087815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1054-30_0_4_line_109 |  | 107 | 113 | 0.022253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1054-30_0_4_line_110 |  | 108 | 109 | 0.021021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1054-30_0_4_line_111 |  | 109 | 110 | 0.0044381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1054-30_0_4_line_112 |  | 110 | 111 | 0.021205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1054-30_0_4_line_113 |  | 111 | 112 | 0.0078812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1054-30_0_4_line_114 |  | 112 | 131 | 0.014066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1054-30_0_4_line_115 |  | 113 | 114 | 0.020418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1054-30_0_4_line_116 |  | 114 | 115 | 0.018521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1054-30_0_4_line_117 |  | 115 | 116 | 0.001896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1054-30_0_4_line_118 |  | 116 | 123 | 0.020924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1054-30_0_4_line_119 |  | 117 | 118 | 0.047972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1054-30_0_4_line_120 |  | 117 | 119 | 0.031368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1054-30_0_4_line_121 |  | 119 | 120 | 0.017186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1054-30_0_4_line_122 |  | 120 | 122 | 0.053875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1054-30_0_4_line_123 |  | 121 | 122 | 0.05964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1054-30_0_4_line_124 |  | 121 | 123 | 0.0031885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1054-30_0_4_line_125 |  | 124 | 125 | 0.010253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1054-30_0_4_line_126 |  | 124 | 126 | 0.0087545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1054-30_0_4_line_127 |  | 125 | 127 | 0.010363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1054-30_0_4_line_128 |  | 126 | 128 | 0.014672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1054-30_0_4_line_129 |  | 127 | 129 | 0.011937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1054-30_0_4_line_130 |  | 128 | 130 | 0.0030657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1054-30_0_4_line_131 |  | 129 | 131 | 0.010783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-30_0_4_trafo_28 | 0.63 MVA 20/0.4 kV | 133 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2669969.4854 | 1216203.2684 | 2670002.6826 | 1216232.5906
1 | 2669945.1561 | 1216181.7789 | 2669969.4854 | 1216203.2684
2 | 2669945.1561 | 1216181.7789 | 2669967.8212 | 1216157.207 | 2669974.2355 | 1216150.2446 | 2669977.7316 | 1216153.1986 | 2669980.1727 | 1216150.2921
3 | 2669980.1727 | 1216150.2921 | 2669984.5622 | 1216145.0625
4 | 2669956.0103 | 1216129.0617 | 2669980.1727 | 1216150.2921
5 | 2669980.1727 | 1216150.2921 | 2670015.1082 | 1216180.677
6 | 2669956.0103 | 1216129.0617 | 2669960.8041 | 1216123.6701 | 2669967.1677 | 1216116.5069 | 2669977.74 | 1216104.6057
7 | 2670015.1082 | 1216180.677 | 2670032.8981 | 1216161.9852
8 | 2670015.1082 | 1216180.677 | 2670012.6019 | 1216183.3159
9 | 2669986.0816 | 1216095.2154 | 2669977.74 | 1216104.6057
10 | 2670012.6019 | 1216183.3159 | 2670022.5994 | 1216191.9277 | 2670026.6149 | 1216194.6098 | 2670031.1504 | 1216197.6317 | 2670039.5441 | 1216200.5655 | 2670048.2772 | 1216200.468 | 2670049.612 | 1216200.1046
11 | 2670049.612 | 1216200.1046 | 2670058.1417 | 1216197.7822 | 2670084.4356 | 1216188.7563
12 | 2670121.108 | 1216176.7504 | 2670089.8337 | 1216186.9033 | 2670084.4356 | 1216188.7563
13 | 2670169.1305 | 1216158.9183 | 2670179.9218 | 1216170.6354
14 | 2670152.1317 | 1216142.6191 | 2670169.1305 | 1216158.9183
15 | 2670152.1317 | 1216142.6191 | 2670149.3898 | 1216145.2663
16 | 2670152.1317 | 1216142.6191 | 2670154.9964 | 1216139.8621 | 2670165.9713 | 1216150.5307
17 | 2670152.1317 | 1216142.6191 | 2670144.3739 | 1216135.0336
18 | 2670064.4409 | 1216192.3865 | 2670059.6745 | 1216193.9867 | 2670057.0968 | 1216194.7427
19 | 2670071.5068 | 1216190.0141 | 2670064.4409 | 1216192.3865
20 | 2670149.3898 | 1216145.2663 | 2670154.0049 | 1216149.9124 | 2670155.3055 | 1216152.9518 | 2670155.2788 | 1216155.2196 | 2670154.4213 | 1216159.0453 | 2670152.2792 | 1216162.3444 | 2670148.522 | 1216164.1569 | 2670143.8057 | 1216165.7404
21 | 2670183.8767 | 1216167.6981 | 2670180.4906 | 1216164.6445 | 2670165.9713 | 1216150.5307
22 | 2670132.209 | 1216123.139 | 2670144.3739 | 1216135.0336
23 | 2670071.5068 | 1216190.0141 | 2670086.8597 | 1216184.8595
24 | 2670179.06 | 1216087.3414 | 2670178.224 | 1216086.5189
25 | 2670177.1011 | 1216085.4141 | 2670178.224 | 1216086.5189
26 | 2670175.1679 | 1216087.5713 | 2670177.1011 | 1216085.4141
27 | 2670157.2098 | 1216070.1367 | 2670175.1679 | 1216087.5713
28 | 2670175.1679 | 1216087.5713 | 2670193.8102 | 1216105.67
29 | 2670140.1163 | 1216053.5416 | 2670157.2098 | 1216070.1367
30 | 2670157.2098 | 1216070.1367 | 2670156.5787 | 1216065.2226
31 | 2670213.6661 | 1216124.9471 | 2670193.8102 | 1216105.67
32 | 2670206.3505 | 1216114.1918 | 2670207.1338 | 1216114.9625
33 | 2670207.8487 | 1216115.6659 | 2670207.1338 | 1216114.9625
34 | 2670155.7973 | 1216064.4538 | 2670156.5787 | 1216065.2226
35 | 2670155.7973 | 1216064.4538 | 2670154.9513 | 1216063.6214
36 | 2670213.6661 | 1216124.9471 | 2670207.8487 | 1216115.6659
37 | 2670230.594 | 1216141.3814 | 2670213.6661 | 1216124.9471
38 | 2670230.594 | 1216141.3814 | 2670228.2349 | 1216135.4169
39 | 2670230.594 | 1216141.3814 | 2670247.6496 | 1216153.0283
40 | 2670140.1163 | 1216053.5416 | 2670123.4193 | 1216037.3314
41 | 2670128.8578 | 1216125.301 | 2670132.209 | 1216123.139
42 | 2670132.209 | 1216123.139 | 2670125.5381 | 1216116.8903
43 | 2670128.8578 | 1216125.301 | 2670116.0725 | 1216133.567 | 2670103.9897 | 1216138.4998
44 | 2670128.8578 | 1216125.301 | 2670112.287 | 1216109.3384
45 | 2670125.5381 | 1216116.8903 | 2670108.6899 | 1216101.1083
46 | 2670103.9897 | 1216138.4998 | 2670096.994 | 1216141.3558
47 | 2670108.6899 | 1216101.1083 | 2670099.1411 | 1216092.1639 | 2670096.1556 | 1216088.4042 | 2670091.804 | 1216081.3708 | 2670089.6815 | 1216076.9516
48 | 2670136.6117 | 1216168.1557 | 2670143.8057 | 1216165.7404
49 | 2670216.2451 | 1216185.2746 | 2670209.3639 | 1216184.8751 | 2670202.5054 | 1216182.4705 | 2670196.3059 | 1216178.9064 | 2670183.8767 | 1216167.6981
50 | 2670096.994 | 1216141.3558 | 2670089.9713 | 1216144.2228
51 | 2670089.6815 | 1216076.9516 | 2670081.6649 | 1216060.2604 | 2670079.2307 | 1216056.8211
52 | 2670136.6117 | 1216168.1557 | 2670129.546 | 1216170.528
53 | 2670216.2451 | 1216185.2746 | 2670236.9911 | 1216186.4792 | 2670241.6649 | 1216186.1341 | 2670245.8797 | 1216184.7829 | 2670247.2642 | 1216183.9952
54 | 2670089.9713 | 1216144.2228 | 2670083.5928 | 1216146.8268 | 2670078.9658 | 1216148.3623 | 2670074.6135 | 1216147.1993 | 2670069.3675 | 1216143.9022 | 2670065.999 | 1216137.2619
55 | 2670091.2263 | 1216087.8792 | 2670089.2241 | 1216090.2572 | 2670088.298 | 1216089.5903 | 2670085.8845 | 1216092.0746 | 2670082.3748 | 1216092.2224 | 2670078.6642 | 1216096.4164
56 | 2670091.2263 | 1216087.8792 | 2670090.0521 | 1216086.3533 | 2670085.7673 | 1216078.7982 | 2670085.3082 | 1216077.7149
57 | 2670078.6642 | 1216096.4164 | 2670073.6429 | 1216102.0921
58 | 2670060.4579 | 1216041.7722 | 2670062.5606 | 1216042.8138 | 2670071.5351 | 1216048.6785 | 2670077.5942 | 1216054.509 | 2670079.2307 | 1216056.8211
59 | 2670129.546 | 1216170.528 | 2670122.7219 | 1216172.8191
60 | 2670247.2642 | 1216183.9952 | 2670262.8247 | 1216172.7749
61 | 2670228.2349 | 1216135.4169 | 2670228.0856 | 1216135.2814
62 | 2670262.1613 | 1216167.2191 | 2670255.8701 | 1216160.4852 | 2670247.6496 | 1216153.0283
63 | 2670123.4193 | 1216037.3314 | 2670133.5545 | 1216042.5678
64 | 2670123.4193 | 1216037.3314 | 2670116.355 | 1216025.5335
65 | 2670262.1613 | 1216167.2191 | 2670262.8247 | 1216172.7749
66 | 2670258.6271 | 1216074.1262 | 2670264.0412 | 1216089.5699 | 2670266.6705 | 1216101.4362
67 | 2670274.7834 | 1216134.011 | 2670271.5444 | 1216117.1535 | 2670267.062 | 1216103.203 | 2670266.6705 | 1216101.4362
68 | 2670258.19 | 1216072.8794 | 2670258.6271 | 1216074.1262
69 | 2670276.3418 | 1216172.6453 | 2670277.3314 | 1216164.0626 | 2670276.3447 | 1216142.1371 | 2670274.7834 | 1216134.011
70 | 2670276.3418 | 1216172.6453 | 2670272.795 | 1216169.5015 | 2670268.7733 | 1216167.3416 | 2670262.1613 | 1216167.2191
71 | 2670116.355 | 1216025.5335 | 2670098.6565 | 1216008.0051
72 | 2670220.8151 | 1216030.1563 | 2670258.19 | 1216072.8794
73 | 2670220.8151 | 1216030.1563 | 2670214.3359 | 1216028.4122 | 2670206.8157 | 1216024.1432 | 2670200.243 | 1216018.6683
74 | 2670225.5527 | 1216021.1842 | 2670225.5876 | 1216025.3095 | 2670224.5285 | 1216028.1988 | 2670220.8151 | 1216030.1563 | 2670220.8151 | 1216030.1563
75 | 2670198.9907 | 1216017.6252 | 2670200.243 | 1216018.6683
76 | 2670225.5527 | 1216021.1842 | 2670223.8461 | 1216015.227 | 2670217.8505 | 1215995.6329 | 2670211.777 | 1215982.0083 | 2670209.7914 | 1215979.2825
77 | 2670021.9468 | 1216079.008 | 2670021.9058 | 1216078.9723
78 | 2670029.4909 | 1216085.5746 | 2670021.9468 | 1216079.008
79 | 2670009.8358 | 1216068.4663 | 2670021.9058 | 1216078.9723
80 | 2670009.8358 | 1216068.4663 | 2670024.9957 | 1216051.4054
81 | 2669986.0816 | 1216095.2154 | 2670009.8358 | 1216068.4663
82 | 2670027.865 | 1216048.1762 | 2670024.9957 | 1216051.4054
83 | 2669986.0816 | 1216095.2154 | 2669998.6395 | 1216105.8489
84 | 2670038.2299 | 1216035.2453 | 2670027.865 | 1216048.1762
85 | 2670004.4564 | 1216110.7743 | 2669998.6395 | 1216105.8489
86 | 2670038.2299 | 1216035.2453 | 2670048.2354 | 1216040.6107 | 2670049.9091 | 1216041.3412
87 | 2670038.2299 | 1216035.2453 | 2670040.8113 | 1216032.0403
88 | 2670103.1803 | 1216017.6825 | 2670098.6565 | 1216008.0051
89 | 2670082.7364 | 1215997.8347 | 2670103.1803 | 1216017.6825
90 | 2670073.6429 | 1216102.0921 | 2670068.7939 | 1216107.5728
91 | 2670068.7939 | 1216107.5728 | 2670058.4304 | 1216119.2867
92 | 2670049.9091 | 1216041.3412 | 2670058.9173 | 1216045.2725 | 2670065.2261 | 1216049.2492 | 2670066.1962 | 1216050.0949
93 | 2670056.8492 | 1216121.074 | 2670064.9816 | 1216135.2563 | 2670065.999 | 1216137.2619
94 | 2670056.8492 | 1216121.074 | 2670058.4304 | 1216119.2867
95 | 2670040.8113 | 1216032.0403 | 2670060.4579 | 1216041.7722
96 | 2670040.8113 | 1216032.0403 | 2670044.5697 | 1216030.7614 | 2670045.2613 | 1216030.0691 | 2670049.6019 | 1216025.7729 | 2670051.6372 | 1216023.7582
97 | 2670071.7572 | 1215987.1755 | 2670082.7364 | 1215997.8347
98 | 2670071.7572 | 1215987.1755 | 2670062.9027 | 1215972.595
99 | 2670071.7572 | 1215987.1755 | 2670070.7425 | 1215988.2309 | 2670063.41 | 1215995.8724
100 | 2670107.9449 | 1216177.7803 | 2670122.7219 | 1216172.8191
101 | 2670107.9449 | 1216177.7803 | 2670100.7499 | 1216180.196
102 | 2670100.7499 | 1216180.196 | 2670093.6836 | 1216182.5685
103 | 2670093.6836 | 1216182.5685 | 2670086.8597 | 1216184.8595
104 | 2670052.9569 | 1216125.1378 | 2670047.9127 | 1216130.4041
105 | 2670056.8492 | 1216121.074 | 2670052.9569 | 1216125.1378
106 | 2670209.7914 | 1215979.2825 | 2670203.9833 | 1215971.3097 | 2670200.7201 | 1215968.2171
107 | 2670200.7201 | 1215968.2171 | 2670197.2611 | 1215964.9389
108 | 2670198.9907 | 1216017.6252 | 2670196.9051 | 1216015.888 | 2670192.4511 | 1216011.7683
109 | 2670197.2611 | 1215964.9389 | 2670185.2622 | 1215953.567 | 2670181.4847 | 1215949.2698
110 | 2670192.4511 | 1216011.7683 | 2670184.1207 | 1216004.0633 | 2670177.018 | 1215997.4952
111 | 2670177.018 | 1215997.4952 | 2670173.7595 | 1215994.4821
112 | 2670158.1908 | 1215980.0854 | 2670173.7595 | 1215994.4821
113 | 2670158.1908 | 1215980.0854 | 2670152.4045 | 1215974.7346
114 | 2670142.077 | 1215965.1846 | 2670152.4045 | 1215974.7346
115 | 2670172.3006 | 1215931.2523 | 2670173.8286 | 1215935.3542 | 2670178.3687 | 1215945.7253 | 2670181.4847 | 1215949.2698
116 | 2670172.3006 | 1215931.2523 | 2670165.8355 | 1215913.8966
117 | 2670165.1737 | 1215912.1198 | 2670165.8355 | 1215913.8966
118 | 2670165.1737 | 1215912.1198 | 2670164.6646 | 1215910.753 | 2670158.0294 | 1215892.4528
119 | 2670265.8115 | 1215849.5292 | 2670254.7865 | 1215838.2794 | 2670232.9747 | 1215821.1783 | 2670229.5244 | 1215818.2838
120 | 2670281.3668 | 1215875.9943 | 2670280.288 | 1215868.9549 | 2670274.7388 | 1215861.7405 | 2670266.9342 | 1215850.6748 | 2670265.8115 | 1215849.5292
121 | 2670264.9602 | 1215880.9152 | 2670272.6833 | 1215879.572 | 2670281.3668 | 1215875.9943
122 | 2670264.9602 | 1215880.9152 | 2670242.4078 | 1215875.7573 | 2670220.0416 | 1215870.913 | 2670212.6681 | 1215868.2047
123 | 2670156.9425 | 1215889.4553 | 2670212.6681 | 1215868.2047
124 | 2670156.9425 | 1215889.4553 | 2670158.0294 | 1215892.4528
125 | 2670110.2077 | 1215935.818 | 2670117.7537 | 1215942.7594
126 | 2670110.2077 | 1215935.818 | 2670103.7646 | 1215929.8912
127 | 2670125.3809 | 1215949.7755 | 2670117.7537 | 1215942.7594
128 | 2670092.9662 | 1215919.958 | 2670103.7646 | 1215929.8912
129 | 2670125.3809 | 1215949.7755 | 2670131.6079 | 1215955.5036 | 2670134.1604 | 1215957.8638
130 | 2670090.7099 | 1215917.8826 | 2670092.9662 | 1215919.958
131 | 2670142.077 | 1215965.1846 | 2670134.1604 | 1215957.8638

## bus_geodata
| x | y | coords
0 | 2669969.4854 | 1216203.2684
1 | 2670002.6826 | 1216232.5906
2 | 2669945.1561 | 1216181.7789
3 | 2669980.1727 | 1216150.2921
4 | 2669984.5622 | 1216145.0625
5 | 2669956.0103 | 1216129.0617
6 | 2670015.1082 | 1216180.677
7 | 2669977.74 | 1216104.6057
8 | 2670012.6019 | 1216183.3159
9 | 2670049.612 | 1216200.1046
10 | 2670032.8981 | 1216161.9852
11 | 2670084.4356 | 1216188.7563
12 | 2670121.108 | 1216176.7504
13 | 2670169.1305 | 1216158.9183
14 | 2670179.9218 | 1216170.6354
15 | 2670152.1317 | 1216142.6191
16 | 2670057.0968 | 1216194.7427
17 | 2670064.4409 | 1216192.3865
18 | 2670149.3898 | 1216145.2663
19 | 2670165.9713 | 1216150.5307
20 | 2670144.3739 | 1216135.0336
21 | 2670071.5068 | 1216190.0141
22 | 2670178.224 | 1216086.5189
23 | 2670179.06 | 1216087.3414
24 | 2670177.1011 | 1216085.4141
25 | 2670175.1679 | 1216087.5713
26 | 2670157.2098 | 1216070.1367
27 | 2670193.8102 | 1216105.67
28 | 2670206.3505 | 1216114.1918
29 | 2670207.1338 | 1216114.9625
30 | 2670156.5787 | 1216065.2226
31 | 2670155.7973 | 1216064.4538
32 | 2670207.8487 | 1216115.6659
33 | 2670213.6661 | 1216124.9471
34 | 2670230.594 | 1216141.3814
35 | 2670154.9513 | 1216063.6214
36 | 2670140.1163 | 1216053.5416
37 | 2670132.209 | 1216123.139
38 | 2670128.8578 | 1216125.301
39 | 2670125.5381 | 1216116.8903
40 | 2670103.9897 | 1216138.4998
41 | 2670112.287 | 1216109.3384
42 | 2670108.6899 | 1216101.1083
43 | 2670143.8057 | 1216165.7404
44 | 2670183.8767 | 1216167.6981
45 | 2670096.994 | 1216141.3558
46 | 2670089.6815 | 1216076.9516
47 | 2670136.6117 | 1216168.1557
48 | 2670216.2451 | 1216185.2746
49 | 2670089.9713 | 1216144.2228
50 | 2670091.2263 | 1216087.8792
51 | 2670078.6642 | 1216096.4164
52 | 2670085.3082 | 1216077.7149
53 | 2670079.2307 | 1216056.8211
54 | 2670129.546 | 1216170.528
55 | 2670247.2642 | 1216183.9952
56 | 2670228.2349 | 1216135.4169
57 | 2670247.6496 | 1216153.0283
58 | 2670123.4193 | 1216037.3314
59 | 2670262.8247 | 1216172.7749
60 | 2670266.6705 | 1216101.4362
61 | 2670258.6271 | 1216074.1262
62 | 2670274.7834 | 1216134.011
63 | 2670276.3418 | 1216172.6453
64 | 2670228.0856 | 1216135.2814
65 | 2670262.1613 | 1216167.2191
66 | 2670133.5545 | 1216042.5678
67 | 2670116.355 | 1216025.5335
68 | 2670258.19 | 1216072.8794
69 | 2670220.8151 | 1216030.1563
70 | 2670200.243 | 1216018.6683
71 | 2670225.5527 | 1216021.1842
72 | 2670021.9468 | 1216079.008
73 | 2670021.9058 | 1216078.9723
74 | 2670029.4909 | 1216085.5746
75 | 2670009.8358 | 1216068.4663
76 | 2670024.9957 | 1216051.4054
77 | 2669986.0816 | 1216095.2154
78 | 2670027.865 | 1216048.1762
79 | 2669998.6395 | 1216105.8489
80 | 2670038.2299 | 1216035.2453
81 | 2670004.4564 | 1216110.7743
82 | 2670098.6565 | 1216008.0051
83 | 2670103.1803 | 1216017.6825
84 | 2670073.6429 | 1216102.0921
85 | 2670068.7939 | 1216107.5728
86 | 2670066.1962 | 1216050.0949
87 | 2670049.9091 | 1216041.3412
88 | 2670065.999 | 1216137.2619
89 | 2670058.4304 | 1216119.2867
90 | 2670060.4579 | 1216041.7722
91 | 2670040.8113 | 1216032.0403
92 | 2670051.6372 | 1216023.7582
93 | 2670082.7364 | 1215997.8347
94 | 2670071.7572 | 1215987.1755
95 | 2670062.9027 | 1215972.595
96 | 2670063.41 | 1215995.8724
97 | 2670122.7219 | 1216172.8191
98 | 2670107.9449 | 1216177.7803
99 | 2670100.7499 | 1216180.196
100 | 2670093.6836 | 1216182.5685
101 | 2670052.9569 | 1216125.1378
102 | 2670047.9127 | 1216130.4041
103 | 2670056.8492 | 1216121.074
104 | 2670209.7914 | 1215979.2825
105 | 2670200.7201 | 1215968.2171
106 | 2670198.9907 | 1216017.6252
107 | 2670197.2611 | 1215964.9389
108 | 2670192.4511 | 1216011.7683
109 | 2670177.018 | 1215997.4952
110 | 2670173.7595 | 1215994.4821
111 | 2670158.1908 | 1215980.0854
112 | 2670152.4045 | 1215974.7346
113 | 2670181.4847 | 1215949.2698
114 | 2670172.3006 | 1215931.2523
115 | 2670165.8355 | 1215913.8966
116 | 2670165.1737 | 1215912.1198
117 | 2670265.8115 | 1215849.5292
118 | 2670229.5244 | 1215818.2838
119 | 2670281.3668 | 1215875.9943
120 | 2670264.9602 | 1215880.9152
121 | 2670156.9425 | 1215889.4553
122 | 2670212.6681 | 1215868.2047
123 | 2670158.0294 | 1215892.4528
124 | 2670110.2077 | 1215935.818
125 | 2670117.7537 | 1215942.7594
126 | 2670103.7646 | 1215929.8912
127 | 2670125.3809 | 1215949.7755
128 | 2670092.9662 | 1215919.958
129 | 2670134.1604 | 1215957.8638
130 | 2670090.7099 | 1215917.8826
131 | 2670142.077 | 1215965.1846
132 | 2670086.8597 | 1216184.8595
133 | 2670132.209 | 1216123.139

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97326 | -0.51414 | 0.02458 | 0.0061604
1 | 0.97247 | -0.52977 | 0.019159 | 0.0048017
2 | 0.97458 | -0.48805 | 0 | 0
3 | 0.97667 | -0.44699 | 0 | 0
4 | 0.97662 | -0.44791 | 0.0074087 | 0.0018568
5 | 0.97972 | -0.38741 | 0 | 0
6 | 0.97448 | -0.48991 | 0 | 0
7 | 0.98283 | -0.32709 | 0.0088468 | 0.0022172
8 | 0.97434 | -0.49278 | 0 | 0
9 | 0.97264 | -0.52633 | 0.016399 | 0.0041099
10 | 0.9743 | -0.49358 | 0.0077562 | 0.0019439
11 | 0.97173 | -0.54426 | 0.016398 | 0.0041098
12 | 0.97136 | -0.55149 | 0.010144 | 0.0025424
13 | 0.99412 | -0.11152 | 0 | 0
14 | 0.99397 | -0.11437 | 0.010133 | 0.0025396
15 | 0.99434 | -0.10732 | 0 | 0
16 | 0.99277 | -0.13767 | 0.001965 | 0.00049247
17 | 0.99278 | -0.1374 | 0.0021045 | 0.00052743
18 | 0.99426 | -0.10879 | 0 | 0
19 | 0.99294 | -0.13391 | 0.0024827 | 0.00062222
20 | 0.99528 | -0.089345 | 0.0037033 | 0.00092813
21 | 0.99281 | -0.13687 | 0.0021439 | 0.0005373
22 | 0.97897 | -0.40366 | 0.0014909 | 0.00037365
23 | 0.97897 | -0.40369 | 0.0016583 | 0.00041561
24 | 0.97898 | -0.40357 | 0.0014507 | 0.00036359
25 | 0.97899 | -0.40332 | 0.0037472 | 0.00093914
26 | 0.97819 | -0.419 | 0.003915 | 0.0009812
27 | 0.98002 | -0.38313 | 0.0039569 | 0.00099168
28 | 0.98117 | -0.36063 | 0.00099052 | 0.00024825
29 | 0.98117 | -0.36061 | 0.0017203 | 0.00043115
30 | 0.97817 | -0.41939 | 0.0015303 | 0.00038352
31 | 0.97817 | -0.41944 | 0.0013851 | 0.00034713
32 | 0.98117 | -0.36056 | 0.0016705 | 0.00041866
33 | 0.98122 | -0.3597 | 0.0027633 | 0.00069255
34 | 0.9824 | -0.33671 | 0.0026724 | 0.00066978
35 | 0.97817 | -0.41947 | 0.0013279 | 0.00033281
36 | 0.97761 | -0.43041 | 0.0038677 | 0.00096934
37 | 0.99679 | -0.060671 | 0 | 0
38 | 0.99672 | -0.062111 | 0 | 0
39 | 0.99769 | -0.043653 | 0.0040029 | 0.0010032
40 | 0.99624 | -0.07138 | 0.0021778 | 0.00054581
41 | 0.99668 | -0.062894 | 0.0019394 | 0.00048607
42 | 1 | 0 | -0.36188 | -0.092818
43 | 0.99368 | -0.11999 | 0.0019293 | 0.00048352
44 | 0.99116 | -0.16767 | 0.0034787 | 0.00087186
45 | 0.99612 | -0.07357 | 0.0020877 | 0.00052321
46 | 0.99802 | -0.037218 | 0.0027073 | 0.00067852
47 | 0.99354 | -0.12266 | 0.0019068 | 0.00047789
48 | 0.98851 | -0.21852 | 0.0024883 | 0.00062363
49 | 0.99602 | -0.07549 | 0.0021475 | 0.00053821
50 | 0.99539 | -0.087763 | 0 | 0
51 | 0.99541 | -0.087438 | 0.0010424 | 0.00026125
52 | 0.99538 | -0.087992 | 0.0011002 | 0.00027573
53 | 0.99659 | -0.064011 | 0.0016941 | 0.00042457
54 | 0.99342 | -0.12502 | 0.001871 | 0.00046891
55 | 0.98635 | -0.2601 | 0.0025315 | 0.00063445
56 | 0.98238 | -0.33704 | 0.0014044 | 0.00035197
57 | 0.98353 | -0.3146 | 0.001407 | 0.00035263
58 | 0.97712 | -0.43992 | 0.0031603 | 0.00079204
59 | 0.98505 | -0.28509 | 0 | 0
60 | 0.98123 | -0.35927 | 0.0022688 | 0.00056861
61 | 0.98015 | -0.38014 | 0.0015929 | 0.00039921
62 | 0.98253 | -0.33403 | 0.0014064 | 0.00035248
63 | 0.98405 | -0.30445 | 0 | 0
64 | 0.98238 | -0.33704 | 0.0014028 | 0.00035157
65 | 0.98468 | -0.29239 | 0 | 0
66 | 0.97709 | -0.4407 | 0.0037538 | 0.00094079
67 | 0.97693 | -0.4438 | 0.0036572 | 0.00091657
68 | 0.98011 | -0.38109 | 0.0017453 | 0.00043741
69 | 0.97806 | -0.42105 | 0.005063 | 0.0012689
70 | 0.97733 | -0.43532 | 0.0014153 | 0.00035471
71 | 0.97785 | -0.42517 | 0 | 0
72 | 0.98808 | -0.22593 | 0.0015494 | 0.00038832
73 | 0.98808 | -0.22593 | 0.0017929 | 0.00044933
74 | 0.98807 | -0.22606 | 0.00068276 | 0.00017112
75 | 0.98814 | -0.22478 | 0 | 0
76 | 0.99079 | -0.17414 | 0.0022625 | 0.00056703
77 | 0.98412 | -0.30203 | 0 | 0
78 | 0.9913 | -0.16441 | 0 | 0
79 | 0.98397 | -0.30497 | 0.0019255 | 0.00048257
80 | 0.99325 | -0.12721 | 0 | 0
81 | 0.98392 | -0.30607 | 0.0079899 | 0.0020025
82 | 0.97665 | -0.44918 | 0.0019521 | 0.00048925
83 | 0.97656 | -0.45111 | 0.0016472 | 0.00041282
84 | 0.99542 | -0.087152 | 0.0010706 | 0.00026832
85 | 0.99544 | -0.086738 | 0.00097628 | 0.00024468
86 | 0.9932 | -0.12823 | 0.0010821 | 0.00027119
87 | 0.99322 | -0.12787 | 0.0017429 | 0.00043682
88 | 0.99569 | -0.081937 | 0.0019102 | 0.00047874
89 | 0.9955 | -0.085585 | 0.002085 | 0.00052254
90 | 0.99509 | -0.092386 | 0.0013324 | 0.00033392
91 | 0.99375 | -0.11779 | 0 | 0
92 | 0.99373 | -0.11823 | 0.0017597 | 0.00044103
93 | 0.97634 | -0.45539 | 0.0017187 | 0.00043075
94 | 0.97625 | -0.45721 | 0 | 0
95 | 0.97619 | -0.45841 | 0.003838 | 0.00096189
96 | 0.97622 | -0.4578 | 0.0026625 | 0.0006673
97 | 0.99331 | -0.12707 | 0.0017481 | 0.00043811
98 | 0.99311 | -0.13102 | 0.0019291 | 0.00048347
99 | 0.99302 | -0.13269 | 0.0021432 | 0.00053713
100 | 0.99295 | -0.13404 | 0.0021048 | 0.00052752
101 | 0.99549 | -0.085725 | 0.0021146 | 0.00052997
102 | 0.99548 | -0.085976 | 0.0019597 | 0.00049114
103 | 0.99551 | -0.085322 | 0 | 0
104 | 0.97619 | -0.45771 | 0.0022745 | 0.00057005
105 | 0.97569 | -0.46752 | 0.0020468 | 0.00051298
106 | 0.97729 | -0.43625 | 0.001384 | 0.00034687
107 | 0.97553 | -0.4706 | 0.0021614 | 0.0005417
108 | 0.97704 | -0.44105 | 0.0031796 | 0.00079689
109 | 0.97652 | -0.45133 | 0.0011683 | 0.00029281
110 | 0.97641 | -0.45341 | 0.004476 | 0.0011218
111 | 0.976 | -0.46159 | 0.0026094 | 0.00065397
112 | 0.97586 | -0.46426 | 0.0021331 | 0.00053461
113 | 0.97484 | -0.48412 | 0.0015032 | 0.00037675
114 | 0.97424 | -0.49597 | 0.0021579 | 0.00054082
115 | 0.97373 | -0.506 | 0.0013925 | 0.00034899
116 | 0.97368 | -0.50698 | 0.001628 | 0.00040801
117 | 0.97039 | -0.57203 | 0.0072824 | 0.0018251
118 | 0.97001 | -0.57949 | 0.0083958 | 0.0021042
119 | 0.97085 | -0.56293 | 0 | 0
120 | 0.9711 | -0.55795 | 0 | 0
121 | 0.97309 | -0.51853 | 0.0016605 | 0.00041615
122 | 0.97189 | -0.54235 | 0.0059836 | 0.0014996
123 | 0.97316 | -0.51716 | 0.0031256 | 0.00078336
124 | 0.97513 | -0.47874 | 0.0035842 | 0.0008983
125 | 0.97523 | -0.47673 | 0.001431 | 0.00035863
126 | 0.97507 | -0.47989 | 0.0013751 | 0.00034464
127 | 0.97535 | -0.47442 | 0.0013386 | 0.00033548
128 | 0.97499 | -0.48144 | 0.0042293 | 0.00106
129 | 0.9755 | -0.47146 | 0.0016305 | 0.00040863
130 | 0.97499 | -0.48153 | 0.0015376 | 0.00038535
131 | 0.97565 | -0.46848 | 0.0012413 | 0.00031109
132 | 0.9929 | -0.13509 | 0.0019638 | 0.00049218
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.019173 | 0.0048103 | -0.019159 | -0.0048017 | 1.4275e-05 | 8.5861e-06 | 0.029316 | 0.029316 | 0.029316 | 0.97326 | -0.51414 | 0.97247 | -0.52977 | 8.0539
1 | -0.043754 | -0.010971 | 0.043808 | 0.011005 | 5.4476e-05 | 3.4461e-05 | 0.066897 | 0.066897 | 0.066897 | 0.97326 | -0.51414 | 0.97458 | -0.48805 | 18.3783
2 | -0.043808 | -0.011005 | 0.043894 | 0.01106 | 8.6038e-05 | 5.4424e-05 | 0.066897 | 0.066897 | 0.066897 | 0.97458 | -0.48805 | 0.97667 | -0.44699 | 18.3783
3 | 0.007409 | 0.0018569 | -0.0074087 | -0.0018568 | 3.2588e-07 | 1.2322e-07 | 0.011288 | 0.011288 | 0.011288 | 0.97667 | -0.44699 | 0.97662 | -0.44791 | 3.1011
4 | -0.10221 | -0.025752 | 0.1025 | 0.025939 | 0.00029219 | 0.0001866 | 0.15577 | 0.15577 | 0.15577 | 0.97667 | -0.44699 | 0.97972 | -0.38741 | 42.7934
5 | 0.050904 | 0.012836 | -0.0508 | -0.01277 | 0.00010434 | 6.6201e-05 | 0.077583 | 0.077583 | 0.077583 | 0.97667 | -0.44699 | 0.97448 | -0.48991 | 21.3141
6 | -0.1025 | -0.025939 | 0.1028 | 0.026129 | 0.00029767 | 0.0001901 | 0.15577 | 0.15577 | 0.15577 | 0.97972 | -0.38741 | 0.98283 | -0.32709 | 42.7933
7 | 0.0077575 | 0.0019444 | -0.0077562 | -0.0019439 | 1.3561e-06 | 5.4691e-07 | 0.011846 | 0.011846 | 0.011846 | 0.97448 | -0.48991 | 0.9743 | -0.49358 | 3.2543
8 | 0.043042 | 0.010825 | -0.043036 | -0.010821 | 5.8907e-06 | 3.7248e-06 | 0.065738 | 0.065738 | 0.065738 | 0.97448 | -0.48991 | 0.97434 | -0.49278 | 18.0598
9 | -0.11164 | -0.028346 | 0.11178 | 0.028432 | 0.00013478 | 8.6101e-05 | 0.16916 | 0.16916 | 0.16916 | 0.98283 | -0.32709 | 0.98412 | -0.30203 | 46.473
10 | 0.043036 | 0.010821 | -0.042967 | -0.010778 | 6.8846e-05 | 4.3533e-05 | 0.065738 | 0.065738 | 0.065738 | 0.97434 | -0.49278 | 0.97264 | -0.52633 | 18.0599
11 | 0.026569 | 0.006668 | -0.026546 | -0.0066539 | 2.2705e-05 | 1.4077e-05 | 0.04065 | 0.04065 | 0.04065 | 0.97264 | -0.52633 | 0.97173 | -0.54426 | 11.1677
12 | 0.010148 | 0.0025441 | -0.010144 | -0.0025424 | 3.4943e-06 | 1.7585e-06 | 0.015539 | 0.01554 | 0.01554 | 0.97173 | -0.54426 | 0.97136 | -0.55149 | 4.2691
13 | 0.010135 | 0.0025403 | -0.010133 | -0.0025396 | 1.3747e-06 | 6.7328e-07 | 0.01517 | 0.01517 | 0.01517 | 0.99412 | -0.11152 | 0.99397 | -0.11437 | 4.1676
14 | -0.010135 | -0.0025403 | 0.010137 | 0.0025413 | 2.0293e-06 | 9.9381e-07 | 0.01517 | 0.01517 | 0.01517 | 0.99412 | -0.11152 | 0.99434 | -0.10732 | 4.1675
15 | 0.021834 | 0.0054801 | -0.021833 | -0.0054792 | 1.524e-06 | 9.2601e-07 | 0.032677 | 0.032677 | 0.032677 | 0.99434 | -0.10732 | 0.99426 | -0.10879 | 8.9773
16 | 0.15864 | 0.040707 | -0.15843 | -0.040577 | 0.00020434 | 0.00013028 | 0.23774 | 0.23774 | 0.23774 | 0.99434 | -0.10732 | 0.99294 | -0.13391 | 32.6567
17 | -0.19061 | -0.048728 | 0.19078 | 0.048834 | 0.00016592 | 0.00010591 | 0.28559 | 0.28559 | 0.28559 | 0.99434 | -0.10732 | 0.99528 | -0.089345 | 39.229
18 | -0.001965 | -0.00049247 | 0.001965 | 0.00049239 | 2.5093e-08 | -8.3686e-08 | 0.0029452 | 0.0029452 | 0.0029452 | 0.99277 | -0.13767 | 0.99278 | -0.1374 | 0.80913
19 | -0.0040695 | -0.0010198 | 0.0040696 | 0.0010198 | 1.0398e-07 | -2.9831e-08 | 0.0060994 | 0.0060994 | 0.0060994 | 0.99278 | -0.1374 | 0.99281 | -0.13687 | 1.6757
20 | 0.021833 | 0.0054792 | -0.021821 | -0.0054721 | 1.1662e-05 | 7.0861e-06 | 0.032677 | 0.032677 | 0.032677 | 0.99426 | -0.10879 | 0.99368 | -0.11999 | 8.9773
21 | 0.15595 | 0.039954 | -0.1557 | -0.039792 | 0.00025475 | 0.0001624 | 0.23402 | 0.23402 | 0.23402 | 0.99294 | -0.13391 | 0.99116 | -0.16767 | 32.1457
22 | -0.19448 | -0.049762 | 0.19475 | 0.049935 | 0.00027037 | 0.00017259 | 0.29112 | 0.29112 | 0.29112 | 0.99528 | -0.089345 | 0.99679 | -0.060671 | 39.9895
23 | -0.0062134 | -0.0015571 | 0.0062139 | 0.0015572 | 5.2669e-07 | 1.2764e-07 | 0.0093126 | 0.0093125 | 0.0093126 | 0.99281 | -0.13687 | 0.9929 | -0.13509 | 2.5584
24 | 0.0016583 | 0.0004156 | -0.0016583 | -0.00041561 | 2.7943e-09 | -1.2958e-08 | 0.0025206 | 0.0025206 | 0.0025206 | 0.97897 | -0.40366 | 0.97897 | -0.40369 | 0.69247
25 | -0.0031492 | -0.00078925 | 0.0031492 | 0.00078924 | 1.3535e-08 | -1.1144e-08 | 0.0047867 | 0.0047867 | 0.0047867 | 0.97897 | -0.40366 | 0.97898 | -0.40357 | 1.315
26 | -0.0046 | -0.0011528 | 0.0046 | 0.0011528 | 5.3102e-08 | -2.4367e-09 | 0.0069918 | 0.0069918 | 0.0069918 | 0.97898 | -0.40357 | 0.97899 | -0.40332 | 1.9208
27 | 0.034476 | 0.008661 | -0.03445 | -0.0086448 | 2.578e-05 | 1.6185e-05 | 0.052409 | 0.052409 | 0.052409 | 0.97899 | -0.40332 | 0.97819 | -0.419 | 14.398
28 | -0.042823 | -0.010753 | 0.042864 | 0.010779 | 4.1288e-05 | 2.6097e-05 | 0.065096 | 0.065096 | 0.065096 | 0.97899 | -0.40332 | 0.98002 | -0.38313 | 17.8835
29 | 0.026291 | 0.0066002 | -0.026277 | -0.0065913 | 1.4293e-05 | 8.8488e-06 | 0.039998 | 0.039998 | 0.039998 | 0.97819 | -0.419 | 0.97761 | -0.43041 | 10.9886
30 | 0.0042433 | 0.0010634 | -0.0042433 | -0.0010634 | 7.7414e-08 | -1.2649e-08 | 0.0064549 | 0.0064549 | 0.0064549 | 0.97819 | -0.419 | 0.97817 | -0.41939 | 1.7733
31 | -0.046821 | -0.011771 | 0.046873 | 0.011804 | 5.2468e-05 | 3.323e-05 | 0.071104 | 0.071104 | 0.071104 | 0.98002 | -0.38313 | 0.98122 | -0.3597 | 19.534
32 | -0.00099052 | -0.00024825 | 0.00099052 | 0.00024823 | 9.2997e-10 | -1.3283e-08 | 0.0015022 | 0.0015022 | 0.0015022 | 0.98117 | -0.36063 | 0.98117 | -0.36061 | 0.41269
33 | -0.0027108 | -0.00067939 | 0.0027108 | 0.00067938 | 6.3566e-09 | -8.5986e-09 | 0.0041112 | 0.0041112 | 0.0041112 | 0.98117 | -0.36061 | 0.98117 | -0.36056 | 1.1294
34 | 0.002713 | 0.00067992 | -0.002713 | -0.00067993 | 7.0019e-09 | -9.2793e-09 | 0.0041271 | 0.0041271 | 0.0041271 | 0.97817 | -0.41939 | 0.97817 | -0.41944 | 1.1338
35 | 0.0013279 | 0.0003328 | -0.0013279 | -0.00033281 | 1.8162e-09 | -1.3735e-08 | 0.0020201 | 0.0020201 | 0.0020201 | 0.97817 | -0.41944 | 0.97817 | -0.41947 | 0.55497
36 | -0.0043813 | -0.001098 | 0.0043815 | 0.001098 | 1.8135e-07 | -2.2286e-08 | 0.0066446 | 0.0066445 | 0.0066446 | 0.98117 | -0.36056 | 0.98122 | -0.3597 | 1.8254
37 | -0.054018 | -0.013595 | 0.054078 | 0.013632 | 5.9401e-05 | 3.7718e-05 | 0.081939 | 0.081939 | 0.081939 | 0.98122 | -0.3597 | 0.9824 | -0.33671 | 22.5106
38 | 0.0028072 | 0.00070348 | -0.0028071 | -0.00070353 | 4.3486e-08 | -5.3379e-08 | 0.004252 | 0.004252 | 0.004252 | 0.9824 | -0.33671 | 0.98238 | -0.33704 | 1.1681
39 | -0.059557 | -0.015006 | 0.05962 | 0.015046 | 6.3066e-05 | 4.0101e-05 | 0.090238 | 0.090238 | 0.090238 | 0.9824 | -0.33671 | 0.98353 | -0.3146 | 24.7908
40 | 0.022409 | 0.005622 | -0.022399 | -0.0056158 | 1.0154e-05 | 6.2072e-06 | 0.034111 | 0.034111 | 0.034111 | 0.97761 | -0.43041 | 0.97712 | -0.43992 | 9.3713
41 | 0.02063 | 0.0051752 | -0.020629 | -0.0051743 | 1.4157e-06 | 8.5417e-07 | 0.030798 | 0.030798 | 0.030798 | 0.99679 | -0.060671 | 0.99672 | -0.062111 | 8.4611
42 | -0.21538 | -0.05511 | 0.21556 | 0.055224 | 0.00017761 | 0.00011343 | 0.32192 | 0.32192 | 0.32192 | 0.99679 | -0.060671 | 0.99769 | -0.043653 | 44.22
43 | 0.018689 | 0.0046885 | -0.018681 | -0.0046836 | 8.2555e-06 | 4.9152e-06 | 0.027903 | 0.027903 | 0.027903 | 0.99672 | -0.062111 | 0.99624 | -0.07138 | 7.6657
44 | 0.0019395 | 0.00048582 | -0.0019394 | -0.00048607 | 7.2338e-08 | -2.5357e-07 | 0.0028954 | 0.0028955 | 0.0028955 | 0.99672 | -0.062111 | 0.99668 | -0.062894 | 0.79548
45 | -0.21956 | -0.056227 | 0.22003 | 0.056524 | 0.00046537 | 0.00029723 | 0.32789 | 0.32789 | 0.32789 | 0.99769 | -0.043653 | 1 | 0 | 45.04
46 | 0.016503 | 0.0041378 | -0.016501 | -0.0041368 | 1.7218e-06 | 1.0036e-06 | 0.02465 | 0.02465 | 0.02465 | 0.99624 | -0.07138 | 0.99612 | -0.07357 | 6.772
47 | 0.14021 | 0.036294 | -0.13995 | -0.036132 | 0.00025447 | 0.00016204 | 0.20904 | 0.20904 | 0.20904 | 1 | 0 | 0.99802 | -0.037218 | 28.7143
48 | 0.019892 | 0.0049886 | -0.019889 | -0.0049871 | 2.5252e-06 | 1.5178e-06 | 0.029788 | 0.029788 | 0.029788 | 0.99368 | -0.11999 | 0.99354 | -0.12266 | 8.1836
49 | 0.15222 | 0.03892 | -0.15185 | -0.038682 | 0.00037346 | 0.00023803 | 0.2288 | 0.2288 | 0.2288 | 0.99116 | -0.16767 | 0.98851 | -0.21852 | 31.4283
50 | 0.014414 | 0.0036136 | -0.014412 | -0.0036128 | 1.3188e-06 | 7.4527e-07 | 0.021532 | 0.021532 | 0.021532 | 0.99612 | -0.07357 | 0.99602 | -0.07549 | 5.9153
51 | 0.13724 | 0.035453 | -0.13706 | -0.035339 | 0.00017911 | 0.00011404 | 0.205 | 0.205 | 0.205 | 0.99802 | -0.037218 | 0.99659 | -0.064011 | 28.1599
52 | 0.017982 | 0.0045092 | -0.01798 | -0.004508 | 2.0274e-06 | 1.201e-06 | 0.026933 | 0.026933 | 0.026933 | 0.99354 | -0.12266 | 0.99342 | -0.12502 | 7.3991
53 | 0.14936 | 0.038058 | -0.14906 | -0.037868 | 0.00029902 | 0.00019056 | 0.22505 | 0.22505 | 0.22505 | 0.98851 | -0.21852 | 0.98635 | -0.2601 | 30.9139
54 | 0.012265 | 0.0030746 | -0.012261 | -0.0030726 | 3.7661e-06 | 2.0211e-06 | 0.018323 | 0.018324 | 0.018324 | 0.99602 | -0.07549 | 0.99569 | -0.081937 | 5.034
55 | -0.0011002 | -0.00027559 | 0.0011002 | 0.00027538 | 1.7066e-08 | -2.078e-07 | 0.0016446 | 0.0016446 | 0.0016446 | 0.99539 | -0.087763 | 0.99541 | -0.087438 | 0.45182
56 | 0.0011002 | 0.00027559 | -0.0011002 | -0.00027573 | 1.1957e-08 | -1.4557e-07 | 0.0016446 | 0.0016447 | 0.0016447 | 0.99539 | -0.087763 | 0.99538 | -0.087992 | 0.45184
57 | -0.0021426 | -0.00053663 | 0.0021427 | 0.00053655 | 2.9151e-08 | -7.9851e-08 | 0.0032029 | 0.0032028 | 0.0032029 | 0.99541 | -0.087438 | 0.99542 | -0.087152 | 0.87991
58 | 0.13537 | 0.034915 | -0.13518 | -0.034796 | 0.00018686 | 0.00011895 | 0.20247 | 0.20247 | 0.20247 | 0.99659 | -0.064011 | 0.99509 | -0.092386 | 27.8125
59 | 0.016109 | 0.0040391 | -0.016108 | -0.0040382 | 1.5718e-06 | 9.1275e-07 | 0.02413 | 0.02413 | 0.02413 | 0.99342 | -0.12502 | 0.99331 | -0.12707 | 6.6292
60 | 0.14653 | 0.037233 | -0.14635 | -0.037121 | 0.00017605 | 0.00011218 | 0.22123 | 0.22123 | 0.22123 | 0.98635 | -0.2601 | 0.98505 | -0.28509 | 30.3893
61 | 0.0014028 | 0.00035157 | -0.0014028 | -0.00035157 | 3.4064e-10 | -2.3351e-09 | 0.0021248 | 0.0021248 | 0.0021248 | 0.98238 | -0.33704 | 0.98238 | -0.33704 | 0.58373
62 | -0.061027 | -0.015398 | 0.061092 | 0.01544 | 6.4993e-05 | 4.1337e-05 | 0.092367 | 0.092367 | 0.092367 | 0.98353 | -0.3146 | 0.98468 | -0.29239 | 25.3756
63 | 0.0037539 | 0.00094074 | -0.0037538 | -0.00094079 | 1.3981e-07 | -5.3413e-08 | 0.0057167 | 0.0057167 | 0.0057167 | 0.97712 | -0.43992 | 0.97709 | -0.4407 | 1.5705
64 | 0.015485 | 0.003883 | -0.015482 | -0.0038814 | 2.8677e-06 | 1.6631e-06 | 0.023582 | 0.023582 | 0.023582 | 0.97712 | -0.43992 | 0.97693 | -0.4438 | 6.4786
65 | 0.14635 | 0.037121 | -0.1463 | -0.037089 | 5.1355e-05 | 3.2725e-05 | 0.22123 | 0.22123 | 0.22123 | 0.98505 | -0.28509 | 0.98468 | -0.29239 | 30.3893
66 | 0.08126 | 0.020556 | -0.081178 | -0.020505 | 8.1292e-05 | 5.1307e-05 | 0.1233 | 0.1233 | 0.1233 | 0.98123 | -0.35927 | 0.98015 | -0.38014 | 16.9365
67 | -0.083528 | -0.021125 | 0.08363 | 0.021189 | 0.00010128 | 6.3968e-05 | 0.12674 | 0.12674 | 0.12674 | 0.98123 | -0.35927 | 0.98253 | -0.33403 | 17.4091
68 | 0.079585 | 0.020106 | -0.079582 | -0.020103 | 3.6197e-06 | 2.2833e-06 | 0.12088 | 0.12088 | 0.12088 | 0.98015 | -0.38014 | 0.98011 | -0.38109 | 16.6043
69 | -0.085036 | -0.021541 | 0.085157 | 0.021618 | 0.00012101 | 7.6459e-05 | 0.12887 | 0.12887 | 0.12887 | 0.98253 | -0.33403 | 0.98405 | -0.30445 | 17.7016
70 | -0.085157 | -0.021618 | 0.085207 | 0.021649 | 4.945e-05 | 3.1244e-05 | 0.12887 | 0.12887 | 0.12887 | 0.98405 | -0.30445 | 0.98468 | -0.29239 | 17.7016
71 | 0.011825 | 0.0029648 | -0.011822 | -0.0029632 | 3.0305e-06 | 1.6277e-06 | 0.018012 | 0.018012 | 0.018012 | 0.97693 | -0.4438 | 0.97665 | -0.44918 | 4.9483
72 | 0.077837 | 0.019666 | -0.077688 | -0.019572 | 0.00014878 | 9.3788e-05 | 0.11823 | 0.11823 | 0.11823 | 0.98011 | -0.38109 | 0.97806 | -0.42105 | 16.2404
73 | 0.032801 | 0.0082447 | -0.032778 | -0.0082307 | 2.2338e-05 | 1.3996e-05 | 0.049911 | 0.049912 | 0.049912 | 0.97806 | -0.42105 | 0.97733 | -0.43532 | 13.712
74 | 0.039824 | 0.010059 | -0.039816 | -0.010054 | 7.8542e-06 | 4.7406e-06 | 0.060616 | 0.060616 | 0.060616 | 0.97806 | -0.42105 | 0.97785 | -0.42517 | 8.3264
75 | 0.031363 | 0.007876 | -0.031362 | -0.0078751 | 1.3939e-06 | 8.7167e-07 | 0.047757 | 0.047757 | 0.047757 | 0.97733 | -0.43532 | 0.97729 | -0.43625 | 13.12
76 | 0.039816 | 0.010054 | -0.039754 | -0.010015 | 6.1973e-05 | 3.91e-05 | 0.060616 | 0.060617 | 0.060617 | 0.97785 | -0.42517 | 0.97619 | -0.45771 | 16.6529
77 | -0.0022322 | -0.00055931 | 0.0022322 | 0.00055931 | 2.3124e-10 | -5.4991e-10 | 0.0033615 | 0.0033615 | 0.0033615 | 0.98808 | -0.22593 | 0.98808 | -0.22593 | 0.9235
78 | 0.00068276 | 0.00017099 | -0.00068276 | -0.00017112 | 3.9651e-09 | -1.2557e-07 | 0.0010282 | 0.0010282 | 0.0010282 | 0.98808 | -0.22593 | 0.98807 | -0.22606 | 0.28248
79 | -0.004025 | -0.0010086 | 0.0040253 | 0.0010086 | 2.2048e-07 | -6.3865e-08 | 0.0060615 | 0.0060615 | 0.0060615 | 0.98808 | -0.22593 | 0.98814 | -0.22478 | 1.6653
80 | -0.12618 | -0.032217 | 0.12649 | 0.032415 | 0.00030968 | 0.0001979 | 0.19022 | 0.19022 | 0.19022 | 0.98814 | -0.22478 | 0.99079 | -0.17414 | 52.2577
81 | 0.12215 | 0.031209 | -0.1217 | -0.030918 | 0.00045444 | 0.00029038 | 0.18416 | 0.18416 | 0.18416 | 0.98814 | -0.22478 | 0.98412 | -0.30203 | 50.5925
82 | -0.12875 | -0.032982 | 0.12881 | 0.033021 | 6.0726e-05 | 3.8809e-05 | 0.19362 | 0.19362 | 0.19362 | 0.99079 | -0.17414 | 0.9913 | -0.16441 | 53.1911
83 | 0.0099172 | 0.0024859 | -0.0099158 | -0.0024852 | 1.3875e-06 | 6.7896e-07 | 0.014995 | 0.014995 | 0.014995 | 0.98412 | -0.30203 | 0.98397 | -0.30497 | 4.1196
84 | -0.12881 | -0.033021 | 0.12904 | 0.03317 | 0.00023274 | 0.00014874 | 0.19362 | 0.19362 | 0.19362 | 0.9913 | -0.16441 | 0.99325 | -0.12721 | 53.1911
85 | 0.0079903 | 0.0020026 | -0.0079899 | -0.0020025 | 4.1733e-07 | 1.7028e-07 | 0.012083 | 0.012083 | 0.012083 | 0.98397 | -0.30497 | 0.98392 | -0.30607 | 3.3196
86 | 0.0028251 | 0.00070767 | -0.002825 | -0.00070778 | 8.8527e-08 | -1.1392e-07 | 0.0042322 | 0.0042323 | 0.0042323 | 0.99325 | -0.12721 | 0.99322 | -0.12787 | 1.1627
87 | -0.13187 | -0.033877 | 0.13193 | 0.033916 | 6.0345e-05 | 3.8568e-05 | 0.19785 | 0.19785 | 0.19785 | 0.99325 | -0.12721 | 0.99375 | -0.11779 | 54.3538
88 | 0.0098698 | 0.0024739 | -0.0098689 | -0.0024735 | 9.0587e-07 | 4.4609e-07 | 0.015038 | 0.015038 | 0.015038 | 0.97665 | -0.44918 | 0.97656 | -0.45111 | 4.1312
89 | 0.0082218 | 0.0020606 | -0.0082201 | -0.0020599 | 1.677e-06 | 7.1687e-07 | 0.012528 | 0.012528 | 0.012528 | 0.97656 | -0.45111 | 0.97634 | -0.45539 | 3.4417
90 | -0.0032133 | -0.00080488 | 0.0032133 | 0.00080482 | 6.3312e-08 | -5.461e-08 | 0.0048033 | 0.0048032 | 0.0048033 | 0.99542 | -0.087152 | 0.99544 | -0.086738 | 1.3196
91 | -0.0041896 | -0.0010495 | 0.0041898 | 0.0010494 | 2.3003e-07 | -5.6118e-08 | 0.0062626 | 0.0062625 | 0.0062626 | 0.99544 | -0.086738 | 0.9955 | -0.085585 | 1.7205
92 | -0.0010821 | -0.00027119 | 0.0010821 | 0.00027096 | 1.8304e-08 | -2.2866e-07 | 0.0016211 | 0.0016211 | 0.0016211 | 0.9932 | -0.12823 | 0.99322 | -0.12787 | 0.44537
93 | 0.010351 | 0.0025938 | -0.010349 | -0.002593 | 1.6688e-06 | 8.262e-07 | 0.015469 | 0.015469 | 0.015469 | 0.99569 | -0.081937 | 0.99551 | -0.085322 | 4.2497
94 | -0.0062748 | -0.001572 | 0.0062749 | 0.001572 | 7.872e-08 | 1.9354e-08 | 0.009379 | 0.009379 | 0.009379 | 0.9955 | -0.085585 | 0.99551 | -0.085322 | 2.5767
95 | 0.13385 | 0.034462 | -0.13369 | -0.034357 | 0.00016523 | 0.00010518 | 0.20048 | 0.20048 | 0.20048 | 0.99509 | -0.092386 | 0.99375 | -0.11779 | 27.5388
96 | 0.0017598 | 0.00044088 | -0.0017597 | -0.00044103 | 3.6243e-08 | -1.5714e-07 | 0.002635 | 0.0026351 | 0.0026351 | 0.99375 | -0.11779 | 0.99373 | -0.11823 | 0.72392
97 | 0.0065014 | 0.0016292 | -0.0065008 | -0.001629 | 5.6339e-07 | 1.6922e-07 | 0.0099085 | 0.0099086 | 0.0099086 | 0.97634 | -0.45539 | 0.97625 | -0.45721 | 2.7221
98 | 0.0038382 | 0.00096181 | -0.003838 | -0.00096189 | 2.1894e-07 | -7.3156e-08 | 0.0058502 | 0.0058503 | 0.0058503 | 0.97625 | -0.45721 | 0.97619 | -0.45841 | 1.6072
99 | 0.0026626 | 0.00066719 | -0.0026625 | -0.0006673 | 7.4454e-08 | -1.0307e-07 | 0.0040584 | 0.0040584 | 0.0040584 | 0.97625 | -0.45721 | 0.97622 | -0.4578 | 1.115
100 | 0.01436 | 0.0036001 | -0.014357 | -0.0035985 | 2.7049e-06 | 1.5294e-06 | 0.021512 | 0.021512 | 0.021512 | 0.99331 | -0.12707 | 0.99311 | -0.13102 | 5.9098
101 | 0.012428 | 0.0031151 | -0.012427 | -0.0031145 | 9.8691e-07 | 5.3343e-07 | 0.018621 | 0.018621 | 0.018621 | 0.99311 | -0.13102 | 0.99302 | -0.13269 | 5.1157
102 | 0.010284 | 0.0025774 | -0.010283 | -0.0025771 | 6.6376e-07 | 3.2838e-07 | 0.01541 | 0.01541 | 0.01541 | 0.99302 | -0.13269 | 0.99295 | -0.13404 | 4.2335
103 | 0.0081782 | 0.0020496 | -0.0081778 | -0.0020494 | 4.0544e-07 | 1.6638e-07 | 0.012256 | 0.012256 | 0.012256 | 0.99295 | -0.13404 | 0.9929 | -0.13509 | 3.3669
104 | 0.0019597 | 0.00049106 | -0.0019597 | -0.00049114 | 2.3465e-08 | -7.9792e-08 | 0.0029292 | 0.0029293 | 0.0029293 | 0.99549 | -0.085725 | 0.99548 | -0.085976 | 0.80474
105 | -0.0040743 | -0.001021 | 0.0040744 | 0.001021 | 7.8262e-08 | -2.3073e-08 | 0.00609 | 0.00609 | 0.00609 | 0.99549 | -0.085725 | 0.99551 | -0.085322 | 1.6731
106 | 0.03748 | 0.0094447 | -0.037462 | -0.0094336 | 1.7588e-05 | 1.1077e-05 | 0.057149 | 0.05715 | 0.05715 | 0.97619 | -0.45771 | 0.97569 | -0.46752 | 15.7004
107 | 0.035415 | 0.0089206 | -0.03541 | -0.0089173 | 5.2166e-06 | 3.2791e-06 | 0.054028 | 0.054028 | 0.054028 | 0.97569 | -0.46752 | 0.97553 | -0.4706 | 14.8428
108 | 0.029978 | 0.0075283 | -0.029971 | -0.007524 | 6.8623e-06 | 4.2819e-06 | 0.045649 | 0.045649 | 0.045649 | 0.97729 | -0.43625 | 0.97704 | -0.44105 | 12.5411
109 | 0.033249 | 0.0083756 | -0.033227 | -0.0083622 | 2.1477e-05 | 1.3468e-05 | 0.050731 | 0.050731 | 0.050731 | 0.97553 | -0.4706 | 0.97484 | -0.48412 | 13.9371
110 | 0.026791 | 0.0067271 | -0.026778 | -0.0067189 | 1.3127e-05 | 8.1381e-06 | 0.040807 | 0.040807 | 0.040807 | 0.97704 | -0.44105 | 0.97652 | -0.45133 | 11.2107
111 | 0.02561 | 0.0064261 | -0.025607 | -0.0064246 | 2.5348e-06 | 1.5668e-06 | 0.039027 | 0.039027 | 0.039027 | 0.97652 | -0.45133 | 0.97641 | -0.45341 | 10.7216
112 | 0.021131 | 0.0053028 | -0.021123 | -0.0052978 | 8.2476e-06 | 5.0134e-06 | 0.032205 | 0.032206 | 0.032206 | 0.97641 | -0.45341 | 0.976 | -0.46159 | 8.8477
113 | 0.018514 | 0.0046438 | -0.018511 | -0.0046424 | 2.3548e-06 | 1.4086e-06 | 0.028227 | 0.028227 | 0.028227 | 0.976 | -0.46159 | 0.97586 | -0.46426 | 7.7548
114 | 0.016378 | 0.0041078 | -0.016375 | -0.0041058 | 3.2901e-06 | 1.93e-06 | 0.024975 | 0.024975 | 0.024975 | 0.97586 | -0.46426 | 0.97565 | -0.46848 | 6.8612
115 | 0.031724 | 0.0079854 | -0.031706 | -0.0079742 | 1.7964e-05 | 1.1242e-05 | 0.048437 | 0.048437 | 0.048437 | 0.97484 | -0.48412 | 0.97424 | -0.49597 | 13.3068
116 | 0.029548 | 0.0074334 | -0.029534 | -0.0074245 | 1.4152e-05 | 8.827e-06 | 0.045141 | 0.045141 | 0.045141 | 0.97424 | -0.49597 | 0.97373 | -0.506 | 12.4013
117 | 0.028142 | 0.0070755 | -0.02814 | -0.0070747 | 1.3155e-06 | 8.1831e-07 | 0.043013 | 0.043013 | 0.043013 | 0.97373 | -0.506 | 0.97368 | -0.50698 | 11.8167
118 | 0.026512 | 0.0066667 | -0.026499 | -0.0066587 | 1.2886e-05 | 7.9872e-06 | 0.040525 | 0.040525 | 0.040525 | 0.97368 | -0.50698 | 0.97316 | -0.51716 | 11.1333
119 | 0.0083988 | 0.0021055 | -0.0083958 | -0.0021042 | 2.984e-06 | 1.3174e-06 | 0.012879 | 0.012879 | 0.012879 | 0.97039 | -0.57203 | 0.97001 | -0.57949 | 3.5383
120 | -0.015681 | -0.0039306 | 0.015688 | 0.0039346 | 6.8016e-06 | 3.9653e-06 | 0.024046 | 0.024046 | 0.024046 | 0.97039 | -0.57203 | 0.97085 | -0.56293 | 6.6061
121 | -0.015688 | -0.0039346 | 0.015692 | 0.0039368 | 3.7264e-06 | 2.1723e-06 | 0.024046 | 0.024046 | 0.024046 | 0.97085 | -0.56293 | 0.9711 | -0.55795 | 6.6061
122 | -0.015692 | -0.0039368 | 0.015703 | 0.0039436 | 1.1681e-05 | 6.809e-06 | 0.024046 | 0.024046 | 0.024046 | 0.9711 | -0.55795 | 0.97189 | -0.54235 | 6.606
123 | 0.021712 | 0.0054583 | -0.021687 | -0.0054432 | 2.4662e-05 | 1.5044e-05 | 0.033207 | 0.033207 | 0.033207 | 0.97309 | -0.51853 | 0.97189 | -0.54235 | 9.1228
124 | -0.023372 | -0.0058744 | 0.023374 | 0.0058754 | 1.5278e-06 | 9.3818e-07 | 0.035746 | 0.035746 | 0.035746 | 0.97309 | -0.51853 | 0.97316 | -0.51716 | 9.8203
125 | -0.010727 | -0.0026885 | 0.010728 | 0.002689 | 1.0302e-06 | 5.3144e-07 | 0.016369 | 0.016369 | 0.016369 | 0.97513 | -0.47874 | 0.97523 | -0.47673 | 4.497
126 | 0.0071428 | 0.0017902 | -0.0071424 | -0.00179 | 3.9003e-07 | 1.4042e-07 | 0.0109 | 0.0109 | 0.0109 | 0.97513 | -0.47874 | 0.97507 | -0.47989 | 2.9945
127 | -0.012159 | -0.0030476 | 0.01216 | 0.0030483 | 1.3376e-06 | 7.2676e-07 | 0.018553 | 0.018553 | 0.018553 | 0.97523 | -0.47673 | 0.97535 | -0.47442 | 5.0969
128 | 0.0057673 | 0.0014454 | -0.0057669 | -0.0014453 | 4.262e-07 | 8.9776e-08 | 0.0088013 | 0.0088013 | 0.0088013 | 0.97507 | -0.47989 | 0.97499 | -0.48144 | 2.4179
129 | -0.013499 | -0.0033838 | 0.013501 | 0.0033849 | 1.8987e-06 | 1.0661e-06 | 0.020595 | 0.020595 | 0.020595 | 0.97535 | -0.47442 | 0.9755 | -0.47146 | 5.6579
130 | 0.0015376 | 0.00038532 | -0.0015376 | -0.00038535 | 6.3306e-09 | -3.4181e-08 | 0.0023466 | 0.0023466 | 0.0023466 | 0.97499 | -0.48144 | 0.97499 | -0.48153 | 0.64468
131 | -0.015131 | -0.0037935 | 0.015133 | 0.0037948 | 2.1542e-06 | 1.2441e-06 | 0.023082 | 0.023082 | 0.023082 | 0.9755 | -0.47146 | 0.97565 | -0.46848 | 6.3411

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.365 | 0.093599

## res_load
| p_mw | q_mvar
0 | 0.02458 | 0.0061604
1 | 0.019159 | 0.0048017
2 | 0.0074087 | 0.0018568
3 | 0.0088468 | 0.0022172
4 | 0.016399 | 0.0041099
5 | 0.0077562 | 0.0019439
6 | 0.016398 | 0.0041098
7 | 0.010144 | 0.0025424
8 | 0.010133 | 0.0025396
9 | 0.001965 | 0.00049247
10 | 0.0021045 | 0.00052743
11 | 0.0024827 | 0.00062222
12 | 0.0037033 | 0.00092813
13 | 0.0021439 | 0.0005373
14 | 0.0014909 | 0.00037365
15 | 0.0016583 | 0.00041561
16 | 0.0014507 | 0.00036359
17 | 0.0037472 | 0.00093914
18 | 0.003915 | 0.0009812
19 | 0.0039569 | 0.00099168
20 | 0.00099052 | 0.00024825
21 | 0.0017203 | 0.00043115
22 | 0.0015303 | 0.00038352
23 | 0.0013851 | 0.00034713
24 | 0.0016705 | 0.00041866
25 | 0.0027633 | 0.00069255
26 | 0.0026724 | 0.00066978
27 | 0.0013279 | 0.00033281
28 | 0.0038677 | 0.00096934
29 | 0.0040029 | 0.0010032
30 | 0.0021778 | 0.00054581
31 | 0.0019394 | 0.00048607
32 | 0.0031155 | 0.00078081
33 | 0.0019293 | 0.00048352
34 | 0.0034787 | 0.00087186
35 | 0.0020877 | 0.00052321
36 | 0.0027073 | 0.00067852
37 | 0.0019068 | 0.00047789
38 | 0.0024883 | 0.00062363
39 | 0.0021475 | 0.00053821
40 | 0.0010424 | 0.00026125
41 | 0.0011002 | 0.00027573
42 | 0.0016941 | 0.00042457
43 | 0.001871 | 0.00046891
44 | 0.0025315 | 0.00063445
45 | 0.0014044 | 0.00035197
46 | 0.001407 | 0.00035263
47 | 0.0031603 | 0.00079204
48 | 0.0022688 | 0.00056861
49 | 0.0015929 | 0.00039921
50 | 0.0014064 | 0.00035248
51 | 0.0014028 | 0.00035157
52 | 0.0037538 | 0.00094079
53 | 0.0036572 | 0.00091657
54 | 0.0017453 | 0.00043741
55 | 0.005063 | 0.0012689
56 | 0.0014153 | 0.00035471
57 | 0.0015494 | 0.00038832
58 | 0.0017929 | 0.00044933
59 | 0.00068276 | 0.00017112
60 | 0.0022625 | 0.00056703
61 | 0.0019255 | 0.00048257
62 | 0.0079899 | 0.0020025
63 | 0.0019521 | 0.00048925
64 | 0.0016472 | 0.00041282
65 | 0.0010706 | 0.00026832
66 | 0.00097628 | 0.00024468
67 | 0.0010821 | 0.00027119
68 | 0.0017429 | 0.00043682
69 | 0.0019102 | 0.00047874
70 | 0.002085 | 0.00052254
71 | 0.0013324 | 0.00033392
72 | 0.0017597 | 0.00044103
73 | 0.0017187 | 0.00043075
74 | 0.003838 | 0.00096189
75 | 0.0026625 | 0.0006673
76 | 0.0017481 | 0.00043811
77 | 0.0019291 | 0.00048347
78 | 0.0021432 | 0.00053713
79 | 0.0021048 | 0.00052752
80 | 0.0021146 | 0.00052997
81 | 0.0019597 | 0.00049114
82 | 0.0022745 | 0.00057005
83 | 0.0020468 | 0.00051298
84 | 0.001384 | 0.00034687
85 | 0.0021614 | 0.0005417
86 | 0.0031796 | 0.00079689
87 | 0.0011683 | 0.00029281
88 | 0.004476 | 0.0011218
89 | 0.0026094 | 0.00065397
90 | 0.0021331 | 0.00053461
91 | 0.0015032 | 0.00037675
92 | 0.0021579 | 0.00054082
93 | 0.0013925 | 0.00034899
94 | 0.001628 | 0.00040801
95 | 0.0072824 | 0.0018251
96 | 0.0083958 | 0.0021042
97 | 0.0016605 | 0.00041615
98 | 0.0059836 | 0.0014996
99 | 0.0031256 | 0.00078336
100 | 0.0035842 | 0.0008983
101 | 0.001431 | 0.00035863
102 | 0.0013751 | 0.00034464
103 | 0.0013386 | 0.00033548
104 | 0.0042293 | 0.00106
105 | 0.0016305 | 0.00040863
106 | 0.0015376 | 0.00038535
107 | 0.0012413 | 0.00031109
108 | 0.0019638 | 0.00049218

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1