## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-32_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-32_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-32_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-32_0_3_node_58 | 0.4 | n |  | TRUE
4 | bus_LV_1054-32_0_3_node_34 | 0.4 | n |  | TRUE
5 | bus_LV_1054-32_0_3_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_1054-32_0_3_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_1054-32_0_3_node_79 | 0.4 | n |  | TRUE
8 | bus_LV_1054-32_0_3_node_188 | 0.4 | n |  | TRUE
9 | bus_LV_1054-32_0_3_node_162 | 0.4 | n |  | TRUE
10 | bus_LV_1054-32_0_3_node_159 | 0.4 | n |  | TRUE
11 | bus_LV_1054-32_0_3_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_1054-32_0_3_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_1054-32_0_3_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1054-32_0_3_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_1054-32_0_3_node_220 | 0.4 | n |  | TRUE
16 | bus_LV_1054-32_0_3_node_168 | 0.4 | n |  | TRUE
17 | bus_LV_1054-32_0_3_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_1054-32_0_3_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1054-32_0_3_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_1054-32_0_3_node_49 | 0.4 | n |  | TRUE
21 | bus_LV_1054-32_0_3_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_1054-32_0_3_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_1054-32_0_3_node_75 | 0.4 | n |  | TRUE
24 | bus_LV_1054-32_0_3_node_235 | 0.4 | n |  | TRUE
25 | bus_LV_1054-32_0_3_node_264 | 0.4 | n |  | TRUE
26 | bus_LV_1054-32_0_3_node_224 | 0.4 | n |  | TRUE
27 | bus_LV_1054-32_0_3_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_1054-32_0_3_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_1054-32_0_3_node_55 | 0.4 | n |  | TRUE
30 | bus_LV_1054-32_0_3_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_1054-32_0_3_node_56 | 0.4 | n |  | TRUE
32 | bus_LV_1054-32_0_3_node_57 | 0.4 | n |  | TRUE
33 | bus_LV_1054-32_0_3_node_139 | 0.4 | n |  | TRUE
34 | bus_LV_1054-32_0_3_node_143 | 0.4 | n |  | TRUE
35 | bus_LV_1054-32_0_3_node_221 | 0.4 | n |  | TRUE
36 | bus_LV_1054-32_0_3_node_68 | 0.4 | n |  | TRUE
37 | bus_LV_1054-32_0_3_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_1054-32_0_3_node_71 | 0.4 | n |  | TRUE
39 | bus_LV_1054-32_0_3_node_98 | 0.4 | n |  | TRUE
40 | bus_LV_1054-32_0_3_node_73 | 0.4 | n |  | TRUE
41 | bus_LV_1054-32_0_3_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_1054-32_0_3_node_76 | 0.4 | n |  | TRUE
43 | bus_LV_1054-32_0_3_node_77 | 0.4 | n |  | TRUE
44 | bus_LV_1054-32_0_3_node_78 | 0.4 | n |  | TRUE
45 | bus_LV_1054-32_0_3_node_103 | 0.4 | n |  | TRUE
46 | bus_LV_1054-32_0_3_node_271 | 0.4 | n |  | TRUE
47 | bus_LV_1054-32_0_3_node_80 | 0.4 | n |  | TRUE
48 | bus_LV_1054-32_0_3_node_81 | 0.4 | n |  | TRUE
49 | bus_LV_1054-32_0_3_node_82 | 0.4 | n |  | TRUE
50 | bus_LV_1054-32_0_3_node_83 | 0.4 | n |  | TRUE
51 | bus_LV_1054-32_0_3_node_96 | 0.4 | n |  | TRUE
52 | bus_LV_1054-32_0_3_node_84 | 0.4 | n |  | TRUE
53 | bus_LV_1054-32_0_3_node_256 | 0.4 | n |  | TRUE
54 | bus_LV_1054-32_0_3_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_1054-32_0_3_node_92 | 0.4 | n |  | TRUE
56 | bus_LV_1054-32_0_3_node_93 | 0.4 | n |  | TRUE
57 | bus_LV_1054-32_0_3_node_94 | 0.4 | n |  | TRUE
58 | bus_LV_1054-32_0_3_node_95 | 0.4 | n |  | TRUE
59 | bus_LV_1054-32_0_3_node_212 | 0.4 | n |  | TRUE
60 | bus_LV_1054-32_0_3_node_173 | 0.4 | n |  | TRUE
61 | bus_LV_1054-32_0_3_node_97 | 0.4 | n |  | TRUE
62 | bus_LV_1054-32_0_3_node_166 | 0.4 | n |  | TRUE
63 | bus_LV_1054-32_0_3_node_101 | 0.4 | n |  | TRUE
64 | bus_LV_1054-32_0_3_node_99 | 0.4 | n |  | TRUE
65 | bus_LV_1054-32_0_3_node_100 | 0.4 | n |  | TRUE
66 | bus_LV_1054-32_0_3_node_102 | 0.4 | n |  | TRUE
67 | bus_LV_1054-32_0_3_node_104 | 0.4 | n |  | TRUE
68 | bus_LV_1054-32_0_3_node_250 | 0.4 | n |  | TRUE
69 | bus_LV_1054-32_0_3_node_118 | 0.4 | n |  | TRUE
70 | bus_LV_1054-32_0_3_node_105 | 0.4 | n |  | TRUE
71 | bus_LV_1054-32_0_3_node_107 | 0.4 | n |  | TRUE
72 | bus_LV_1054-32_0_3_node_108 | 0.4 | n |  | TRUE
73 | bus_LV_1054-32_0_3_node_225 | 0.4 | n |  | TRUE
74 | bus_LV_1054-32_0_3_node_116 | 0.4 | n |  | TRUE
75 | bus_LV_1054-32_0_3_node_117 | 0.4 | n |  | TRUE
76 | bus_LV_1054-32_0_3_node_120 | 0.4 | n |  | TRUE
77 | bus_LV_1054-32_0_3_node_121 | 0.4 | n |  | TRUE
78 | bus_LV_1054-32_0_3_node_122 | 0.4 | n |  | TRUE
79 | bus_LV_1054-32_0_3_node_123 | 0.4 | n |  | TRUE
80 | bus_LV_1054-32_0_3_node_211 | 0.4 | n |  | TRUE
81 | bus_LV_1054-32_0_3_node_208 | 0.4 | n |  | TRUE
82 | bus_LV_1054-32_0_3_node_274 | 0.4 | n |  | TRUE
83 | bus_LV_1054-32_0_3_node_275 | 0.4 | n |  | TRUE
84 | bus_LV_1054-32_0_3_node_167 | 0.4 | n |  | TRUE
85 | bus_LV_1054-32_0_3_node_136 | 0.4 | n |  | TRUE
86 | bus_LV_1054-32_0_3_node_253 | 0.4 | n |  | TRUE
87 | bus_LV_1054-32_0_3_node_284 | 0.4 | n |  | TRUE
88 | bus_LV_1054-32_0_3_node_160 | 0.4 | n |  | TRUE
89 | bus_LV_1054-32_0_3_node_161 | 0.4 | n |  | TRUE
90 | bus_LV_1054-32_0_3_node_169 | 0.4 | n |  | TRUE
91 | bus_LV_1054-32_0_3_node_171 | 0.4 | n |  | TRUE
92 | bus_LV_1054-32_0_3_node_172 | 0.4 | n |  | TRUE
93 | bus_LV_1054-32_0_3_node_189 | 0.4 | n |  | TRUE
94 | bus_LV_1054-32_0_3_node_191 | 0.4 | n |  | TRUE
95 | bus_LV_1054-32_0_3_node_230 | 0.4 | n |  | TRUE
96 | bus_LV_1054-32_0_3_node_209 | 0.4 | n |  | TRUE
97 | bus_LV_1054-32_0_3_node_210 | 0.4 | n |  | TRUE
98 | bus_LV_1054-32_0_3_node_268 | 0.4 | n |  | TRUE
99 | bus_LV_1054-32_0_3_node_236 | 0.4 | n |  | TRUE
100 | bus_LV_1054-32_0_3_node_222 | 0.4 | n |  | TRUE
101 | bus_LV_1054-32_0_3_node_223 | 0.4 | n |  | TRUE
102 | bus_LV_1054-32_0_3_node_237 | 0.4 | n |  | TRUE
103 | bus_LV_1054-32_0_3_node_252 | 0.4 | n |  | TRUE
104 | bus_LV_1054-32_0_3_node_233 | 0.4 | n |  | TRUE
105 | bus_LV_1054-32_0_3_node_234 | 0.4 | n |  | TRUE
106 | bus_LV_1054-32_0_3_node_245 | 0.4 | n |  | TRUE
107 | bus_LV_1054-32_0_3_node_246 | 0.4 | n |  | TRUE
108 | bus_LV_1054-32_0_3_node_247 | 0.4 | n |  | TRUE
109 | bus_LV_1054-32_0_3_node_248 | 0.4 | n |  | TRUE
110 | bus_LV_1054-32_0_3_node_249 | 0.4 | n |  | TRUE
111 | bus_LV_1054-32_0_3_node_254 | 0.4 | n |  | TRUE
112 | bus_LV_1054-32_0_3_node_257 | 0.4 | n |  | TRUE
113 | bus_LV_1054-32_0_3_node_263 | 0.4 | n |  | TRUE
114 | bus_LV_1054-32_0_3_node_265 | 0.4 | n |  | TRUE
115 | bus_LV_1054-32_0_3_node_270 | 0.4 | n |  | TRUE
116 | bus_MV_211_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-32_0_3_load_0 | 0 | 0.0010631 | 0.00026643 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-32_0_3_load_1 | 1 | 0.00097689 | 0.00024483 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-32_0_3_load_85 | 6 | 0.003006 | 0.00075338 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-32_0_3_load_79 | 7 | 0.0015964 | 0.0004001 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-32_0_3_load_188 | 8 | 0.0037648 | 0.00094354 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-32_0_3_load_162 | 9 | 0.0020448 | 0.00051247 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-32_0_3_load_159 | 10 | 0.0020442 | 0.00051232 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-32_0_3_load_42 | 11 | 0.0023537 | 0.0005899 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-32_0_3_load_43 | 12 | 0.0030029 | 0.00075259 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-32_0_3_load_44 | 13 | 0.0029682 | 0.0007439 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-32_0_3_load_45 | 14 | 0.0017422 | 0.00043664 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-32_0_3_load_220 | 15 | 0.0024043 | 0.00060259 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-32_0_3_load_168 | 16 | 0.002074 | 0.00051979 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-32_0_3_load_46 | 17 | 0.0039435 | 0.00098833 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-32_0_3_load_47 | 18 | 0.0074032 | 0.0018554 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-32_0_3_load_49 | 20 | 0.0035651 | 0.0008935 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-32_0_3_load_51 | 22 | 0.0030204 | 0.00075697 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-32_0_3_load_235 | 24 | 0.0053131 | 0.0013316 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-32_0_3_load_264 | 25 | 0.0036758 | 0.00092125 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-32_0_3_load_224 | 26 | 0.0051289 | 0.0012854 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-32_0_3_load_52 | 27 | 0.0039039 | 0.0009784 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-32_0_3_load_53 | 28 | 0.0051018 | 0.0012786 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-32_0_3_load_55 | 29 | 0.0017155 | 0.00042995 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-32_0_3_load_143 | 34 | 0.0019347 | 0.00048488 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-32_0_3_load_221 | 35 | 0.0063233 | 0.0015848 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-32_0_3_load_68 | 36 | 0.0016094 | 0.00040336 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-32_0_3_load_69 | 37 | 0.0028438 | 0.00071272 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-32_0_3_load_98 | 39 | 0.007908 | 0.0019819 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-32_0_3_load_73 | 40 | 0.0024767 | 0.00062072 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-32_0_3_load_74 | 41 | 0.0034106 | 0.00085477 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-32_0_3_load_76 | 42 | 0.0023622 | 0.00059203 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-32_0_3_load_77 | 43 | 0.0024254 | 0.00060785 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-32_0_3_load_78 | 44 | 0.0041114 | 0.0010304 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-32_0_3_load_103 | 45 | 0.0020933 | 0.00052463 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-32_0_3_load_271 | 46 | 0.016665 | 0.0041767 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-32_0_3_load_81 | 48 | 0.0025801 | 0.00064663 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-32_0_3_load_82 | 49 | 0.0018087 | 0.0004533 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-32_0_3_load_96 | 51 | 0.0031929 | 0.00080022 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-32_0_3_load_256 | 53 | 0.0044334 | 0.0011111 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-32_0_3_load_106 | 54 | 0.0026414 | 0.000662 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-32_0_3_load_92 | 55 | 0.0048525 | 0.0012161 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-32_0_3_load_93 | 56 | 0.0037305 | 0.00093494 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-32_0_3_load_94 | 57 | 0.0020664 | 0.0005179 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-32_0_3_load_212 | 59 | 0.0036966 | 0.00092644 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-32_0_3_load_173 | 60 | 0.003654 | 0.00091578 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-32_0_3_load_97 | 61 | 0.0023722 | 0.00059454 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-32_0_3_load_166 | 62 | 0.002375 | 0.00059524 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-32_0_3_load_99 | 64 | 0.0021019 | 0.00052679 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-32_0_3_load_100 | 65 | 0.0018764 | 0.00047028 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-32_0_3_load_102 | 66 | 0.0016647 | 0.00041722 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-32_0_3_load_104 | 67 | 0.0019482 | 0.00048827 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-32_0_3_load_250 | 68 | 0.0033281 | 0.0008341 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-32_0_3_load_118 | 69 | 0.0022711 | 0.00056919 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-32_0_3_load_105 | 70 | 0.00098776 | 0.00024756 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-32_0_3_load_107 | 71 | 0.00098809 | 0.00024764 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-32_0_3_load_108 | 72 | 0.0061418 | 0.0015393 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-32_0_3_load_225 | 73 | 0.0033187 | 0.00083174 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-32_0_3_load_116 | 74 | 0.0018483 | 0.00046322 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-32_0_3_load_117 | 75 | 0.0012699 | 0.00031826 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-32_0_3_load_123 | 79 | 0.0020597 | 0.00051621 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-32_0_3_load_211 | 80 | 0.0024431 | 0.0006123 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-32_0_3_load_208 | 81 | 0.0020565 | 0.0005154 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-32_0_3_load_274 | 82 | 0.0083326 | 0.0020883 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-32_0_3_load_275 | 83 | 0.0028135 | 0.00070513 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-32_0_3_load_167 | 84 | 0.0020568 | 0.00051549 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-32_0_3_load_136 | 85 | 0.00072824 | 0.00018251 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-32_0_3_load_253 | 86 | 0.00066373 | 0.00016635 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-32_0_3_load_284 | 87 | 0.0017967 | 0.00045031 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-32_0_3_load_160 | 88 | 0.0020316 | 0.00050916 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-32_0_3_load_161 | 89 | 0.0026956 | 0.00067557 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-32_0_3_load_169 | 90 | 0.0020009 | 0.00050146 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-32_0_3_load_171 | 91 | 0.0024415 | 0.00061189 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-32_0_3_load_172 | 92 | 0.0040894 | 0.0010249 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-32_0_3_load_189 | 93 | 0.00074781 | 0.00018742 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-32_0_3_load_191 | 94 | 0.0012268 | 0.00030745 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-32_0_3_load_230 | 95 | 0.00066383 | 0.00016637 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-32_0_3_load_209 | 96 | 0.0027692 | 0.00069403 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-32_0_3_load_210 | 97 | 0.0032273 | 0.00080885 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-32_0_3_load_268 | 98 | 0.0025858 | 0.00064805 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-32_0_3_load_236 | 99 | 0.0043582 | 0.0010923 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-32_0_3_load_222 | 100 | 0.00084318 | 0.00021132 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-32_0_3_load_223 | 101 | 0.0026992 | 0.00067649 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-32_0_3_load_237 | 102 | 0.0032678 | 0.00081899 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-32_0_3_load_252 | 103 | 0.00070533 | 0.00017677 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-32_0_3_load_233 | 104 | 0.0051081 | 0.0012802 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-32_0_3_load_234 | 105 | 0.0026408 | 0.00066184 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-32_0_3_load_245 | 106 | 0.0017575 | 0.00044046 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-32_0_3_load_246 | 107 | 0.00164 | 0.00041103 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-32_0_3_load_247 | 108 | 0.001788 | 0.00044812 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-32_0_3_load_248 | 109 | 0.0022837 | 0.00057236 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1054-32_0_3_load_249 | 110 | 0.0017336 | 0.00043449 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1054-32_0_3_load_254 | 111 | 0.0019291 | 0.00048347 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1054-32_0_3_load_257 | 112 | 0.0030706 | 0.00076957 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1054-32_0_3_load_263 | 113 | 0.0047745 | 0.0011966 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1054-32_0_3_load_265 | 114 | 0.0035733 | 0.00089556 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1054-32_0_3_load_270 | 115 | 0.0028398 | 0.00071173 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 72 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-32_0_3_line_0 |  | 0 | 1 | 0.026022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-32_0_3_line_1 |  | 1 | 2 | 0.011486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-32_0_3_line_2 |  | 2 | 3 | 0.014174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-32_0_3_line_3 |  | 3 | 35 | 0.060549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-32_0_3_line_4 |  | 3 | 30 | 0.040738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-32_0_3_line_5 |  | 3 | 32 | 0.056477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-32_0_3_line_6 |  | 4 | 5 | 0.049401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-32_0_3_line_7 |  | 4 | 6 | 0.036295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-32_0_3_line_8 |  | 4 | 7 | 0.04116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-32_0_3_line_9 |  | 4 | 8 | 0.092319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-32_0_3_line_10 |  | 5 | 9 | 0.011679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-32_0_3_line_11 |  | 5 | 10 | 0.02129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-32_0_3_line_12 |  | 6 | 54 | 0.0079844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-32_0_3_line_13 |  | 8 | 93 | 0.0038874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-32_0_3_line_14 |  | 10 | 88 | 0.0062279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-32_0_3_line_15 |  | 11 | 12 | 0.00069443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-32_0_3_line_16 |  | 11 | 13 | 0.0060958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-32_0_3_line_17 |  | 12 | 14 | 0.026551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-32_0_3_line_18 |  | 13 | 15 | 0.040336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-32_0_3_line_19 |  | 14 | 16 | 0.01064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-32_0_3_line_20 |  | 15 | 42 | 0.031424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-32_0_3_line_21 |  | 16 | 90 | 0.00090906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-32_0_3_line_22 |  | 17 | 18 | 0.0091705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-32_0_3_line_23 |  | 17 | 19 | 0.023749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1054-32_0_3_line_24 |  | 18 | 20 | 0.037081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-32_0_3_line_25 |  | 19 | 21 | 0.011033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-32_0_3_line_26 |  | 19 | 22 | 0.027791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1054-32_0_3_line_27 |  | 20 | 23 | 0.017694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-32_0_3_line_28 |  | 21 | 24 | 0.0098524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-32_0_3_line_29 |  | 21 | 25 | 0.013755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-32_0_3_line_30 |  | 22 | 26 | 0.0055897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1054-32_0_3_line_31 |  | 23 | 43 | 0.011941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-32_0_3_line_32 |  | 23 | 44 | 0.016303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1054-32_0_3_line_33 |  | 23 | 40 | 0.033081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1054-32_0_3_line_34 |  | 24 | 104 | 0.013111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1054-32_0_3_line_35 |  | 25 | 113 | 0.017443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-32_0_3_line_36 |  | 26 | 73 | 0.0050319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1054-32_0_3_line_37 |  | 27 | 28 | 0.050324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1054-32_0_3_line_38 |  | 28 | 29 | 0.03708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1054-32_0_3_line_39 |  | 29 | 32 | 0.018391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1054-32_0_3_line_40 |  | 30 | 31 | 0.028132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-32_0_3_line_41 |  | 31 | 33 | 0.004181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1054-32_0_3_line_42 |  | 31 | 34 | 0.081843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1054-32_0_3_line_43 |  | 33 | 87 | 0.022429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1054-32_0_3_line_44 |  | 34 | 85 | 0.036219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-32_0_3_line_45 |  | 35 | 100 | 0.010959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1054-32_0_3_line_46 |  | 36 | 37 | 0.027664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1054-32_0_3_line_47 |  | 37 | 38 | 0.017316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1054-32_0_3_line_48 |  | 38 | 39 | 0.018538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1054-32_0_3_line_49 |  | 39 | 63 | 0.026849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-32_0_3_line_50 |  | 40 | 41 | 0.0086185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1054-32_0_3_line_51 |  | 41 | 42 | 0.02563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1054-32_0_3_line_52 |  | 43 | 45 | 0.023107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-32_0_3_line_53 |  | 44 | 46 | 0.016513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1054-32_0_3_line_54 |  | 45 | 63 | 0.014285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1054-32_0_3_line_55 |  | 46 | 115 | 0.0037547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-32_0_3_line_56 |  | 47 | 48 | 0.011204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1054-32_0_3_line_57 |  | 47 | 49 | 0.037728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-32_0_3_line_58 |  | 49 | 50 | 0.017813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1054-32_0_3_line_59 |  | 50 | 51 | 0.032569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1054-32_0_3_line_60 |  | 50 | 52 | 0.051637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1054-32_0_3_line_61 |  | 51 | 57 | 0.016854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1054-32_0_3_line_62 |  | 52 | 53 | 0.0095119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1054-32_0_3_line_63 |  | 53 | 112 | 0.010195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1054-32_0_3_line_64 |  | 54 | 70 | 0.0090941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-32_0_3_line_65 |  | 55 | 56 | 0.011992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1054-32_0_3_line_66 |  | 55 | 57 | 0.011476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1054-32_0_3_line_67 |  | 56 | 58 | 0.032014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1054-32_0_3_line_68 |  | 58 | 59 | 0.01471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1054-32_0_3_line_69 |  | 58 | 60 | 0.018709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1054-32_0_3_line_70 |  | 59 | 99 | 0.0057777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1054-32_0_3_line_71 |  | 60 | 92 | 0.012553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-32_0_3_line_72 |  | 61 | 62 | 0.0056538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1054-32_0_3_line_73 |  | 62 | 84 | 0.020069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1054-32_0_3_line_74 |  | 63 | 67 | 0.014247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1054-32_0_3_line_75 |  | 63 | 64 | 0.028556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1054-32_0_3_line_76 |  | 64 | 65 | 0.01349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-32_0_3_line_77 |  | 65 | 66 | 0.0061074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-32_0_3_line_78 |  | 66 | 68 | 0.0040876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-32_0_3_line_79 |  | 67 | 69 | 0.00097587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-32_0_3_line_80 |  | 68 | 111 | 0.0085621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1054-32_0_3_line_81 |  | 69 | 74 | 0.022336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1054-32_0_3_line_82 |  | 70 | 71 | 0.0029409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1054-32_0_3_line_83 |  | 71 | 72 | 0.025227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-32_0_3_line_84 |  | 72 | 73 | 0.02001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1054-32_0_3_line_85 |  | 74 | 75 | 0.004626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1054-32_0_3_line_86 |  | 76 | 77 | 0.01581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-32_0_3_line_87 |  | 76 | 78 | 0.006134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1054-32_0_3_line_88 |  | 76 | 79 | 0.019705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-32_0_3_line_89 |  | 77 | 80 | 0.015796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1054-32_0_3_line_90 |  | 77 | 81 | 0.020978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-32_0_3_line_91 |  | 78 | 82 | 0.0079514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1054-32_0_3_line_92 |  | 78 | 83 | 0.016915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1054-32_0_3_line_93 |  | 79 | 84 | 0.0031101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1054-32_0_3_line_94 |  | 81 | 96 | 0.00039508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1054-32_0_3_line_95 |  | 85 | 86 | 0.081366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1054-32_0_3_line_96 |  | 86 | 103 | 0.004952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1054-32_0_3_line_97 |  | 88 | 89 | 0.0081275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1054-32_0_3_line_98 |  | 91 | 92 | 0.021855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1054-32_0_3_line_99 |  | 93 | 94 | 0.019014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1054-32_0_3_line_100 |  | 94 | 95 | 0.00086555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1054-32_0_3_line_101 |  | 95 | 103 | 0.020521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1054-32_0_3_line_102 |  | 96 | 97 | 0.012949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-32_0_3_line_103 |  | 97 | 98 | 0.0041639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-32_0_3_line_104 |  | 98 | 109 | 0.0043996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1054-32_0_3_line_105 |  | 99 | 105 | 0.026614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1054-32_0_3_line_106 |  | 100 | 101 | 0.023079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1054-32_0_3_line_107 |  | 101 | 102 | 0.034335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1054-32_0_3_line_108 |  | 104 | 105 | 0.016762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1054-32_0_3_line_109 |  | 106 | 107 | 0.0069861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1054-32_0_3_line_110 |  | 106 | 108 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1054-32_0_3_line_111 |  | 107 | 109 | 0.0089251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1054-32_0_3_line_112 |  | 108 | 110 | 0.0062262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1054-32_0_3_line_113 |  | 110 | 111 | 0.0010306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1054-32_0_3_line_114 |  | 113 | 114 | 0.0054282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-32_0_3_trafo_108 | 0.63 MVA 20/0.4 kV | 116 | 72 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2668601.1389 | 1213779.8166 | 2668599.7016 | 1213763.6057 | 2668608.1374 | 1213758.7213
1 | 2668618.0774 | 1213752.966 | 2668608.1374 | 1213758.7213
2 | 2668618.0774 | 1213752.966 | 2668626.2718 | 1213742.5648 | 2668626.9028 | 1213741.8605
3 | 2668626.9028 | 1213741.8605 | 2668633.7444 | 1213744.0517 | 2668684.5451 | 1213760.3966
4 | 2668595.4983 | 1213727.5348 | 2668629.9653 | 1213738.4492 | 2668626.9028 | 1213741.8605
5 | 2668679.4326 | 1213754.1284 | 2668674.5738 | 1213752.5826 | 2668629.9653 | 1213738.4492 | 2668626.9028 | 1213741.8605
6 | 2668401.3988 | 1213918.5476 | 2668393.4782 | 1213919.0459 | 2668388.4672 | 1213918.855 | 2668381.5227 | 1213917.6969 | 2668377.179 | 1213916.2684 | 2668371.2927 | 1213913.5771 | 2668363.7351 | 1213908.9209 | 2668355.9995 | 1213903.2175
7 | 2668401.3988 | 1213918.5476 | 2668401.8984 | 1213921.3439 | 2668411.655 | 1213953.3442
8 | 2668401.3988 | 1213918.5476 | 2668413.4103 | 1213917.6737 | 2668418.5554 | 1213917.4325 | 2668427.58 | 1213918.6924 | 2668434.9856 | 1213920.712 | 2668441.5406 | 1213923.6368
9 | 2668401.3988 | 1213918.5476 | 2668412.8045 | 1213826.9358
10 | 2668355.9995 | 1213903.2175 | 2668346.6026 | 1213896.283
11 | 2668355.9995 | 1213903.2175 | 2668355.3263 | 1213904.2994 | 2668357.3068 | 1213915.7403 | 2668357.1268 | 1213924.1435
12 | 2668413.9836 | 1213960.9815 | 2668411.655 | 1213953.3442
13 | 2668412.8045 | 1213826.9358 | 2668413.3377 | 1213823.0851
14 | 2668362.5025 | 1213926.2694 | 2668359.4818 | 1213926.1051 | 2668357.7596 | 1213925.2626 | 2668357.1268 | 1213924.1435 | 2668357.1268 | 1213924.1435
15 | 2668328.1917 | 1213963.6454 | 2668327.6263 | 1213963.2422
16 | 2668333.1547 | 1213967.1847 | 2668328.1917 | 1213963.6454
17 | 2668306.8099 | 1213946.8084 | 2668317.1671 | 1213955.7833 | 2668327.6263 | 1213963.2422
18 | 2668329.5761 | 1214007.3619 | 2668333.1547 | 1213967.1847
19 | 2668306.8099 | 1213946.8084 | 2668298.7693 | 1213939.8408
20 | 2668329.5761 | 1214007.3619 | 2668353.7209 | 1214027.4749
21 | 2668298.7693 | 1213939.8408 | 2668298.0822 | 1213939.2455
22 | 2668433.3918 | 1214058.3375 | 2668442.5601 | 1214058.5396
23 | 2668453.5126 | 1214045.6583 | 2668453.1873 | 1214058.7739 | 2668442.5601 | 1214058.5396
24 | 2668433.3918 | 1214058.3375 | 2668426.875 | 1214058.1939 | 2668426.818 | 1214063.1519 | 2668416.824 | 1214062.9927 | 2668416.549 | 1214069.0822 | 2668407.8003 | 1214072.8188
25 | 2668453.5126 | 1214045.6583 | 2668458.3445 | 1214045.5693 | 2668463.8171 | 1214042.5969
26 | 2668453.5126 | 1214045.6583 | 2668449.3715 | 1214044.4656 | 2668446.1392 | 1214041.5156 | 2668442.1622 | 1214035.2882 | 2668437.4358 | 1214024.5674
27 | 2668391.5278 | 1214079.7686 | 2668407.8003 | 1214072.8188
28 | 2668463.8171 | 1214042.5969 | 2668467.5534 | 1214044.6522 | 2668473.1317 | 1214044.9827
29 | 2668463.8171 | 1214042.5969 | 2668467.9575 | 1214034.595 | 2668468.6276 | 1214029.8969
30 | 2668437.4358 | 1214024.5674 | 2668435.1809 | 1214019.4526
31 | 2668391.5278 | 1214079.7686 | 2668380.6033 | 1214084.5896
32 | 2668391.5278 | 1214079.7686 | 2668393.8493 | 1214095.9054 | 2668393.8493 | 1214095.9054
33 | 2668391.5278 | 1214079.7686 | 2668390.9967 | 1214073.1028 | 2668389.519 | 1214066.1815 | 2668387.0413 | 1214059.6935 | 2668381.8348 | 1214052.0513 | 2668379.6356 | 1214049.8316
34 | 2668473.1317 | 1214044.9827 | 2668486.2198 | 1214045.7581
35 | 2668470.7248 | 1214012.5843 | 2668469.8906 | 1214021.042 | 2668468.6276 | 1214029.8969
36 | 2668433.151 | 1214014.8484 | 2668435.1809 | 1214019.4526
37 | 2668671.1723 | 1213702.7874 | 2668670.1246 | 1213700.9657 | 2668664.6401 | 1213695.6993 | 2668659.108 | 1213693.9011 | 2668642.0615 | 1213691.3256 | 2668633.1274 | 1213692.7348 | 2668626.3493 | 1213695.5808 | 2668625.1832 | 1213695.5673
38 | 2668671.1723 | 1213702.7874 | 2668683.5589 | 1213724.3239 | 2668685.0043 | 1213731.3894 | 2668683.9154 | 1213736.2934
39 | 2668679.4326 | 1213754.1284 | 2668680.3714 | 1213750.448 | 2668683.3939 | 1213738.6421 | 2668683.9154 | 1213736.2934
40 | 2668595.4983 | 1213727.5348 | 2668568.6073 | 1213719.0203
41 | 2668568.6073 | 1213719.0203 | 2668566.9755 | 1213722.8706
42 | 2668568.6073 | 1213719.0203 | 2668556.9215 | 1213715.317 | 2668497.8082 | 1213694.8584 | 2668491.2653 | 1213692.2854
43 | 2668566.9755 | 1213722.8706 | 2668556.7266 | 1213742.832
44 | 2668491.2653 | 1213692.2854 | 2668483.3258 | 1213727.6237
45 | 2668684.5451 | 1213760.3966 | 2668690.6559 | 1213762.3628 | 2668694.9814 | 1213763.7389
46 | 2668316.0884 | 1214161.01 | 2668316.2005 | 1214157.4318 | 2668315.1058 | 1214147.5686 | 2668313.3067 | 1214138.8648 | 2668311.7244 | 1214133.8354
47 | 2668304.8715 | 1214118.0107 | 2668306.8779 | 1214121.2246 | 2668310.1261 | 1214128.7554 | 2668311.7244 | 1214133.8354
48 | 2668304.8715 | 1214118.0107 | 2668321.831 | 1214110.5262
49 | 2668346.3941 | 1214099.686 | 2668321.831 | 1214110.5262
50 | 2668373.4137 | 1214043.8793 | 2668375.2721 | 1214045.4274 | 2668379.6356 | 1214049.8316
51 | 2668373.4137 | 1214043.8793 | 2668353.7209 | 1214027.4749
52 | 2668359.463 | 1214093.9187 | 2668380.6033 | 1214084.5896
53 | 2668393.8493 | 1214095.9054 | 2668395.5155 | 1214101.6169 | 2668399.5988 | 1214107.1895 | 2668402.3157 | 1214109.6342
54 | 2668346.3941 | 1214099.686 | 2668359.463 | 1214093.9187
55 | 2668405.1068 | 1214112.1457 | 2668402.3157 | 1214109.6342
56 | 2668499.6763 | 1213934.8634 | 2668499.1527 | 1213946.0533
57 | 2668499.6763 | 1213934.8634 | 2668510.4179 | 1213935.4316 | 2668520.9772 | 1213936.6536 | 2668527.2398 | 1213938.3155 | 2668533.583 | 1213940.9011 | 2668536.1576 | 1213942.465
58 | 2668550.2137 | 1213953.1554 | 2668545.4861 | 1213948.1313 | 2668536.1576 | 1213942.465
59 | 2668550.2137 | 1213953.1554 | 2668537.862 | 1213969.0901 | 2668535.408 | 1213975.7439 | 2668534.8174 | 1213981.0273
60 | 2668550.2137 | 1213953.1554 | 2668555.5342 | 1213958.7979 | 2668559.6916 | 1213963.204 | 2668568.9029 | 1213973.3162 | 2668575.737 | 1213979.4431 | 2668586.5073 | 1213985.4262 | 2668589.1726 | 1213984.8343
61 | 2668534.8174 | 1213981.0273 | 2668534.4597 | 1213984.2272 | 2668535.807 | 1213992.5701 | 2668538.2574 | 1213997.1375
62 | 2668589.1726 | 1213984.8343 | 2668598.4455 | 1213986.9533
63 | 2668598.4455 | 1213986.9533 | 2668606.8561 | 1213987.4281 | 2668608.6041 | 1213987.1418
64 | 2668416.6358 | 1213969.6803 | 2668413.9836 | 1213960.9815
65 | 2668543.836 | 1214007.1659 | 2668547.7063 | 1214013.9869 | 2668548.8712 | 1214017.9692
66 | 2668538.2574 | 1213997.1375 | 2668540.1945 | 1214000.7479 | 2668543.836 | 1214007.1659
67 | 2668549.9712 | 1214049.5352 | 2668551.7764 | 1214034.5688 | 2668551.0316 | 1214025.3545 | 2668548.8712 | 1214017.9692
68 | 2668549.9712 | 1214049.5352 | 2668535.2871 | 1214048.6652
69 | 2668549.9712 | 1214049.5352 | 2668551.4036 | 1214052.4535 | 2668563.5309 | 1214062.0391
70 | 2668529.5195 | 1214048.3235 | 2668535.2871 | 1214048.6652
71 | 2668575.3811 | 1214064.7626 | 2668567.5203 | 1214064.4574 | 2668564.8924 | 1214063.1152 | 2668563.5309 | 1214062.0391
72 | 2668277.2828 | 1214076.0703 | 2668275.8005 | 1214073.8168 | 2668274.4359 | 1214071.194
73 | 2668264.9269 | 1214053.533 | 2668266.6294 | 1214056.1897 | 2668274.4359 | 1214071.194
74 | 2668346.3941 | 1214099.686 | 2668351.2531 | 1214113.0788
75 | 2668346.3941 | 1214099.686 | 2668341.3825 | 1214077.6926 | 2668339.545 | 1214071.9817
76 | 2668334.302 | 1214059.6055 | 2668334.657 | 1214060.0934 | 2668337.774 | 1214066.4775 | 2668339.545 | 1214071.9817
77 | 2668334.302 | 1214059.6055 | 2668330.7087 | 1214054.667
78 | 2668327.7405 | 1214051.8565 | 2668330.7087 | 1214054.667 | 2668330.7087 | 1214054.667
79 | 2668351.5859 | 1214113.9962 | 2668351.2531 | 1214113.0788
80 | 2668321.5231 | 1214045.9697 | 2668327.7405 | 1214051.8565
81 | 2668351.5859 | 1214113.9962 | 2668356.8567 | 1214128.5239 | 2668359.2572 | 1214134.9731
82 | 2668417.4935 | 1213972.4933 | 2668416.6358 | 1213969.6803
83 | 2668425.0791 | 1213996.5389 | 2668424.2545 | 1213994.6685 | 2668417.4935 | 1213972.4933
84 | 2668425.0791 | 1213996.5389 | 2668433.151 | 1214014.8484
85 | 2668359.2572 | 1214134.9731 | 2668360.8709 | 1214139.3085
86 | 2668248.9866 | 1214037.4428 | 2668249.7518 | 1214036.2841 | 2668251.4609 | 1214032.3012 | 2668252.069 | 1214027.6163 | 2668251.0203 | 1214022.3566
87 | 2668248.9866 | 1214037.4428 | 2668245.6011 | 1214042.5628
88 | 2668248.9866 | 1214037.4428 | 2668254.4782 | 1214041.4303 | 2668263.2489 | 1214050.9144
89 | 2668251.0203 | 1214022.3566 | 2668246.3234 | 1214009.328 | 2668246.0116 | 1214007.4062
90 | 2668251.0203 | 1214022.3566 | 2668259.668 | 1214020.0319 | 2668271.6801 | 1214019.516
91 | 2668245.6011 | 1214042.5628 | 2668239.2532 | 1214037.7743
92 | 2668245.6011 | 1214042.5628 | 2668253.1249 | 1214050.1647 | 2668256.8011 | 1214055.1811
93 | 2668264.9269 | 1214053.533 | 2668263.2489 | 1214050.9144 | 2668263.2489 | 1214050.9144
94 | 2668272.0749 | 1214019.4991 | 2668271.6801 | 1214019.516
95 | 2668483.3258 | 1213727.6237 | 2668419.558 | 1213778.1612
96 | 2668418.8788 | 1213783.0664 | 2668419.558 | 1213778.1612
97 | 2668370.618 | 1213926.7109 | 2668362.5025 | 1213926.2694
98 | 2668575.3811 | 1214064.7626 | 2668586.6452 | 1214065.2 | 2668588.3143 | 1214066.0308 | 2668596.9858 | 1214066.9311
99 | 2668415.9455 | 1213804.251 | 2668413.3377 | 1213823.0851
100 | 2668416.0642 | 1213803.3937 | 2668415.9455 | 1213804.251
101 | 2668418.8788 | 1213783.0664 | 2668416.0642 | 1213803.3937
102 | 2668272.0749 | 1214019.4991 | 2668285.0122 | 1214018.9435 | 2668285.0122 | 1214018.9435
103 | 2668289.1633 | 1214019.269 | 2668289.1633 | 1214019.269 | 2668285.0122 | 1214018.9435
104 | 2668293.3948 | 1214020.4736 | 2668289.1633 | 1214019.269
105 | 2668529.5195 | 1214048.3235 | 2668502.9521 | 1214046.7495
106 | 2668716.9705 | 1213770.7486 | 2668705.0508 | 1213766.9425 | 2668694.9814 | 1213763.7389
107 | 2668716.9705 | 1213770.7486 | 2668738.3205 | 1213777.5658 | 2668749.5704 | 1213781.5138
108 | 2668486.2198 | 1214045.7581 | 2668502.9521 | 1214046.7495
109 | 2668305.4594 | 1214030.7599 | 2668300.3865 | 1214025.9567
110 | 2668305.4594 | 1214030.7599 | 2668316.2536 | 1214040.9804
111 | 2668293.3948 | 1214020.4736 | 2668293.7211 | 1214020.5665 | 2668298.2475 | 1214023.9315 | 2668300.3865 | 1214025.9567
112 | 2668316.2536 | 1214040.9804 | 2668320.7747 | 1214045.2611
113 | 2668321.5231 | 1214045.9697 | 2668320.7747 | 1214045.2611
114 | 2668471.2575 | 1214007.1824 | 2668470.7248 | 1214012.5843

## bus_geodata
| x | y | coords
0 | 2668601.1389 | 1213779.8166
1 | 2668608.1374 | 1213758.7213
2 | 2668618.0774 | 1213752.966
3 | 2668626.9028 | 1213741.8605
4 | 2668401.3988 | 1213918.5476
5 | 2668355.9995 | 1213903.2175
6 | 2668411.655 | 1213953.3442
7 | 2668441.5406 | 1213923.6368
8 | 2668412.8045 | 1213826.9358
9 | 2668346.6026 | 1213896.283
10 | 2668357.1268 | 1213924.1435
11 | 2668328.1917 | 1213963.6454
12 | 2668327.6263 | 1213963.2422
13 | 2668333.1547 | 1213967.1847
14 | 2668306.8099 | 1213946.8084
15 | 2668329.5761 | 1214007.3619
16 | 2668298.7693 | 1213939.8408
17 | 2668442.5601 | 1214058.5396
18 | 2668433.3918 | 1214058.3375
19 | 2668453.5126 | 1214045.6583
20 | 2668407.8003 | 1214072.8188
21 | 2668463.8171 | 1214042.5969
22 | 2668437.4358 | 1214024.5674
23 | 2668391.5278 | 1214079.7686
24 | 2668473.1317 | 1214044.9827
25 | 2668468.6276 | 1214029.8969
26 | 2668435.1809 | 1214019.4526
27 | 2668625.1832 | 1213695.5673
28 | 2668671.1723 | 1213702.7874
29 | 2668683.9154 | 1213736.2934
30 | 2668595.4983 | 1213727.5348
31 | 2668568.6073 | 1213719.0203
32 | 2668679.4326 | 1213754.1284
33 | 2668566.9755 | 1213722.8706
34 | 2668491.2653 | 1213692.2854
35 | 2668684.5451 | 1213760.3966
36 | 2668316.0884 | 1214161.01
37 | 2668311.7244 | 1214133.8354
38 | 2668304.8715 | 1214118.0107
39 | 2668321.831 | 1214110.5262
40 | 2668379.6356 | 1214049.8316
41 | 2668373.4137 | 1214043.8793
42 | 2668353.7209 | 1214027.4749
43 | 2668380.6033 | 1214084.5896
44 | 2668393.8493 | 1214095.9054
45 | 2668359.463 | 1214093.9187
46 | 2668402.3157 | 1214109.6342
47 | 2668499.6763 | 1213934.8634
48 | 2668499.1527 | 1213946.0533
49 | 2668536.1576 | 1213942.465
50 | 2668550.2137 | 1213953.1554
51 | 2668534.8174 | 1213981.0273
52 | 2668589.1726 | 1213984.8343
53 | 2668598.4455 | 1213986.9533
54 | 2668413.9836 | 1213960.9815
55 | 2668543.836 | 1214007.1659
56 | 2668548.8712 | 1214017.9692
57 | 2668538.2574 | 1213997.1375
58 | 2668549.9712 | 1214049.5352
59 | 2668535.2871 | 1214048.6652
60 | 2668563.5309 | 1214062.0391
61 | 2668277.2828 | 1214076.0703
62 | 2668274.4359 | 1214071.194
63 | 2668346.3941 | 1214099.686
64 | 2668339.545 | 1214071.9817
65 | 2668334.302 | 1214059.6055
66 | 2668330.7087 | 1214054.667
67 | 2668351.2531 | 1214113.0788
68 | 2668327.7405 | 1214051.8566
69 | 2668351.5859 | 1214113.9962
70 | 2668416.6358 | 1213969.6803
71 | 2668417.4935 | 1213972.4933
72 | 2668425.0791 | 1213996.5389
73 | 2668433.151 | 1214014.8484
74 | 2668359.2572 | 1214134.9731
75 | 2668360.8709 | 1214139.3085
76 | 2668248.9866 | 1214037.4428
77 | 2668251.0203 | 1214022.3566
78 | 2668245.6011 | 1214042.5628
79 | 2668263.2489 | 1214050.9144
80 | 2668246.0116 | 1214007.4062
81 | 2668271.6801 | 1214019.516
82 | 2668239.2532 | 1214037.7743
83 | 2668256.8011 | 1214055.1811
84 | 2668264.9269 | 1214053.533
85 | 2668483.3258 | 1213727.6237
86 | 2668419.558 | 1213778.1612
87 | 2668556.7266 | 1213742.832
88 | 2668362.5025 | 1213926.2694
89 | 2668370.618 | 1213926.7109
90 | 2668298.0822 | 1213939.2455
91 | 2668596.9858 | 1214066.9311
92 | 2668575.3811 | 1214064.7626
93 | 2668413.3377 | 1213823.0851
94 | 2668415.9455 | 1213804.251
95 | 2668416.0642 | 1213803.3937
96 | 2668272.0749 | 1214019.4991
97 | 2668285.0122 | 1214018.9435
98 | 2668289.1633 | 1214019.269
99 | 2668529.5195 | 1214048.3235
100 | 2668694.9814 | 1213763.7389
101 | 2668716.9705 | 1213770.7486
102 | 2668749.5704 | 1213781.5138
103 | 2668418.8788 | 1213783.0664
104 | 2668486.2198 | 1214045.7581
105 | 2668502.9521 | 1214046.7495
106 | 2668305.4594 | 1214030.7599
107 | 2668300.3865 | 1214025.9567
108 | 2668316.2536 | 1214040.9804
109 | 2668293.3948 | 1214020.4736
110 | 2668320.7748 | 1214045.2611
111 | 2668321.5231 | 1214045.9697
112 | 2668608.6041 | 1213987.1418
113 | 2668470.7248 | 1214012.5843
114 | 2668471.2575 | 1214007.1824
115 | 2668405.1068 | 1214112.1457
116 | 2668453.5126 | 1214045.6583

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98431 | -0.30196 | 0.0010631 | 0.00026643
1 | 0.98434 | -0.30146 | 0.00097689 | 0.00024483
2 | 0.98436 | -0.30104 | 0 | 0
3 | 0.98439 | -0.30052 | 0 | 0
4 | 0.9961 | -0.074325 | 0 | 0
5 | 0.99571 | -0.08198 | 0 | 0
6 | 0.99772 | -0.043408 | 0.003006 | 0.00075338
7 | 0.99604 | -0.075479 | 0.0015964 | 0.0004001
8 | 0.99286 | -0.13639 | 0.0037648 | 0.00094354
9 | 0.99569 | -0.0824 | 0.0020448 | 0.00051247
10 | 0.99558 | -0.084515 | 0.0020442 | 0.00051232
11 | 0.98256 | -0.33493 | 0.0023537 | 0.0005899
12 | 0.98256 | -0.33504 | 0.0030029 | 0.00075259
13 | 0.98263 | -0.3337 | 0.0029682 | 0.0007439
14 | 0.98242 | -0.33783 | 0.0017422 | 0.00043664
15 | 0.98315 | -0.3234 | 0.0024043 | 0.00060259
16 | 0.98238 | -0.33861 | 0.002074 | 0.00051979
17 | 0.99267 | -0.13949 | 0.0039435 | 0.00098833
18 | 0.99151 | -0.16171 | 0.0074032 | 0.0018554
19 | 0.99422 | -0.10998 | 0 | 0
20 | 0.98707 | -0.24717 | 0.0035651 | 0.0008935
21 | 0.99352 | -0.12342 | 0 | 0
22 | 0.99691 | -0.058701 | 0.0030204 | 0.00075697
23 | 0.98501 | -0.28709 | 0 | 0
24 | 0.99301 | -0.13335 | 0.0053131 | 0.0013316
25 | 0.99337 | -0.12634 | 0.0036758 | 0.00092125
26 | 0.99745 | -0.048273 | 0.0051289 | 0.0012854
27 | 0.98316 | -0.32453 | 0.0039039 | 0.0009784
28 | 0.98334 | -0.32099 | 0.0051018 | 0.0012786
29 | 0.98365 | -0.31497 | 0.0017155 | 0.00042995
30 | 0.98536 | -0.28155 | 0 | 0
31 | 0.98603 | -0.26848 | 0 | 0
32 | 0.98383 | -0.31142 | 0 | 0
33 | 0.98602 | -0.26861 | 0 | 0
34 | 0.98812 | -0.22791 | 0.0019347 | 0.00048488
35 | 0.98365 | -0.31483 | 0.0063233 | 0.0015848
36 | 0.98109 | -0.36347 | 0.0016094 | 0.00040336
37 | 0.98113 | -0.36267 | 0.0028438 | 0.00071272
38 | 0.9812 | -0.36127 | 0 | 0
39 | 0.98128 | -0.35978 | 0.007908 | 0.0019819
40 | 0.98426 | -0.30184 | 0.0024767 | 0.00062072
41 | 0.98408 | -0.3053 | 0.0034106 | 0.00085477
42 | 0.98363 | -0.31403 | 0.0023622 | 0.00059203
43 | 0.98416 | -0.30371 | 0.0024254 | 0.00060785
44 | 0.98466 | -0.29401 | 0.0041114 | 0.0010304
45 | 0.98255 | -0.33495 | 0.0020933 | 0.00052463
46 | 0.98436 | -0.2998 | 0.016665 | 0.0041767
47 | 0.98797 | -0.23089 | 0 | 0
48 | 0.98795 | -0.23141 | 0.0025801 | 0.00064663
49 | 0.98806 | -0.22916 | 0.0018087 | 0.0004533
50 | 0.98813 | -0.22776 | 0 | 0
51 | 0.98849 | -0.22084 | 0.0031929 | 0.00080022
52 | 0.98778 | -0.23468 | 0 | 0
53 | 0.98771 | -0.23596 | 0.0044334 | 0.0011111
54 | 0.9981 | -0.036201 | 0.0026414 | 0.000662
55 | 0.9889 | -0.2128 | 0.0048525 | 0.0012161
56 | 0.98915 | -0.2081 | 0.0037305 | 0.00093494
57 | 0.98872 | -0.21631 | 0.0020664 | 0.0005179
58 | 0.9899 | -0.19343 | 0 | 0
59 | 0.99039 | -0.18403 | 0.0036966 | 0.00092644
60 | 0.98973 | -0.19682 | 0.003654 | 0.00091578
61 | 0.97578 | -0.46763 | 0.0023722 | 0.00059454
62 | 0.97579 | -0.46739 | 0.002375 | 0.00059524
63 | 0.98159 | -0.35377 | 0 | 0
64 | 0.98018 | -0.38129 | 0.0021019 | 0.00052679
65 | 0.97954 | -0.39381 | 0.0018764 | 0.00047028
66 | 0.97926 | -0.39927 | 0.0016647 | 0.00041722
67 | 0.98149 | -0.35566 | 0.0019482 | 0.00048827
68 | 0.97908 | -0.4028 | 0.0033281 | 0.0008341
69 | 0.98148 | -0.35576 | 0.0022711 | 0.00056919
70 | 0.99855 | -0.027578 | 0.00098776 | 0.00024756
71 | 0.9987 | -0.024741 | 0.00098809 | 0.00024764
72 | 1 | 0 | -0.28268 | -0.071807
73 | 0.99796 | -0.03867 | 0.0033187 | 0.00083174
74 | 0.98142 | -0.35702 | 0.0018483 | 0.00046322
75 | 0.98141 | -0.35712 | 0.0012699 | 0.00031826
76 | 0.97606 | -0.46206 | 0 | 0
77 | 0.97635 | -0.45627 | 0 | 0
78 | 0.976 | -0.46331 | 0 | 0
79 | 0.9759 | -0.46525 | 0.0020597 | 0.00051621
80 | 0.97632 | -0.45698 | 0.0024431 | 0.0006123
81 | 0.97679 | -0.44766 | 0.0020565 | 0.0005154
82 | 0.97594 | -0.46452 | 0.0083326 | 0.0020883
83 | 0.97595 | -0.46418 | 0.0028135 | 0.00070513
84 | 0.97588 | -0.46564 | 0.0020568 | 0.00051549
85 | 0.98911 | -0.20877 | 0.00072824 | 0.00018251
86 | 0.99138 | -0.16484 | 0.00066373 | 0.00016635
87 | 0.98599 | -0.26934 | 0.0017967 | 0.00045031
88 | 0.99555 | -0.085033 | 0.0020316 | 0.00050916
89 | 0.99553 | -0.085418 | 0.0026956 | 0.00067557
90 | 0.98237 | -0.33864 | 0.0020009 | 0.00050146
91 | 0.9896 | -0.19922 | 0.0024415 | 0.00061189
92 | 0.98965 | -0.19827 | 0.0040894 | 0.0010249
93 | 0.99274 | -0.13876 | 0.00074781 | 0.00018742
94 | 0.99215 | -0.15008 | 0.0012268 | 0.00030745
95 | 0.99213 | -0.15057 | 0.00066383 | 0.00016637
96 | 0.9768 | -0.44748 | 0.0027692 | 0.00069403
97 | 0.97713 | -0.44103 | 0.0032273 | 0.00080885
98 | 0.97725 | -0.43871 | 0.0025858 | 0.00064805
99 | 0.9906 | -0.17996 | 0.0043582 | 0.0010923
100 | 0.98358 | -0.31618 | 0.00084318 | 0.00021132
101 | 0.98346 | -0.31866 | 0.0026992 | 0.00067649
102 | 0.98335 | -0.32068 | 0.0032678 | 0.00081899
103 | 0.99153 | -0.16211 | 0.00070533 | 0.00017677
104 | 0.99238 | -0.14535 | 0.0051081 | 0.0012802
105 | 0.99167 | -0.15919 | 0.0026408 | 0.00066184
106 | 0.97792 | -0.42558 | 0.0017575 | 0.00044046
107 | 0.97768 | -0.4303 | 0.00164 | 0.00041103
108 | 0.97845 | -0.41508 | 0.001788 | 0.00044812
109 | 0.97738 | -0.43606 | 0.0022837 | 0.00057236
110 | 0.97868 | -0.41048 | 0.0017336 | 0.00043449
111 | 0.97873 | -0.40969 | 0.0019291 | 0.00048347
112 | 0.98768 | -0.23651 | 0.0030706 | 0.00076957
113 | 0.99324 | -0.12892 | 0.0047745 | 0.0011966
114 | 0.99322 | -0.12926 | 0.0035733 | 0.00089556
115 | 0.98435 | -0.29999 | 0.0028398 | 0.00071173
116 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010631 | -0.00026643 | 0.0010631 | 0.00026611 | 2.52e-08 | -3.1465e-07 | 0.0016071 | 0.0016069 | 0.0016071 | 0.98431 | -0.30196 | 0.98434 | -0.30146 | 0.4415
1 | -0.00204 | -0.00051094 | 0.00204 | 0.00051082 | 4.0958e-08 | -1.1979e-07 | 0.0030837 | 0.0030836 | 0.0030837 | 0.98434 | -0.30146 | 0.98436 | -0.30104 | 0.84717
2 | -0.00204 | -0.00051082 | 0.0020401 | 0.00051068 | 5.0541e-08 | -1.4784e-07 | 0.0030836 | 0.0030836 | 0.0030836 | 0.98436 | -0.30104 | 0.98439 | -0.30052 | 0.84715
3 | 0.013144 | 0.0032966 | -0.013135 | -0.0032916 | 8.9643e-06 | 4.968e-06 | 0.019869 | 0.01987 | 0.01987 | 0.98439 | -0.30052 | 0.98365 | -0.31483 | 5.4587
4 | -0.025916 | -0.006499 | 0.025939 | 0.0065135 | 2.3446e-05 | 1.4487e-05 | 0.039176 | 0.039176 | 0.039176 | 0.98439 | -0.30052 | 0.98536 | -0.28155 | 10.7627
5 | 0.010732 | 0.0026917 | -0.010726 | -0.0026889 | 5.5742e-06 | 2.8499e-06 | 0.016223 | 0.016223 | 0.016223 | 0.98439 | -0.30052 | 0.98383 | -0.31142 | 4.457
6 | 0.0088203 | 0.002211 | -0.0088171 | -0.0022096 | 3.2163e-06 | 1.4156e-06 | 0.013176 | 0.013177 | 0.013177 | 0.9961 | -0.074325 | 0.99571 | -0.08198 | 3.6199
7 | -0.048909 | -0.01239 | 0.048982 | 0.012436 | 7.2748e-05 | 4.6086e-05 | 0.073109 | 0.073109 | 0.073109 | 0.9961 | -0.074325 | 0.99772 | -0.043408 | 20.0849
8 | 0.0015965 | 0.00039962 | -0.0015964 | -0.0004001 | 8.7785e-08 | -4.7958e-07 | 0.0023847 | 0.0023849 | 0.0023849 | 0.9961 | -0.074325 | 0.99604 | -0.075479 | 0.6552
9 | 0.038492 | 0.0097795 | -0.038378 | -0.0097074 | 0.00011465 | 7.2181e-05 | 0.057548 | 0.057549 | 0.057549 | 0.9961 | -0.074325 | 0.99286 | -0.13639 | 15.81
10 | 0.0020448 | 0.00051234 | -0.0020448 | -0.00051247 | 4.0895e-08 | -1.2573e-07 | 0.0030558 | 0.0030558 | 0.0030558 | 0.99571 | -0.08198 | 0.99569 | -0.0824 | 0.83952
11 | 0.0067723 | 0.0016972 | -0.0067715 | -0.001697 | 8.178e-07 | 2.465e-07 | 0.010121 | 0.010121 | 0.010121 | 0.99571 | -0.08198 | 0.99558 | -0.084515 | 2.7805
12 | -0.051988 | -0.01319 | 0.052006 | 0.013201 | 1.8026e-05 | 1.1433e-05 | 0.077592 | 0.077592 | 0.077592 | 0.99772 | -0.043408 | 0.9981 | -0.036201 | 21.3165
13 | 0.034613 | 0.0087638 | -0.034609 | -0.0087614 | 3.9276e-06 | 2.4634e-06 | 0.051906 | 0.051906 | 0.051906 | 0.99286 | -0.13639 | 0.99274 | -0.13876 | 14.26
14 | 0.0047273 | 0.0011847 | -0.0047272 | -0.0011847 | 1.1659e-07 | -6.3641e-09 | 0.0070655 | 0.0070656 | 0.0070656 | 0.99558 | -0.084515 | 0.99555 | -0.085033 | 1.9411
15 | 0.0088209 | 0.0022106 | -0.0088208 | -0.0022106 | 4.6471e-08 | 2.0946e-08 | 0.013359 | 0.013359 | 0.013359 | 0.98256 | -0.33493 | 0.98256 | -0.33504 | 3.6699
16 | -0.011175 | -0.0028005 | 0.011175 | 0.0028009 | 6.5466e-07 | 3.4177e-07 | 0.016923 | 0.016923 | 0.016923 | 0.98256 | -0.33493 | 0.98263 | -0.3337 | 4.6492
17 | 0.005818 | 0.001458 | -0.0058172 | -0.0014578 | 7.7296e-07 | 1.5846e-07 | 0.0088109 | 0.008811 | 0.008811 | 0.98256 | -0.33504 | 0.98242 | -0.33783 | 2.4206
18 | -0.014143 | -0.0035448 | 0.01415 | 0.0035487 | 6.9387e-06 | 3.9295e-06 | 0.021418 | 0.021418 | 0.021418 | 0.98263 | -0.3337 | 0.98315 | -0.3234 | 5.884
19 | 0.004075 | 0.0010212 | -0.0040748 | -0.0010212 | 1.5199e-07 | -3.7435e-08 | 0.0061721 | 0.0061722 | 0.0061722 | 0.98242 | -0.33783 | 0.98238 | -0.33861 | 1.6957
20 | -0.016555 | -0.0041513 | 0.016562 | 0.0041556 | 7.3985e-06 | 4.3364e-06 | 0.025057 | 0.025057 | 0.025057 | 0.98315 | -0.3234 | 0.98363 | -0.31403 | 6.8837
21 | 0.0020009 | 0.00050145 | -0.0020009 | -0.00050146 | 3.1314e-09 | -9.5054e-09 | 0.0030307 | 0.0030307 | 0.0030307 | 0.98238 | -0.33861 | 0.98237 | -0.33864 | 0.83262
22 | 0.13824 | 0.035201 | -0.13809 | -0.035107 | 0.00014795 | 9.4573e-05 | 0.20742 | 0.20742 | 0.20742 | 0.99267 | -0.13949 | 0.99151 | -0.16171 | 56.9836
23 | -0.14218 | -0.03619 | 0.14239 | 0.036319 | 0.00020266 | 0.00012909 | 0.21333 | 0.21333 | 0.21333 | 0.99267 | -0.13949 | 0.99422 | -0.10998 | 29.3038
24 | 0.13069 | 0.033251 | -0.13015 | -0.032909 | 0.00053588 | 0.00034249 | 0.19631 | 0.19631 | 0.19631 | 0.99151 | -0.16171 | 0.98707 | -0.24717 | 53.9314
25 | 0.069302 | 0.017457 | -0.069257 | -0.017429 | 4.4538e-05 | 2.8361e-05 | 0.10375 | 0.10375 | 0.10375 | 0.99422 | -0.10998 | 0.99352 | -0.12342 | 28.5036
26 | -0.21169 | -0.053776 | 0.21221 | 0.05411 | 0.00052391 | 0.00033458 | 0.31708 | 0.31708 | 0.31708 | 0.99422 | -0.10998 | 0.99691 | -0.058701 | 43.5555
27 | 0.12659 | 0.032015 | -0.12635 | -0.031861 | 0.0002419 | 0.00015459 | 0.19094 | 0.19094 | 0.19094 | 0.98707 | -0.24717 | 0.98501 | -0.28709 | 52.455
28 | 0.057231 | 0.014414 | -0.057204 | -0.014397 | 2.7161e-05 | 1.7256e-05 | 0.085741 | 0.085741 | 0.085741 | 0.99352 | -0.12342 | 0.99301 | -0.13335 | 23.5552
29 | 0.012026 | 0.0030147 | -0.012025 | -0.0030138 | 1.6736e-06 | 8.9298e-07 | 0.018012 | 0.018012 | 0.018012 | 0.99352 | -0.12342 | 0.99337 | -0.12634 | 4.9485
30 | -0.21523 | -0.054867 | 0.21534 | 0.054937 | 0.00010839 | 6.9226e-05 | 0.32159 | 0.32159 | 0.32159 | 0.99691 | -0.058701 | 0.99745 | -0.048273 | 44.1748
31 | 0.077876 | 0.019693 | -0.077814 | -0.019653 | 6.2041e-05 | 3.9554e-05 | 0.11771 | 0.11771 | 0.11771 | 0.98501 | -0.28709 | 0.98416 | -0.30371 | 32.3371
32 | 0.02363 | 0.0059268 | -0.023622 | -0.005922 | 7.7908e-06 | 4.7787e-06 | 0.035698 | 0.035698 | 0.035698 | 0.98501 | -0.28709 | 0.98466 | -0.29401 | 9.8071
33 | 0.024841 | 0.0062409 | -0.024823 | -0.0062301 | 1.7474e-05 | 1.0763e-05 | 0.037531 | 0.037531 | 0.037531 | 0.98501 | -0.28709 | 0.98426 | -0.30184 | 10.3108
34 | 0.051891 | 0.013065 | -0.051861 | -0.013046 | 2.9744e-05 | 1.8867e-05 | 0.077779 | 0.077779 | 0.077779 | 0.99301 | -0.13335 | 0.99238 | -0.14535 | 21.3679
35 | 0.0083489 | 0.0020926 | -0.0083479 | -0.0020921 | 1.0231e-06 | 4.2899e-07 | 0.012506 | 0.012506 | 0.012506 | 0.99337 | -0.12634 | 0.99324 | -0.12892 | 3.4358
36 | -0.22047 | -0.056222 | 0.22057 | 0.056287 | 0.00010227 | 6.5324e-05 | 0.32924 | 0.32924 | 0.32924 | 0.99745 | -0.048273 | 0.99796 | -0.03867 | 45.2258
37 | -0.0039039 | -0.0009784 | 0.0039045 | 0.00097818 | 6.5879e-07 | -2.1665e-07 | 0.0059085 | 0.0059083 | 0.0059085 | 0.98316 | -0.32453 | 0.98334 | -0.32099 | 1.6232
38 | -0.0090063 | -0.0022568 | 0.0090089 | 0.002258 | 2.5826e-06 | 1.1823e-06 | 0.013628 | 0.013628 | 0.013628 | 0.98334 | -0.32099 | 0.98365 | -0.31497 | 3.7441
39 | -0.010724 | -0.0026879 | 0.010726 | 0.0026889 | 1.8152e-06 | 9.2822e-07 | 0.016223 | 0.016223 | 0.016223 | 0.98365 | -0.31497 | 0.98383 | -0.31142 | 4.457
40 | -0.025939 | -0.0065135 | 0.025955 | 0.0065235 | 1.6191e-05 | 1.0004e-05 | 0.039176 | 0.039176 | 0.039176 | 0.98536 | -0.28155 | 0.98603 | -0.26848 | 10.7626
41 | 0.0017968 | 0.00045001 | -0.0017968 | -0.00045006 | 1.1527e-08 | -4.5952e-08 | 0.0027115 | 0.0027115 | 0.0027115 | 0.98603 | -0.26848 | 0.98602 | -0.26861 | 0.74491
42 | -0.027752 | -0.0069735 | 0.027806 | 0.0070069 | 5.3848e-05 | 3.3417e-05 | 0.041887 | 0.041887 | 0.041887 | 0.98603 | -0.26848 | 0.98812 | -0.22791 | 11.5075
43 | 0.0017968 | 0.00045006 | -0.0017967 | -0.00045031 | 6.184e-08 | -2.465e-07 | 0.0027115 | 0.0027116 | 0.0027116 | 0.98602 | -0.26861 | 0.98599 | -0.26934 | 0.74494
44 | -0.029741 | -0.0074918 | 0.029768 | 0.0075088 | 2.726e-05 | 1.6982e-05 | 0.0448 | 0.0448 | 0.0448 | 0.98812 | -0.22791 | 0.98911 | -0.20877 | 12.3078
45 | 0.0068117 | 0.0017069 | -0.0068112 | -0.0017067 | 4.3633e-07 | 1.4015e-07 | 0.010304 | 0.010304 | 0.010304 | 0.98365 | -0.31483 | 0.98358 | -0.31618 | 2.8308
46 | -0.0016094 | -0.00040336 | 0.0016095 | 0.00040305 | 6.1809e-08 | -3.0979e-07 | 0.002441 | 0.0024409 | 0.002441 | 0.98109 | -0.36347 | 0.98113 | -0.36267 | 0.6706
47 | -0.0044533 | -0.0011158 | 0.0044536 | 0.0011157 | 2.9619e-07 | -2.9132e-08 | 0.0067539 | 0.0067538 | 0.0067539 | 0.98113 | -0.36267 | 0.9812 | -0.36127 | 1.8555
48 | -0.0044536 | -0.0011157 | 0.0044539 | 0.0011157 | 3.1708e-07 | -3.1228e-08 | 0.0067538 | 0.0067537 | 0.0067538 | 0.9812 | -0.36127 | 0.98128 | -0.35978 | 1.8554
49 | -0.012362 | -0.0030976 | 0.012365 | 0.0030996 | 3.5379e-06 | 1.925e-06 | 0.018745 | 0.018745 | 0.018745 | 0.98128 | -0.35978 | 0.98159 | -0.35377 | 5.1498
50 | 0.022347 | 0.0056094 | -0.022343 | -0.0056071 | 3.6894e-06 | 2.2517e-06 | 0.033787 | 0.033787 | 0.033787 | 0.98426 | -0.30184 | 0.98408 | -0.3053 | 9.2821
51 | 0.018932 | 0.0047524 | -0.018924 | -0.0047476 | 7.8782e-06 | 4.7166e-06 | 0.02863 | 0.02863 | 0.02863 | 0.98408 | -0.3053 | 0.98363 | -0.31403 | 7.8654
52 | 0.075389 | 0.019046 | -0.075276 | -0.018974 | 0.00011269 | 7.183e-05 | 0.11404 | 0.11404 | 0.11404 | 0.98416 | -0.30371 | 0.98255 | -0.33495 | 31.3297
53 | 0.01951 | 0.0048916 | -0.019505 | -0.0048884 | 5.3834e-06 | 3.2354e-06 | 0.029485 | 0.029485 | 0.029485 | 0.98466 | -0.29401 | 0.98436 | -0.2998 | 8.1003
54 | 0.073183 | 0.018449 | -0.073117 | -0.018407 | 6.5847e-05 | 4.1962e-05 | 0.11087 | 0.11087 | 0.11087 | 0.98255 | -0.33495 | 0.98159 | -0.35377 | 30.4588
55 | 0.0028399 | 0.0007117 | -0.0028398 | -0.00071173 | 2.5948e-08 | -3.1123e-08 | 0.0042929 | 0.0042929 | 0.0042929 | 0.98436 | -0.2998 | 0.98435 | -0.29999 | 1.1794
56 | 0.0025801 | 0.00064653 | -0.0025801 | -0.00064663 | 6.3447e-08 | -1.0286e-07 | 0.003886 | 0.003886 | 0.003886 | 0.98797 | -0.23089 | 0.98795 | -0.23141 | 1.0676
57 | -0.0025801 | -0.00064653 | 0.0025804 | 0.00064618 | 2.1364e-07 | -3.4645e-07 | 0.003886 | 0.0038858 | 0.003886 | 0.98797 | -0.23089 | 0.98806 | -0.22916 | 1.0676
58 | -0.0043891 | -0.0010995 | 0.0043894 | 0.0010994 | 2.9183e-07 | -4.1394e-08 | 0.0066097 | 0.0066096 | 0.0066097 | 0.98806 | -0.22916 | 0.98813 | -0.22776 | 1.8159
59 | -0.011896 | -0.0029812 | 0.0119 | 0.0029832 | 3.9197e-06 | 2.0912e-06 | 0.017915 | 0.017914 | 0.017915 | 0.98813 | -0.22776 | 0.98849 | -0.22084 | 4.9216
60 | 0.0075071 | 0.0018817 | -0.0075046 | -0.0018808 | 2.4748e-06 | 9.2263e-07 | 0.011305 | 0.011305 | 0.011305 | 0.98813 | -0.22776 | 0.98778 | -0.23468 | 3.1058
61 | -0.015093 | -0.0037835 | 0.015097 | 0.0037853 | 3.2627e-06 | 1.8721e-06 | 0.022721 | 0.022721 | 0.022721 | 0.98849 | -0.22084 | 0.98872 | -0.21631 | 6.242
62 | 0.0075046 | 0.0018808 | -0.0075042 | -0.0018806 | 4.5588e-07 | 1.7001e-07 | 0.011305 | 0.011305 | 0.011305 | 0.98778 | -0.23468 | 0.98771 | -0.23596 | 3.1058
63 | 0.0030707 | 0.00076949 | -0.0030706 | -0.00076957 | 8.182e-08 | -7.8119e-08 | 0.0046261 | 0.0046261 | 0.0046261 | 0.98771 | -0.23596 | 0.98768 | -0.23651 | 1.2709
64 | -0.054647 | -0.013863 | 0.05467 | 0.013877 | 2.2669e-05 | 1.4389e-05 | 0.08153 | 0.08153 | 0.08153 | 0.9981 | -0.036201 | 0.99855 | -0.027578 | 22.3983
65 | -0.022018 | -0.0055211 | 0.022023 | 0.0055241 | 4.9365e-06 | 3.0054e-06 | 0.033132 | 0.033132 | 0.033132 | 0.9889 | -0.2128 | 0.98915 | -0.2081 | 9.1023
66 | 0.017166 | 0.0043049 | -0.017163 | -0.0043032 | 2.8715e-06 | 1.6905e-06 | 0.025831 | 0.025831 | 0.025831 | 0.9889 | -0.2128 | 0.98872 | -0.21631 | 7.0963
67 | -0.025754 | -0.006459 | 0.025772 | 0.0064701 | 1.8021e-05 | 1.1122e-05 | 0.038744 | 0.038744 | 0.038744 | 0.98915 | -0.2081 | 0.9899 | -0.19343 | 10.644
68 | -0.035959 | -0.0090234 | 0.035975 | 0.0090336 | 1.6119e-05 | 1.0127e-05 | 0.054057 | 0.054057 | 0.054057 | 0.9899 | -0.19343 | 0.99039 | -0.18403 | 14.8509
69 | 0.010187 | 0.0025533 | -0.010185 | -0.0025525 | 1.6452e-06 | 8.1245e-07 | 0.015313 | 0.015313 | 0.015313 | 0.9899 | -0.19343 | 0.98973 | -0.19682 | 4.2069
70 | -0.039671 | -0.00996 | 0.039679 | 0.0099649 | 7.6991e-06 | 4.853e-06 | 0.059611 | 0.059611 | 0.059611 | 0.99039 | -0.18403 | 0.9906 | -0.17996 | 16.3767
71 | 0.0065314 | 0.0016367 | -0.0065309 | -0.0016366 | 4.5391e-07 | 1.292e-07 | 0.0098196 | 0.0098197 | 0.0098197 | 0.98973 | -0.19682 | 0.98965 | -0.19827 | 2.6977
72 | -0.0023722 | -0.00059454 | 0.0023723 | 0.00059448 | 2.7746e-08 | -5.2868e-08 | 0.0036175 | 0.0036175 | 0.0036175 | 0.97578 | -0.46763 | 0.97579 | -0.46739 | 0.99383
73 | -0.0047473 | -0.0011897 | 0.0047477 | 0.0011897 | 3.9441e-07 | 1.6999e-09 | 0.0072393 | 0.0072392 | 0.0072393 | 0.97579 | -0.46739 | 0.97588 | -0.46564 | 1.9888
74 | 0.0073383 | 0.001839 | -0.0073376 | -0.0018387 | 6.6115e-07 | 2.4307e-07 | 0.011124 | 0.011124 | 0.011124 | 0.98159 | -0.35377 | 0.98149 | -0.35566 | 3.0561
75 | 0.053413 | 0.013469 | -0.053343 | -0.013424 | 7.026e-05 | 4.4606e-05 | 0.081 | 0.081001 | 0.081001 | 0.98159 | -0.35377 | 0.98018 | -0.38129 | 22.2529
76 | 0.051241 | 0.012897 | -0.051211 | -0.012878 | 3.0627e-05 | 1.9431e-05 | 0.07781 | 0.07781 | 0.07781 | 0.98018 | -0.38129 | 0.97954 | -0.39381 | 21.3763
77 | 0.049334 | 0.012408 | -0.049321 | -0.012399 | 1.2869e-05 | 8.1592e-06 | 0.074959 | 0.074959 | 0.074959 | 0.97954 | -0.39381 | 0.97926 | -0.39927 | 20.5932
78 | 0.047657 | 0.011982 | -0.047649 | -0.011977 | 8.0415e-06 | 5.0951e-06 | 0.07243 | 0.07243 | 0.07243 | 0.97926 | -0.39927 | 0.97908 | -0.4028 | 19.8983
79 | 0.0053894 | 0.0013505 | -0.0053894 | -0.0013504 | 2.4431e-08 | 3.3029e-09 | 0.0081707 | 0.0081707 | 0.0081707 | 0.98149 | -0.35566 | 0.98148 | -0.35576 | 2.2447
80 | 0.044321 | 0.011143 | -0.044306 | -0.011134 | 1.4574e-05 | 9.2195e-06 | 0.067372 | 0.067372 | 0.067372 | 0.97908 | -0.4028 | 0.97873 | -0.40969 | 18.5087
81 | 0.0031183 | 0.00078126 | -0.0031181 | -0.00078142 | 1.872e-07 | -1.6245e-07 | 0.0047276 | 0.0047277 | 0.0047277 | 0.98148 | -0.35576 | 0.98142 | -0.35702 | 1.2988
82 | -0.055658 | -0.014125 | 0.055665 | 0.01413 | 7.5978e-06 | 4.8241e-06 | 0.083002 | 0.083002 | 0.083002 | 0.99855 | -0.027578 | 0.9987 | -0.024741 | 22.8027
83 | -0.056653 | -0.014377 | 0.056721 | 0.01442 | 6.7506e-05 | 4.2873e-05 | 0.084474 | 0.084474 | 0.084474 | 0.9987 | -0.024741 | 1 | 0 | 23.2072
84 | 0.22431 | 0.057387 | -0.22389 | -0.057119 | 0.00041902 | 0.00026765 | 0.33419 | 0.33419 | 0.33419 | 1 | 0 | 0.99796 | -0.03867 | 45.9055
85 | 0.0012699 | 0.00031821 | -0.0012699 | -0.00031826 | 6.4308e-09 | -5.4339e-08 | 0.0019254 | 0.0019254 | 0.0019254 | 0.98142 | -0.35702 | 0.98141 | -0.35712 | 0.52895
86 | -0.020013 | -0.005016 | 0.020019 | 0.0050193 | 5.5189e-06 | 3.3344e-06 | 0.03051 | 0.03051 | 0.03051 | 0.97606 | -0.46206 | 0.97635 | -0.45627 | 8.3819
87 | 0.011147 | 0.0027939 | -0.011147 | -0.0027935 | 6.6433e-07 | 3.4851e-07 | 0.016994 | 0.016994 | 0.016994 | 0.97606 | -0.46206 | 0.976 | -0.46331 | 4.6688
88 | 0.0088657 | 0.0022221 | -0.0088644 | -0.0022215 | 1.3499e-06 | 6.1768e-07 | 0.013516 | 0.013516 | 0.013516 | 0.97606 | -0.46206 | 0.9759 | -0.46525 | 3.7132
89 | 0.0024432 | 0.00061216 | -0.0024431 | -0.0006123 | 8.213e-08 | -1.4498e-07 | 0.0037235 | 0.0037236 | 0.0037236 | 0.97635 | -0.45627 | 0.97632 | -0.45698 | 1.023
90 | -0.022462 | -0.0056315 | 0.022471 | 0.0056371 | 9.2194e-06 | 5.6379e-06 | 0.034234 | 0.034234 | 0.034234 | 0.97635 | -0.45627 | 0.97679 | -0.44766 | 9.4049
91 | 0.0083331 | 0.0020885 | -0.0083326 | -0.0020883 | 4.8129e-07 | 2.0866e-07 | 0.012705 | 0.012705 | 0.012705 | 0.976 | -0.46331 | 0.97594 | -0.46452 | 3.4903
92 | 0.0028136 | 0.00070499 | -0.0028135 | -0.00070513 | 1.1672e-07 | -1.3668e-07 | 0.0042896 | 0.0042897 | 0.0042897 | 0.976 | -0.46331 | 0.97595 | -0.46418 | 1.1785
93 | 0.0068046 | 0.0017053 | -0.0068045 | -0.0017052 | 1.2555e-07 | 4.1494e-08 | 0.010375 | 0.010375 | 0.010375 | 0.9759 | -0.46525 | 0.97588 | -0.46564 | 2.8504
94 | -0.024527 | -0.0061525 | 0.024528 | 0.0061526 | 2.0686e-07 | 1.2744e-07 | 0.037366 | 0.037366 | 0.037366 | 0.97679 | -0.44766 | 0.9768 | -0.44748 | 10.2655
95 | -0.030496 | -0.0076913 | 0.030561 | 0.0077314 | 6.4271e-05 | 4.0087e-05 | 0.045896 | 0.045895 | 0.045896 | 0.98911 | -0.20877 | 0.99138 | -0.16484 | 12.6087
96 | -0.031224 | -0.0078977 | 0.031228 | 0.0079003 | 4.0832e-06 | 2.5494e-06 | 0.046892 | 0.046892 | 0.046892 | 0.99138 | -0.16484 | 0.99153 | -0.16211 | 12.8823
97 | 0.0026956 | 0.0006755 | -0.0026956 | -0.00067557 | 4.9476e-08 | -7.4014e-08 | 0.004029 | 0.0040291 | 0.0040291 | 0.99555 | -0.085033 | 0.99553 | -0.085418 | 1.1069
98 | -0.0024415 | -0.00061189 | 0.0024416 | 0.00061168 | 1.1045e-07 | -2.1012e-07 | 0.0036711 | 0.003671 | 0.0036711 | 0.9896 | -0.19922 | 0.98965 | -0.19827 | 1.0085
99 | 0.033861 | 0.0085739 | -0.033843 | -0.0085624 | 1.839e-05 | 1.1524e-05 | 0.050785 | 0.050785 | 0.050785 | 0.99274 | -0.13876 | 0.99215 | -0.15008 | 13.9521
100 | 0.032616 | 0.008255 | -0.032615 | -0.0082545 | 7.7759e-07 | 4.8648e-07 | 0.048946 | 0.048946 | 0.048946 | 0.99215 | -0.15008 | 0.99213 | -0.15057 | 13.4466
101 | 0.031951 | 0.0080881 | -0.031934 | -0.008077 | 1.7693e-05 | 1.1059e-05 | 0.04795 | 0.04795 | 0.04795 | 0.99213 | -0.15057 | 0.99153 | -0.16211 | 13.1731
102 | -0.027297 | -0.0068467 | 0.027305 | 0.0068519 | 8.3974e-06 | 5.2122e-06 | 0.041585 | 0.041585 | 0.041585 | 0.9768 | -0.44748 | 0.97713 | -0.44103 | 11.4244
103 | -0.030533 | -0.0076607 | 0.030536 | 0.0076628 | 3.3762e-06 | 2.1086e-06 | 0.0465 | 0.0465 | 0.0465 | 0.97713 | -0.44103 | 0.97725 | -0.43871 | 12.7746
104 | -0.033122 | -0.0083109 | 0.033126 | 0.0083135 | 4.197e-06 | 2.631e-06 | 0.050437 | 0.050437 | 0.050437 | 0.97725 | -0.43871 | 0.97738 | -0.43606 | 13.8563
105 | -0.044037 | -0.011057 | 0.044081 | 0.011085 | 4.3682e-05 | 2.7613e-05 | 0.066158 | 0.066158 | 0.066158 | 0.9906 | -0.17996 | 0.99167 | -0.15919 | 18.1752
106 | 0.005968 | 0.0014954 | -0.0059673 | -0.0014952 | 7.0551e-07 | 1.5864e-07 | 0.0090286 | 0.0090288 | 0.0090288 | 0.98358 | -0.31618 | 0.98346 | -0.31866 | 2.4804
107 | 0.0032681 | 0.00081876 | -0.0032678 | -0.00081899 | 3.1482e-07 | -2.3414e-07 | 0.0049447 | 0.0049449 | 0.0049449 | 0.98346 | -0.31866 | 0.98335 | -0.32068 | 1.3585
108 | 0.046753 | 0.011766 | -0.046722 | -0.011747 | 3.0905e-05 | 1.9563e-05 | 0.07012 | 0.07012 | 0.07012 | 0.99238 | -0.14535 | 0.99167 | -0.15919 | 19.2638
109 | 0.037068 | 0.0093083 | -0.037059 | -0.009303 | 8.3362e-06 | 5.2476e-06 | 0.05641 | 0.05641 | 0.05641 | 0.97792 | -0.42558 | 0.97768 | -0.4303 | 15.4972
110 | -0.038825 | -0.0097487 | 0.038845 | 0.009761 | 1.946e-05 | 1.2268e-05 | 0.059084 | 0.059084 | 0.059084 | 0.97792 | -0.42558 | 0.97845 | -0.41508 | 16.2318
111 | 0.035419 | 0.008892 | -0.03541 | -0.0088859 | 9.7283e-06 | 6.1142e-06 | 0.053914 | 0.053914 | 0.053914 | 0.97768 | -0.4303 | 0.97738 | -0.43606 | 14.8114
112 | -0.040633 | -0.010209 | 0.040642 | 0.010215 | 8.9181e-06 | 5.6294e-06 | 0.061803 | 0.061803 | 0.061803 | 0.97845 | -0.41508 | 0.97868 | -0.41048 | 16.9788
113 | -0.042375 | -0.010649 | 0.042377 | 0.01065 | 1.6048e-06 | 1.0141e-06 | 0.064439 | 0.064439 | 0.064439 | 0.97868 | -0.41048 | 0.97873 | -0.40969 | 17.703
114 | 0.0035734 | 0.00089553 | -0.0035733 | -0.00089556 | 5.8338e-08 | -3.2916e-08 | 0.0053534 | 0.0053535 | 0.0053535 | 0.99324 | -0.12892 | 0.99322 | -0.12926 | 1.4707

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28882 | 0.073346

## res_load
| p_mw | q_mvar
0 | 0.0010631 | 0.00026643
1 | 0.00097689 | 0.00024483
2 | 0.003006 | 0.00075338
3 | 0.0015964 | 0.0004001
4 | 0.0037648 | 0.00094354
5 | 0.0020448 | 0.00051247
6 | 0.0020442 | 0.00051232
7 | 0.0023537 | 0.0005899
8 | 0.0030029 | 0.00075259
9 | 0.0029682 | 0.0007439
10 | 0.0017422 | 0.00043664
11 | 0.0024043 | 0.00060259
12 | 0.002074 | 0.00051979
13 | 0.0039435 | 0.00098833
14 | 0.0074032 | 0.0018554
15 | 0.0035651 | 0.0008935
16 | 0.0030204 | 0.00075697
17 | 0.0053131 | 0.0013316
18 | 0.0036758 | 0.00092125
19 | 0.0051289 | 0.0012854
20 | 0.0039039 | 0.0009784
21 | 0.0051018 | 0.0012786
22 | 0.0017155 | 0.00042995
23 | 0.0019347 | 0.00048488
24 | 0.0063233 | 0.0015848
25 | 0.0016094 | 0.00040336
26 | 0.0028438 | 0.00071272
27 | 0.007908 | 0.0019819
28 | 0.0024767 | 0.00062072
29 | 0.0034106 | 0.00085477
30 | 0.0023622 | 0.00059203
31 | 0.0024254 | 0.00060785
32 | 0.0041114 | 0.0010304
33 | 0.0020933 | 0.00052463
34 | 0.016665 | 0.0041767
35 | 0.0025801 | 0.00064663
36 | 0.0018087 | 0.0004533
37 | 0.0031929 | 0.00080022
38 | 0.0044334 | 0.0011111
39 | 0.0026414 | 0.000662
40 | 0.0048525 | 0.0012161
41 | 0.0037305 | 0.00093494
42 | 0.0020664 | 0.0005179
43 | 0.0036966 | 0.00092644
44 | 0.003654 | 0.00091578
45 | 0.0023722 | 0.00059454
46 | 0.002375 | 0.00059524
47 | 0.0021019 | 0.00052679
48 | 0.0018764 | 0.00047028
49 | 0.0016647 | 0.00041722
50 | 0.0019482 | 0.00048827
51 | 0.0033281 | 0.0008341
52 | 0.0022711 | 0.00056919
53 | 0.00098776 | 0.00024756
54 | 0.00098809 | 0.00024764
55 | 0.0061418 | 0.0015393
56 | 0.0033187 | 0.00083174
57 | 0.0018483 | 0.00046322
58 | 0.0012699 | 0.00031826
59 | 0.0020597 | 0.00051621
60 | 0.0024431 | 0.0006123
61 | 0.0020565 | 0.0005154
62 | 0.0083326 | 0.0020883
63 | 0.0028135 | 0.00070513
64 | 0.0020568 | 0.00051549
65 | 0.00072824 | 0.00018251
66 | 0.00066373 | 0.00016635
67 | 0.0017967 | 0.00045031
68 | 0.0020316 | 0.00050916
69 | 0.0026956 | 0.00067557
70 | 0.0020009 | 0.00050146
71 | 0.0024415 | 0.00061189
72 | 0.0040894 | 0.0010249
73 | 0.00074781 | 0.00018742
74 | 0.0012268 | 0.00030745
75 | 0.00066383 | 0.00016637
76 | 0.0027692 | 0.00069403
77 | 0.0032273 | 0.00080885
78 | 0.0025858 | 0.00064805
79 | 0.0043582 | 0.0010923
80 | 0.00084318 | 0.00021132
81 | 0.0026992 | 0.00067649
82 | 0.0032678 | 0.00081899
83 | 0.00070533 | 0.00017677
84 | 0.0051081 | 0.0012802
85 | 0.0026408 | 0.00066184
86 | 0.0017575 | 0.00044046
87 | 0.00164 | 0.00041103
88 | 0.001788 | 0.00044812
89 | 0.0022837 | 0.00057236
90 | 0.0017336 | 0.00043449
91 | 0.0019291 | 0.00048347
92 | 0.0030706 | 0.00076957
93 | 0.0047745 | 0.0011966
94 | 0.0035733 | 0.00089556
95 | 0.0028398 | 0.00071173

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1