## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1054-34_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1054-34_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1054-34_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1054-34_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1054-34_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1054-34_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1054-34_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1054-34_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1054-34_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1054-34_0_3_node_73 | 0.4 | n |  | TRUE
10 | bus_LV_1054-34_0_3_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_1054-34_0_3_node_96 | 0.4 | n |  | TRUE
12 | bus_LV_1054-34_0_3_node_97 | 0.4 | n |  | TRUE
13 | bus_LV_1054-34_0_3_node_71 | 0.4 | n |  | TRUE
14 | bus_LV_1054-34_0_3_node_98 | 0.4 | n |  | TRUE
15 | bus_LV_1054-34_0_3_node_85 | 0.4 | n |  | TRUE
16 | bus_LV_1054-34_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1054-34_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1054-34_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1054-34_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1054-34_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1054-34_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1054-34_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1054-34_0_3_node_68 | 0.4 | n |  | TRUE
24 | bus_LV_1054-34_0_3_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_1054-34_0_3_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_1054-34_0_3_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_1054-34_0_3_node_77 | 0.4 | n |  | TRUE
28 | bus_LV_1054-34_0_3_node_57 | 0.4 | n |  | TRUE
29 | bus_LV_1054-34_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1054-34_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1054-34_0_3_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1054-34_0_3_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1054-34_0_3_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1054-34_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1054-34_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1054-34_0_3_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1054-34_0_3_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1054-34_0_3_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1054-34_0_3_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_1054-34_0_3_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_1054-34_0_3_node_74 | 0.4 | n |  | TRUE
42 | bus_LV_1054-34_0_3_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1054-34_0_3_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_1054-34_0_3_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_1054-34_0_3_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_1054-34_0_3_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_1054-34_0_3_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1054-34_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1054-34_0_3_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_1054-34_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1054-34_0_3_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_1054-34_0_3_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_1054-34_0_3_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1054-34_0_3_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_1054-34_0_3_node_104 | 0.4 | n |  | TRUE
56 | bus_LV_1054-34_0_3_node_76 | 0.4 | n |  | TRUE
57 | bus_LV_1054-34_0_3_node_118 | 0.4 | n |  | TRUE
58 | bus_LV_1054-34_0_3_node_117 | 0.4 | n |  | TRUE
59 | bus_LV_1054-34_0_3_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_1054-34_0_3_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_1054-34_0_3_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_1054-34_0_3_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_1054-34_0_3_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_1054-34_0_3_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_1054-34_0_3_node_101 | 0.4 | n |  | TRUE
66 | bus_LV_1054-34_0_3_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_1054-34_0_3_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_1054-34_0_3_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_1054-34_0_3_node_44 | 0.4 | n |  | TRUE
70 | bus_LV_1054-34_0_3_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_1054-34_0_3_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_1054-34_0_3_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_1054-34_0_3_node_99 | 0.4 | n |  | TRUE
74 | bus_LV_1054-34_0_3_node_105 | 0.4 | n |  | TRUE
75 | bus_LV_1054-34_0_3_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_1054-34_0_3_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_1054-34_0_3_node_103 | 0.4 | n |  | TRUE
78 | bus_LV_1054-34_0_3_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_1054-34_0_3_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_1054-34_0_3_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_1054-34_0_3_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_1054-34_0_3_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_1054-34_0_3_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_1054-34_0_3_node_107 | 0.4 | n |  | TRUE
85 | bus_LV_1054-34_0_3_node_106 | 0.4 | n |  | TRUE
86 | bus_LV_1054-34_0_3_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_1054-34_0_3_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_1054-34_0_3_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_1054-34_0_3_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_1054-34_0_3_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_1054-34_0_3_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_1054-34_0_3_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_1054-34_0_3_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_1054-34_0_3_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1054-34_0_3_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1054-34_0_3_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1054-34_0_3_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_1054-34_0_3_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_1054-34_0_3_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_1054-34_0_3_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_1054-34_0_3_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_1054-34_0_3_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_1054-34_0_3_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_1054-34_0_3_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_1054-34_0_3_node_94 | 0.4 | n |  | TRUE
106 | bus_LV_1054-34_0_3_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_1054-34_0_3_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_1054-34_0_3_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_1054-34_0_3_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_1054-34_0_3_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_1054-34_0_3_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_1054-34_0_3_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_1054-34_0_3_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_1054-34_0_3_node_115 | 0.4 | n |  | TRUE
115 | bus_MV_211_0_node_197 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1054-34_0_3_load_0 | 0 | 0.0024433 | 0.00061236 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1054-34_0_3_load_1 | 1 | 0.0027144 | 0.0006803 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1054-34_0_3_load_3 | 3 | 0.0033293 | 0.0008344 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1054-34_0_3_load_4 | 4 | 0.0025289 | 0.0006338 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1054-34_0_3_load_5 | 5 | 0.0055576 | 0.0013929 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1054-34_0_3_load_6 | 6 | 0.0024074 | 0.00060336 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1054-34_0_3_load_7 | 7 | 0.0025454 | 0.00063793 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1054-34_0_3_load_73 | 9 | 0.0023113 | 0.00057927 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1054-34_0_3_load_55 | 10 | 0.0022206 | 0.00055654 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1054-34_0_3_load_96 | 11 | 0.002492 | 0.00062454 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1054-34_0_3_load_71 | 13 | 0.0023387 | 0.00058615 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1054-34_0_3_load_98 | 14 | 0.0029329 | 0.00073506 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1054-34_0_3_load_85 | 15 | 0.0028751 | 0.00072057 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1054-34_0_3_load_9 | 16 | 0.0023016 | 0.00057684 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1054-34_0_3_load_10 | 17 | 0.0011476 | 0.00028761 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1054-34_0_3_load_11 | 18 | 0.0014179 | 0.00035536 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1054-34_0_3_load_12 | 19 | 0.0029951 | 0.00075065 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1054-34_0_3_load_13 | 20 | 0.0022001 | 0.00055141 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1054-34_0_3_load_68 | 23 | 0.0022997 | 0.00057636 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1054-34_0_3_load_67 | 24 | 0.0040235 | 0.0010084 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1054-34_0_3_load_66 | 25 | 0.0043117 | 0.0010806 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1054-34_0_3_load_69 | 26 | 0.0028042 | 0.00070281 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1054-34_0_3_load_57 | 28 | 0.0033992 | 0.00085192 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1054-34_0_3_load_16 | 29 | 0.0016756 | 0.00041994 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1054-34_0_3_load_17 | 30 | 0.0016737 | 0.00041948 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1054-34_0_3_load_19 | 32 | 0.0016756 | 0.00041994 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1054-34_0_3_load_20 | 33 | 0.0016737 | 0.00041948 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1054-34_0_3_load_21 | 34 | 0.0050249 | 0.0012594 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1054-34_0_3_load_22 | 35 | 0.0012391 | 0.00031056 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1054-34_0_3_load_24 | 37 | 0.0025382 | 0.00063614 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1054-34_0_3_load_43 | 38 | 0.0019404 | 0.0004863 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1054-34_0_3_load_53 | 39 | 0.0023879 | 0.00059846 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1054-34_0_3_load_74 | 41 | 0.0024506 | 0.00061419 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1054-34_0_3_load_25 | 42 | 0.0028395 | 0.00071164 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1054-34_0_3_load_26 | 43 | 0.0040411 | 0.0010128 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1054-34_0_3_load_27 | 44 | 0.0041171 | 0.0010318 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1054-34_0_3_load_28 | 45 | 0.0028044 | 0.00070285 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1054-34_0_3_load_32 | 49 | 0.0079381 | 0.0019895 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1054-34_0_3_load_47 | 50 | 0.0030971 | 0.00077622 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1054-34_0_3_load_75 | 51 | 0.019192 | 0.0048099 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1054-34_0_3_load_41 | 52 | 0.0029945 | 0.00075049 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1054-34_0_3_load_104 | 55 | 0.014706 | 0.0036856 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1054-34_0_3_load_118 | 57 | 0.0040099 | 0.001005 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1054-34_0_3_load_39 | 59 | 0.001109 | 0.00027794 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1054-34_0_3_load_33 | 60 | 0.0060529 | 0.001517 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1054-34_0_3_load_38 | 62 | 0.0050629 | 0.0012689 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1054-34_0_3_load_36 | 63 | 0.0011087 | 0.00027786 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1054-34_0_3_load_101 | 65 | 0.010318 | 0.0025859 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1054-34_0_3_load_54 | 66 | 0.018502 | 0.004637 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1054-34_0_3_load_49 | 68 | 0.0032964 | 0.00082616 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1054-34_0_3_load_44 | 69 | 0.0017232 | 0.00043187 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1054-34_0_3_load_65 | 70 | 0.001727 | 0.00043282 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1054-34_0_3_load_100 | 72 | 0.0026184 | 0.00065624 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1054-34_0_3_load_99 | 73 | 0.0024147 | 0.00060519 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1054-34_0_3_load_105 | 74 | 0.013355 | 0.0033472 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1054-34_0_3_load_50 | 75 | 0.0020121 | 0.00050429 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1054-34_0_3_load_52 | 76 | 0.0019603 | 0.00049129 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1054-34_0_3_load_103 | 77 | 0.0032068 | 0.00080371 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1054-34_0_3_load_56 | 78 | 0.0024855 | 0.00062293 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1054-34_0_3_load_58 | 79 | 0.001727 | 0.00043282 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1054-34_0_3_load_59 | 80 | 0.0033355 | 0.00083595 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1054-34_0_3_load_60 | 81 | 0.0017232 | 0.00043187 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1054-34_0_3_load_61 | 82 | 0.0031508 | 0.00078967 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1054-34_0_3_load_63 | 83 | 0.0033836 | 0.00084802 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1054-34_0_3_load_107 | 84 | 0.00295 | 0.00073934 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1054-34_0_3_load_106 | 85 | 0.0028826 | 0.00072244 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1054-34_0_3_load_70 | 87 | 0.0040392 | 0.0010123 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1054-34_0_3_load_72 | 88 | 0.0027861 | 0.00069826 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1054-34_0_3_load_81 | 89 | 0.0041668 | 0.0010443 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1054-34_0_3_load_82 | 90 | 0.0024069 | 0.00060323 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1054-34_0_3_load_102 | 91 | 0.002357 | 0.00059072 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1054-34_0_3_load_116 | 92 | 0.0045946 | 0.0011515 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1054-34_0_3_load_78 | 94 | 0.0050803 | 0.0012732 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1054-34_0_3_load_84 | 96 | 0.0024403 | 0.00061159 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1054-34_0_3_load_86 | 97 | 0.0028267 | 0.00070844 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1054-34_0_3_load_87 | 98 | 0.0023155 | 0.00058032 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1054-34_0_3_load_89 | 99 | 0.0024837 | 0.00062248 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1054-34_0_3_load_88 | 100 | 0.0023305 | 0.00058407 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1054-34_0_3_load_90 | 101 | 0.0025948 | 0.00065033 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1054-34_0_3_load_91 | 102 | 0.0023278 | 0.00058339 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1054-34_0_3_load_92 | 103 | 0.0049287 | 0.0012352 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1054-34_0_3_load_94 | 105 | 0.0024174 | 0.00060586 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1054-34_0_3_load_95 | 106 | 0.0022712 | 0.00056922 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1054-34_0_3_load_113 | 107 | 0.0028311 | 0.00070954 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1054-34_0_3_load_111 | 109 | 0.0035008 | 0.00087739 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1054-34_0_3_load_112 | 110 | 0.0035716 | 0.00089512 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1054-34_0_3_load_109 | 111 | 0.0030472 | 0.00076371 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1054-34_0_3_load_108 | 112 | 0.0027197 | 0.00068162 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1054-34_0_3_load_114 | 113 | 0.0017834 | 0.00044697 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1054-34_0_3_load_115 | 114 | 0.0043469 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1054-34_0_3_line_0 |  | 0 | 1 | 0.021673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1054-34_0_3_line_1 |  | 0 | 2 | 0.0068608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1054-34_0_3_line_2 |  | 1 | 3 | 0.0016439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1054-34_0_3_line_3 |  | 2 | 4 | 0.019513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1054-34_0_3_line_4 |  | 2 | 5 | 0.0038179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1054-34_0_3_line_5 |  | 3 | 6 | 0.02199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1054-34_0_3_line_6 |  | 4 | 7 | 0.00015965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1054-34_0_3_line_7 |  | 5 | 8 | 0.047037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1054-34_0_3_line_8 |  | 6 | 9 | 0.0074044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1054-34_0_3_line_9 |  | 7 | 10 | 0.026358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1054-34_0_3_line_10 |  | 8 | 11 | 0.01081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1054-34_0_3_line_11 |  | 8 | 12 | 0.013058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1054-34_0_3_line_12 |  | 9 | 13 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1054-34_0_3_line_13 |  | 12 | 14 | 0.014406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1054-34_0_3_line_14 |  | 12 | 15 | 0.021192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1054-34_0_3_line_15 |  | 13 | 21 | 0.0055715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1054-34_0_3_line_16 |  | 14 | 111 | 0.010677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1054-34_0_3_line_17 |  | 15 | 95 | 0.019017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1054-34_0_3_line_18 |  | 16 | 17 | 0.0039394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1054-34_0_3_line_19 |  | 16 | 18 | 0.0064248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1054-34_0_3_line_20 |  | 17 | 19 | 0.017704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1054-34_0_3_line_21 |  | 18 | 20 | 0.014487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1054-34_0_3_line_22 |  | 19 | 21 | 0.014102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1054-34_0_3_line_23 |  | 20 | 22 | 0.012078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1054-34_0_3_line_24 |  | 21 | 23 | 0.035539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1054-34_0_3_line_25 |  | 22 | 24 | 0.028434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1054-34_0_3_line_26 |  | 22 | 25 | 0.035535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1054-34_0_3_line_27 |  | 23 | 26 | 0.0032234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1054-34_0_3_line_28 |  | 24 | 27 | 0.11466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1054-34_0_3_line_29 |  | 25 | 28 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1054-34_0_3_line_30 |  | 27 | 86 | 0.11538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1054-34_0_3_line_31 |  | 28 | 78 | 0.022751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1054-34_0_3_line_32 |  | 29 | 30 | 0.0051075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1054-34_0_3_line_33 |  | 29 | 31 | 0.0085433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1054-34_0_3_line_34 |  | 30 | 32 | 0.0051075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1054-34_0_3_line_35 |  | 31 | 33 | 0.012141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1054-34_0_3_line_36 |  | 31 | 34 | 0.0077836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1054-34_0_3_line_37 |  | 32 | 35 | 0.0036829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1054-34_0_3_line_38 |  | 33 | 36 | 0.037056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1054-34_0_3_line_39 |  | 34 | 37 | 0.021312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1054-34_0_3_line_40 |  | 36 | 38 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1054-34_0_3_line_41 |  | 37 | 39 | 0.011468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1054-34_0_3_line_42 |  | 38 | 40 | 0.017363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1054-34_0_3_line_43 |  | 39 | 41 | 0.0075715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1054-34_0_3_line_44 |  | 40 | 53 | 0.003907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1054-34_0_3_line_45 |  | 40 | 47 | 0.046891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1054-34_0_3_line_46 |  | 41 | 77 | 0.01206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1054-34_0_3_line_47 |  | 42 | 43 | 0.020142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1054-34_0_3_line_48 |  | 42 | 44 | 0.025258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1054-34_0_3_line_49 |  | 43 | 45 | 0.0047187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1054-34_0_3_line_50 |  | 44 | 46 | 0.05232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1054-34_0_3_line_51 |  | 45 | 47 | 0.044411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1054-34_0_3_line_52 |  | 46 | 48 | 0.007763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1054-34_0_3_line_53 |  | 46 | 49 | 0.040499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1054-34_0_3_line_54 |  | 47 | 50 | 0.012758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1054-34_0_3_line_55 |  | 48 | 51 | 0.024705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1054-34_0_3_line_56 |  | 49 | 52 | 0.043214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1054-34_0_3_line_57 |  | 50 | 54 | 0.011604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1054-34_0_3_line_58 |  | 51 | 55 | 0.083853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1054-34_0_3_line_59 |  | 52 | 59 | 0.032635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1054-34_0_3_line_60 |  | 53 | 74 | 0.064977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1054-34_0_3_line_61 |  | 54 | 75 | 0.028849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1054-34_0_3_line_62 |  | 54 | 68 | 0.014606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1054-34_0_3_line_63 |  | 56 | 57 | 0.052993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1054-34_0_3_line_64 |  | 56 | 58 | 0.049215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1054-34_0_3_line_65 |  | 58 | 92 | 0.065121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1054-34_0_3_line_66 |  | 59 | 63 | 0.00075197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1054-34_0_3_line_67 |  | 60 | 61 | 0.017597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1054-34_0_3_line_68 |  | 61 | 62 | 0.031948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1054-34_0_3_line_69 |  | 62 | 67 | 0.028677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1054-34_0_3_line_70 |  | 64 | 65 | 0.048557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1054-34_0_3_line_71 |  | 64 | 66 | 0.0067986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1054-34_0_3_line_72 |  | 66 | 67 | 0.037891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1054-34_0_3_line_73 |  | 67 | 68 | 0.027093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1054-34_0_3_line_74 |  | 69 | 70 | 0.0050405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1054-34_0_3_line_75 |  | 70 | 71 | 0.0028583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1054-34_0_3_line_76 |  | 71 | 81 | 0.0021876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1054-34_0_3_line_77 |  | 72 | 73 | 0.0038631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1054-34_0_3_line_78 |  | 73 | 76 | 0.035828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1054-34_0_3_line_79 |  | 75 | 76 | 0.0050259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1054-34_0_3_line_80 |  | 77 | 91 | 0.0048018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_1054-34_0_3_line_81 |  | 79 | 80 | 0.0087374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1054-34_0_3_line_82 |  | 79 | 81 | 0.0050406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1054-34_0_3_line_83 |  | 80 | 82 | 0.0079435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1054-34_0_3_line_84 |  | 82 | 83 | 0.0025601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1054-34_0_3_line_85 |  | 83 | 84 | 0.0086209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1054-34_0_3_line_86 |  | 84 | 85 | 0.0026594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1054-34_0_3_line_87 |  | 85 | 112 | 0.00813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1054-34_0_3_line_88 |  | 86 | 93 | 0.12528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1054-34_0_3_line_89 |  | 87 | 88 | 0.027821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1054-34_0_3_line_90 |  | 88 | 89 | 0.019432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1054-34_0_3_line_91 |  | 89 | 90 | 0.040616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1054-34_0_3_line_92 |  | 90 | 95 | 0.03773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1054-34_0_3_line_93 |  | 90 | 96 | 0.0049114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1054-34_0_3_line_94 |  | 91 | 97 | 0.0062969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_1054-34_0_3_line_95 |  | 92 | 113 | 0.0086727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1054-34_0_3_line_96 |  | 93 | 94 | 0.0030053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1054-34_0_3_line_97 |  | 95 | 97 | 0.018481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_1054-34_0_3_line_98 |  | 96 | 98 | 0.0089596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1054-34_0_3_line_99 |  | 98 | 99 | 0.005255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1054-34_0_3_line_100 |  | 99 | 100 | 0.015854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1054-34_0_3_line_101 |  | 100 | 101 | 0.0053008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1054-34_0_3_line_102 |  | 101 | 102 | 0.0088392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1054-34_0_3_line_103 |  | 102 | 103 | 0.010992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1054-34_0_3_line_104 |  | 103 | 104 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1054-34_0_3_line_105 |  | 104 | 105 | 0.027648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1054-34_0_3_line_106 |  | 104 | 106 | 0.012769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1054-34_0_3_line_107 |  | 105 | 107 | 0.00421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1054-34_0_3_line_108 |  | 106 | 108 | 0.010014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1054-34_0_3_line_109 |  | 108 | 109 | 0.017894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1054-34_0_3_line_110 |  | 108 | 110 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1054-34_0_3_line_111 |  | 109 | 113 | 0.026785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1054-34_0_3_line_112 |  | 110 | 114 | 0.02367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1054-34_0_3_line_113 |  | 111 | 112 | 0.0029825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1054-34_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 115 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2668567.091 | 1214301.0752 | 2668555.7587 | 1214282.6007
1 | 2668570.6784 | 1214306.9234 | 2668567.091 | 1214301.0752
2 | 2668554.8991 | 1214281.1994 | 2668555.7587 | 1214282.6007
3 | 2668570.6784 | 1214306.9234 | 2668575.7289 | 1214312.8963 | 2668580.8693 | 1214318.9815 | 2668583.7284 | 1214321.3697
4 | 2668570.6784 | 1214306.9234 | 2668567.614 | 1214309.2007
5 | 2668554.8991 | 1214281.1994 | 2668548.8783 | 1214271.3839 | 2668545.9363 | 1214263.0226 | 2668545.8268 | 1214261.4154
6 | 2668583.8509 | 1214321.4721 | 2668583.7284 | 1214321.3697
7 | 2668544.2121 | 1214340.9628 | 2668546.9142 | 1214337.8141 | 2668545.3719 | 1214331.2478 | 2668569.8171 | 1214316.4306 | 2668567.614 | 1214309.2007
8 | 2668545.8268 | 1214261.4154 | 2668545.4164 | 1214255.3896 | 2668545.5075 | 1214254.0279
9 | 2668583.8509 | 1214321.4721 | 2668592.9212 | 1214329.0486 | 2668604.7288 | 1214337.5323
10 | 2668544.2121 | 1214340.9628 | 2668549.3021 | 1214347.4698 | 2668550.9589 | 1214349.4063
11 | 2668536.3111 | 1214330.5543 | 2668538.3661 | 1214333.4909 | 2668544.2121 | 1214340.9628
12 | 2668547.9467 | 1214240.105 | 2668545.8566 | 1214248.8128 | 2668545.5075 | 1214254.0279
13 | 2668536.3111 | 1214330.5543 | 2668532.0788 | 1214334.0079 | 2668532.5153 | 1214342.9407
14 | 2668536.3111 | 1214330.5543 | 2668527.2099 | 1214317.5194 | 2668524.663 | 1214312.8776
15 | 2668549.2471 | 1214234.6874 | 2668547.9467 | 1214240.105
16 | 2668521.84 | 1214343.1149 | 2668532.5153 | 1214342.9407 | 2668532.5153 | 1214342.9407
17 | 2668515.515 | 1214296.205 | 2668524.663 | 1214312.8776
18 | 2668583.9448 | 1214241.8018 | 2668583.9448 | 1214241.8018 | 2668580.6659 | 1214239.6183 | 2668580.6659 | 1214239.6183
19 | 2668583.9448 | 1214241.8018 | 2668587.9759 | 1214241.9816 | 2668589.8164 | 1214240.4574
20 | 2668563.1452 | 1214237.0784 | 2668580.6659 | 1214239.6183
21 | 2668604.1399 | 1214241.9008 | 2668597.2131 | 1214241.2207 | 2668595.66 | 1214241.5364 | 2668589.8164 | 1214240.4574
22 | 2668549.2471 | 1214234.6874 | 2668562.5885 | 1214236.9977 | 2668563.1452 | 1214237.0784
23 | 2668615.8296 | 1214243.8587 | 2668612.7944 | 1214243.6014 | 2668605.6692 | 1214242.9968 | 2668604.1399 | 1214241.9008
24 | 2668549.2471 | 1214234.6874 | 2668556.7464 | 1214203.4206 | 2668557.4998 | 1214200.1205
25 | 2668615.8296 | 1214243.8587 | 2668615.9448 | 1214242.4258 | 2668642.7121 | 1214245.9395
26 | 2668615.8296 | 1214243.8587 | 2668612.97 | 1214279.2781
27 | 2668557.4998 | 1214200.1205 | 2668558.2172 | 1214196.9779
28 | 2668750.4279 | 1214253.7705 | 2668748.1724 | 1214254.4004 | 2668735.5385 | 1214248.0508 | 2668721.682 | 1214245.623 | 2668714.2236 | 1214243.6247 | 2668692.2931 | 1214236.5899 | 2668686.2777 | 1214237.2321 | 2668684.1756 | 1214238.3864 | 2668670.297 | 1214248.4218 | 2668664.687 | 1214248.8241 | 2668642.7121 | 1214245.9395
29 | 2668616.907 | 1214295.5701 | 2668614.8796 | 1214291.4109 | 2668612.7823 | 1214281.6029 | 2668612.97 | 1214279.2781
30 | 2668659.8208 | 1214184.6501 | 2668672.0541 | 1214191.5063 | 2668690.308 | 1214199.9107 | 2668698.7546 | 1214211.7376 | 2668734.4723 | 1214239.0773 | 2668743.1349 | 1214245.9926 | 2668750.4279 | 1214253.7705
31 | 2668616.907 | 1214295.5701 | 2668619.8066 | 1214301.5184 | 2668627.535 | 1214315.6805
32 | 2668447.0264 | 1214307.164 | 2668447.0888 | 1214312.2711
33 | 2668447.1931 | 1214320.8137 | 2668447.0888 | 1214312.2711
34 | 2668447.0264 | 1214307.164 | 2668446.9641 | 1214302.0569
35 | 2668447.1931 | 1214320.8137 | 2668447.3436 | 1214332.9536
36 | 2668447.1931 | 1214320.8137 | 2668453.9145 | 1214316.8884
37 | 2668446.9191 | 1214298.3743 | 2668446.9641 | 1214302.0569
38 | 2668447.7979 | 1214370.0071 | 2668447.7069 | 1214362.0566 | 2668447.682 | 1214360.2552 | 2668447.3436 | 1214332.9536
39 | 2668453.9145 | 1214316.8884 | 2668454.4053 | 1214307.2213 | 2668462.5739 | 1214300.9556 | 2668462.4905 | 1214299.6205
40 | 2668447.7979 | 1214370.0071 | 2668434.786 | 1214362.2051
41 | 2668471.985 | 1214297.7825 | 2668469.7508 | 1214297.7137 | 2668469.8201 | 1214299.6157 | 2668462.4905 | 1214299.6205
42 | 2668419.895 | 1214353.2764 | 2668434.786 | 1214362.2051
43 | 2668471.985 | 1214297.7825 | 2668479.5529 | 1214298.0153 | 2668479.5529 | 1214298.0153
44 | 2668421.4779 | 1214349.7034 | 2668419.895 | 1214353.2764
45 | 2668419.895 | 1214353.2764 | 2668385.9792 | 1214332.341 | 2668380.6176 | 1214327.6432
46 | 2668489.5065 | 1214299.9593 | 2668479.4389 | 1214300.0042 | 2668479.5529 | 1214298.0153
47 | 2668353.0018 | 1214287.5814 | 2668344.9086 | 1214269.1373
48 | 2668334.7594 | 1214246.0077 | 2668344.9086 | 1214269.1373
49 | 2668353.0018 | 1214287.5814 | 2668354.8978 | 1214291.9024
50 | 2668312.7661 | 1214198.6294 | 2668316.2757 | 1214203.884 | 2668334.7594 | 1214246.0077
51 | 2668380.6176 | 1214327.6432 | 2668376.9254 | 1214324.41 | 2668369.1115 | 1214315.6594 | 2668362.0901 | 1214306.0062 | 2668355.4917 | 1214293.2559 | 2668354.8978 | 1214291.9024
52 | 2668316.0822 | 1214191.6074 | 2668314.9692 | 1214193.9517 | 2668312.7661 | 1214198.6294
53 | 2668312.7661 | 1214198.6294 | 2668310.2128 | 1214204.0368 | 2668307.4338 | 1214209.9198 | 2668304.012 | 1214210.2586 | 2668301.3893 | 1214211.118 | 2668298.4224 | 1214213.5077 | 2668290.5592 | 1214229.7051
54 | 2668380.6176 | 1214327.6432 | 2668378.1122 | 1214330.861 | 2668372.7039 | 1214337.6501
55 | 2668316.0822 | 1214191.6074 | 2668320.4928 | 1214199.7741 | 2668325.524 | 1214214.3533
56 | 2668274.3808 | 1214269.6363 | 2668277.4486 | 1214258.1734 | 2668284.4668 | 1214242.2548 | 2668290.5592 | 1214229.7051
57 | 2668365.4739 | 1214346.726 | 2668372.7039 | 1214337.6501
58 | 2668325.524 | 1214214.3533 | 2668329.2408 | 1214225.1235 | 2668358.9985 | 1214291.1912
59 | 2668274.3808 | 1214269.6363 | 2668272.64 | 1214276.1407 | 2668271.6827 | 1214284.7907 | 2668271.5476 | 1214292.6051 | 2668272.1265 | 1214300.4167 | 2668272.3984 | 1214301.9427
60 | 2668421.4779 | 1214349.7034 | 2668424.0743 | 1214343.8518 | 2668426.1787 | 1214338.517 | 2668426.0877 | 1214335.8588 | 2668425.2913 | 1214333.1146 | 2668407.7548 | 1214305.8852 | 2668407.0886 | 1214302.3865 | 2668407.8704 | 1214299.7827 | 2668414.0097 | 1214293.6271
61 | 2668365.4739 | 1214346.726 | 2668387.7058 | 1214365.1111
62 | 2668365.4739 | 1214346.726 | 2668367.2169 | 1214351.0487 | 2668364.5066 | 1214354.909 | 2668361.9604 | 1214353.0786 | 2668360.7142 | 1214354.7596
63 | 2668364.6453 | 1214149.4485 | 2668356.8567 | 1214128.5239 | 2668346.3941 | 1214099.686
64 | 2668346.3941 | 1214099.686 | 2668391.5278 | 1214079.7686
65 | 2668391.5278 | 1214079.7686 | 2668393.8493 | 1214095.9054 | 2668395.5155 | 1214101.6169 | 2668399.5988 | 1214107.1895 | 2668408.3347 | 1214115.0501 | 2668424.7363 | 1214130.0254 | 2668426.1345 | 1214131.4528
66 | 2668272.5303 | 1214302.683 | 2668272.3984 | 1214301.9427
67 | 2668301.1663 | 1214396.287 | 2668293.0795 | 1214385.4987 | 2668291.323 | 1214381.7786
68 | 2668301.1663 | 1214396.287 | 2668322.4322 | 1214387.7363 | 2668330.6192 | 1214383.9328
69 | 2668357.7914 | 1214376.1898 | 2668350.081 | 1214376.2904 | 2668341.9573 | 1214378.6654 | 2668330.6192 | 1214383.9328
70 | 2668355.9709 | 1214413.7369 | 2668365.1724 | 1214421.3582 | 2668377.9983 | 1214406.3403 | 2668381.8756 | 1214408.664 | 2668389.6829 | 1214399.1082
71 | 2668355.9709 | 1214413.7369 | 2668357.7929 | 1214407.187
72 | 2668357.7914 | 1214376.1898 | 2668364.0479 | 1214378.3517 | 2668366.3715 | 1214383.6928 | 2668366.0013 | 1214390.8041 | 2668364.1483 | 1214394.7632 | 2668357.7929 | 1214407.187
73 | 2668357.7914 | 1214376.1898 | 2668360.6969 | 1214371.8537 | 2668356.6581 | 1214367.06 | 2668360.4358 | 1214361.5109 | 2668357.7019 | 1214358.8223 | 2668360.7142 | 1214354.7596
74 | 2668488.3986 | 1214367.5099 | 2668488.5159 | 1214362.4707
75 | 2668488.5824 | 1214359.6132 | 2668488.5159 | 1214362.4707
76 | 2668488.5824 | 1214359.6132 | 2668488.6325 | 1214357.4261
77 | 2668419.4188 | 1214390.862 | 2668422.4549 | 1214393.2506
78 | 2668419.4188 | 1214390.862 | 2668407.6153 | 1214381.5755 | 2668391.5789 | 1214368.314
79 | 2668391.5789 | 1214368.314 | 2668387.7058 | 1214365.1111
80 | 2668489.5065 | 1214299.9593 | 2668494.3083 | 1214299.9379
81 | 2668488.748 | 1214352.3869 | 2668488.9481 | 1214343.6518
82 | 2668488.748 | 1214352.3869 | 2668488.6325 | 1214357.4261
83 | 2668488.9481 | 1214343.6518 | 2668488.9481 | 1214343.6518 | 2668496.8905 | 1214343.5222
84 | 2668496.8905 | 1214343.5222 | 2668499.4502 | 1214343.4804
85 | 2668508.07 | 1214343.3397 | 2668499.4502 | 1214343.4804
86 | 2668510.729 | 1214343.2963 | 2668508.07 | 1214343.3397
87 | 2668510.729 | 1214343.2963 | 2668518.858 | 1214343.1636
88 | 2668659.8208 | 1214184.6501 | 2668632.1964 | 1214160.1946 | 2668633.6191 | 1214150.7606 | 2668635.9553 | 1214142.4601 | 2668630.8343 | 1214136.0082 | 2668615.3123 | 1214130.4372 | 2668603.4314 | 1214127.2541 | 2668597.698 | 1214121.2066 | 2668595.6224 | 1214106.8626 | 2668593.0813 | 1214096.6604
89 | 2668522.7903 | 1214211.4781 | 2668530.4445 | 1214184.8178 | 2668530.4842 | 1214184.7441
90 | 2668517.4279 | 1214230.1559 | 2668522.7903 | 1214211.4781
91 | 2668497.355 | 1214263.109 | 2668507.5988 | 1214256.7115 | 2668511.6449 | 1214250.2984 | 2668517.4279 | 1214230.1559
92 | 2668515.515 | 1214296.205 | 2668497.355 | 1214263.109
93 | 2668497.355 | 1214263.109 | 2668494.9627 | 1214258.8196
94 | 2668500.6052 | 1214299.9099 | 2668494.3083 | 1214299.9379
95 | 2668431.8963 | 1214137.89 | 2668430.9376 | 1214136.3561 | 2668426.1345 | 1214131.4528
96 | 2668593.0813 | 1214096.6604 | 2668591.2198 | 1214099.0197
97 | 2668515.515 | 1214296.205 | 2668511.0848 | 1214296.3875 | 2668503.3787 | 1214296.11 | 2668503.1453 | 1214299.8985 | 2668500.6052 | 1214299.9099
98 | 2668490.5985 | 1214250.9948 | 2668494.9627 | 1214258.8196
99 | 2668490.5985 | 1214250.9948 | 2668488.0388 | 1214246.4053
100 | 2668480.3163 | 1214232.5589 | 2668488.0388 | 1214246.4053
101 | 2668480.3163 | 1214232.5589 | 2668477.7343 | 1214227.9295
102 | 2668473.4288 | 1214220.2098 | 2668477.7343 | 1214227.9295
103 | 2668473.4288 | 1214220.2098 | 2668468.0744 | 1214210.6095
104 | 2668461.3201 | 1214198.4992 | 2668468.0744 | 1214210.6095
105 | 2668461.3201 | 1214198.4992 | 2668439.8745 | 1214215.9496
106 | 2668461.3201 | 1214198.4992 | 2668456.0259 | 1214186.8795
107 | 2668436.1179 | 1214217.7822 | 2668439.1698 | 1214216.523 | 2668439.8745 | 1214215.9496
108 | 2668451.874 | 1214177.7667 | 2668456.0259 | 1214186.8795
109 | 2668451.874 | 1214177.7667 | 2668444.4527 | 1214161.4845
110 | 2668451.874 | 1214177.7667 | 2668440.5059 | 1214181.8871
111 | 2668431.8963 | 1214137.89 | 2668438.5528 | 1214148.54 | 2668444.4527 | 1214161.4845
112 | 2668417.785 | 1214188.3822 | 2668431.4177 | 1214185.1811 | 2668440.5059 | 1214181.8871
113 | 2668518.858 | 1214343.1636 | 2668521.84 | 1214343.1149

## bus_geodata
| x | y | coords
0 | 2668567.091 | 1214301.0752
1 | 2668555.7587 | 1214282.6007
2 | 2668570.6784 | 1214306.9234
3 | 2668554.8991 | 1214281.1994
4 | 2668583.7284 | 1214321.3697
5 | 2668567.614 | 1214309.2007
6 | 2668545.8268 | 1214261.4154
7 | 2668583.8509 | 1214321.4721
8 | 2668544.2121 | 1214340.9628
9 | 2668545.5075 | 1214254.0279
10 | 2668604.7288 | 1214337.5323
11 | 2668550.9589 | 1214349.4063
12 | 2668536.3111 | 1214330.5543
13 | 2668547.9467 | 1214240.105
14 | 2668532.5153 | 1214342.9407
15 | 2668524.663 | 1214312.8776
16 | 2668583.9448 | 1214241.8018
17 | 2668580.6659 | 1214239.6183
18 | 2668589.8164 | 1214240.4574
19 | 2668563.1452 | 1214237.0784
20 | 2668604.1399 | 1214241.9008
21 | 2668549.2471 | 1214234.6874
22 | 2668615.8296 | 1214243.8587
23 | 2668557.4998 | 1214200.1205
24 | 2668642.7121 | 1214245.9395
25 | 2668612.97 | 1214279.2781
26 | 2668558.2172 | 1214196.9779
27 | 2668750.4279 | 1214253.7705
28 | 2668616.907 | 1214295.5701
29 | 2668447.0888 | 1214312.2711
30 | 2668447.0264 | 1214307.164
31 | 2668447.1931 | 1214320.8137
32 | 2668446.9641 | 1214302.0569
33 | 2668447.3436 | 1214332.9536
34 | 2668453.9145 | 1214316.8884
35 | 2668446.9191 | 1214298.3743
36 | 2668447.7979 | 1214370.0071
37 | 2668462.4905 | 1214299.6205
38 | 2668434.786 | 1214362.2051
39 | 2668471.985 | 1214297.7825
40 | 2668419.895 | 1214353.2764
41 | 2668479.5529 | 1214298.0153
42 | 2668344.9086 | 1214269.1373
43 | 2668353.0018 | 1214287.5814
44 | 2668334.7594 | 1214246.0077
45 | 2668354.8978 | 1214291.9024
46 | 2668312.7661 | 1214198.6294
47 | 2668380.6176 | 1214327.6432
48 | 2668316.0822 | 1214191.6074
49 | 2668290.5592 | 1214229.7051
50 | 2668372.7039 | 1214337.6501
51 | 2668325.524 | 1214214.3533
52 | 2668274.3808 | 1214269.6363
53 | 2668421.4779 | 1214349.7034
54 | 2668365.4739 | 1214346.726
55 | 2668358.9985 | 1214291.1912
56 | 2668346.3941 | 1214099.686
57 | 2668364.6453 | 1214149.4485
58 | 2668391.5278 | 1214079.7686
59 | 2668272.3984 | 1214301.9427
60 | 2668291.323 | 1214381.7786
61 | 2668301.1663 | 1214396.287
62 | 2668330.6192 | 1214383.9328
63 | 2668272.5303 | 1214302.683
64 | 2668355.9709 | 1214413.7369
65 | 2668389.6829 | 1214399.1082
66 | 2668357.7929 | 1214407.187
67 | 2668357.7914 | 1214376.1898
68 | 2668360.7142 | 1214354.7596
69 | 2668488.3986 | 1214367.5099
70 | 2668488.5159 | 1214362.4707
71 | 2668488.5824 | 1214359.6132
72 | 2668422.4549 | 1214393.2506
73 | 2668419.4188 | 1214390.862
74 | 2668414.0097 | 1214293.6271
75 | 2668387.7058 | 1214365.1111
76 | 2668391.5789 | 1214368.314
77 | 2668489.5065 | 1214299.9593
78 | 2668627.535 | 1214315.6805
79 | 2668488.748 | 1214352.3869
80 | 2668488.9481 | 1214343.6518
81 | 2668488.6325 | 1214357.4261
82 | 2668496.8905 | 1214343.5222
83 | 2668499.4502 | 1214343.4804
84 | 2668508.07 | 1214343.3397
85 | 2668510.729 | 1214343.2963
86 | 2668659.8208 | 1214184.6501
87 | 2668530.4842 | 1214184.7441
88 | 2668522.7903 | 1214211.4781
89 | 2668517.4279 | 1214230.1559
90 | 2668497.355 | 1214263.109
91 | 2668494.3083 | 1214299.9379
92 | 2668426.1345 | 1214131.4528
93 | 2668593.0813 | 1214096.6604
94 | 2668591.2198 | 1214099.0197
95 | 2668515.515 | 1214296.205
96 | 2668494.9627 | 1214258.8196
97 | 2668500.6051 | 1214299.9099
98 | 2668490.5985 | 1214250.9948
99 | 2668488.0388 | 1214246.4053
100 | 2668480.3163 | 1214232.5589
101 | 2668477.7343 | 1214227.9295
102 | 2668473.4288 | 1214220.2098
103 | 2668468.0744 | 1214210.6095
104 | 2668461.3201 | 1214198.4992
105 | 2668439.8745 | 1214215.9496
106 | 2668456.0259 | 1214186.8795
107 | 2668436.1179 | 1214217.7822
108 | 2668451.874 | 1214177.7667
109 | 2668444.4527 | 1214161.4845
110 | 2668440.5059 | 1214181.8871
111 | 2668521.84 | 1214343.1149
112 | 2668518.858 | 1214343.1636
113 | 2668431.8963 | 1214137.89
114 | 2668417.785 | 1214188.3822
115 | 2668447.1931 | 1214320.8137

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98496 | -0.28883 | 0.0024433 | 0.00061236
1 | 0.98401 | -0.30738 | 0.0027144 | 0.0006803
2 | 0.98528 | -0.28267 | 0 | 0
3 | 0.98394 | -0.30871 | 0.0033293 | 0.0008344
4 | 0.98515 | -0.28522 | 0.0025289 | 0.0006338
5 | 0.98548 | -0.27874 | 0.0055576 | 0.0013929
6 | 0.9831 | -0.32517 | 0.0024074 | 0.00060336
7 | 0.98515 | -0.28524 | 0.0025454 | 0.00063793
8 | 0.98821 | -0.2258 | 0 | 0
9 | 0.98283 | -0.3304 | 0.0023113 | 0.00057927
10 | 0.98509 | -0.28629 | 0.0022206 | 0.00055654
11 | 0.98818 | -0.22628 | 0.002492 | 0.00062454
12 | 0.989 | -0.21057 | 0 | 0
13 | 0.98235 | -0.33982 | 0.0023387 | 0.00058615
14 | 0.98858 | -0.21861 | 0.0029329 | 0.00073506
15 | 0.99089 | -0.17413 | 0.0028751 | 0.00072057
16 | 0.98126 | -0.36103 | 0.0023016 | 0.00057684
17 | 0.98135 | -0.35923 | 0.0011476 | 0.00028761
18 | 0.98112 | -0.3637 | 0.0014179 | 0.00035536
19 | 0.98178 | -0.35078 | 0.0029951 | 0.00075065
20 | 0.98084 | -0.36935 | 0.0022001 | 0.00055141
21 | 0.98217 | -0.3433 | 0 | 0
22 | 0.98062 | -0.37357 | 0 | 0
23 | 0.982 | -0.34657 | 0.0022997 | 0.00057636
24 | 0.98038 | -0.37827 | 0.0040235 | 0.0010084
25 | 0.98029 | -0.38014 | 0.0043117 | 0.0010806
26 | 0.98199 | -0.34674 | 0.0028042 | 0.00070281
27 | 0.97984 | -0.38886 | 0 | 0
28 | 0.98019 | -0.38196 | 0.0033992 | 0.00085192
29 | 0.99864 | -0.025783 | 0.0016756 | 0.00041994
30 | 0.99914 | -0.016344 | 0.0016737 | 0.00041948
31 | 0.99781 | -0.041509 | 0 | 0
32 | 0.99964 | -0.0068652 | 0.0016756 | 0.00041994
33 | 0.99631 | -0.069858 | 0.0016737 | 0.00041948
34 | 0.99737 | -0.049804 | 0.0050249 | 0.0012594
35 | 1 | 0 | -0.32714 | -0.083426
36 | 0.99179 | -0.15582 | 0 | 0
37 | 0.99621 | -0.071923 | 0.0025382 | 0.00063614
38 | 0.98993 | -0.19124 | 0.0019404 | 0.0004863
39 | 0.9956 | -0.083676 | 0.0023879 | 0.00059846
40 | 0.98785 | -0.23133 | 0 | 0
41 | 0.9952 | -0.091338 | 0.0024506 | 0.00061419
42 | 0.97901 | -0.40279 | 0.0028395 | 0.00071164
43 | 0.98002 | -0.38303 | 0.0040411 | 0.0010128
44 | 0.97781 | -0.42632 | 0.0041171 | 0.0010318
45 | 0.98028 | -0.37806 | 0.0028044 | 0.00070285
46 | 0.97552 | -0.47131 | 0 | 0
47 | 0.98279 | -0.32916 | 0 | 0
48 | 0.97527 | -0.47613 | 0 | 0
49 | 0.97502 | -0.48107 | 0.0079381 | 0.0019895
50 | 0.98214 | -0.34191 | 0.0030971 | 0.00077622
51 | 0.97449 | -0.49149 | 0.019192 | 0.0048099
52 | 0.97481 | -0.4852 | 0.0029945 | 0.00075049
53 | 0.9878 | -0.23226 | 0 | 0
54 | 0.98158 | -0.35287 | 0 | 0
55 | 0.97334 | -0.51415 | 0.014706 | 0.0036856
56 | 0.9864 | -0.26146 | 0 | 0
57 | 0.9862 | -0.26527 | 0.0040099 | 0.001005
58 | 0.98658 | -0.25792 | 0 | 0
59 | 0.97474 | -0.48653 | 0.001109 | 0.00027794
60 | 0.97942 | -0.39515 | 0.0060529 | 0.001517
61 | 0.97952 | -0.39322 | 0 | 0
62 | 0.97969 | -0.38971 | 0.0050629 | 0.0012689
63 | 0.97474 | -0.48655 | 0.0011087 | 0.00027786
64 | 0.97891 | -0.40503 | 0 | 0
65 | 0.97845 | -0.41415 | 0.010318 | 0.0025859
66 | 0.97898 | -0.40376 | 0.018502 | 0.004637
67 | 0.97999 | -0.38392 | 0 | 0
68 | 0.98099 | -0.3643 | 0.0032964 | 0.00082616
69 | 0.98768 | -0.23624 | 0.0017232 | 0.00043187
70 | 0.98769 | -0.23608 | 0.001727 | 0.00043282
71 | 0.98769 | -0.23591 | 0 | 0
72 | 0.98113 | -0.36165 | 0.0026184 | 0.00065624
73 | 0.98114 | -0.36147 | 0.0024147 | 0.00060519
74 | 0.987 | -0.24778 | 0.013355 | 0.0033472
75 | 0.98134 | -0.35757 | 0.0020121 | 0.00050429
76 | 0.9813 | -0.35821 | 0.0019603 | 0.00049129
77 | 0.99457 | -0.10338 | 0.0032068 | 0.00080371
78 | 0.98014 | -0.38298 | 0.0024855 | 0.00062293
79 | 0.98773 | -0.2353 | 0.001727 | 0.00043282
80 | 0.98778 | -0.23423 | 0.0033355 | 0.00083595
81 | 0.9877 | -0.23577 | 0.0017232 | 0.00043187
82 | 0.98786 | -0.23278 | 0.0031508 | 0.00078967
83 | 0.98789 | -0.23216 | 0.0033836 | 0.00084802
84 | 0.98802 | -0.22958 | 0.00295 | 0.00073934
85 | 0.98807 | -0.22864 | 0.0028826 | 0.00072244
86 | 0.9793 | -0.39952 | 0 | 0
87 | 0.98984 | -0.19445 | 0.0040392 | 0.0010123
88 | 0.98995 | -0.19245 | 0.0027861 | 0.00069826
89 | 0.99007 | -0.19009 | 0.0041668 | 0.0010443
90 | 0.99048 | -0.18216 | 0.0024069 | 0.00060323
91 | 0.99432 | -0.10809 | 0.002357 | 0.00059072
92 | 0.98682 | -0.25324 | 0.0045946 | 0.0011515
93 | 0.97871 | -0.4111 | 0 | 0
94 | 0.9787 | -0.41138 | 0.0050803 | 0.0012732
95 | 0.99263 | -0.14058 | 0 | 0
96 | 0.99026 | -0.18641 | 0.0024403 | 0.00061159
97 | 0.994 | -0.11418 | 0.0028267 | 0.00070844
98 | 0.98988 | -0.19379 | 0.0023155 | 0.00058032
99 | 0.98967 | -0.19791 | 0.0024837 | 0.00062248
100 | 0.98906 | -0.20963 | 0.0023305 | 0.00058407
101 | 0.98887 | -0.21333 | 0.0025948 | 0.00065033
102 | 0.98857 | -0.2191 | 0.0023278 | 0.00058339
103 | 0.98823 | -0.22582 | 0.0049287 | 0.0012352
104 | 0.98785 | -0.23308 | 0 | 0
105 | 0.98772 | -0.23567 | 0.0024174 | 0.00060586
106 | 0.98757 | -0.23858 | 0.0022712 | 0.00056922
107 | 0.98771 | -0.23589 | 0.0028311 | 0.00070954
108 | 0.98737 | -0.24248 | 0 | 0
109 | 0.98714 | -0.24693 | 0.0035008 | 0.00087739
110 | 0.98728 | -0.24419 | 0.0035716 | 0.00089512
111 | 0.98831 | -0.22402 | 0.0030472 | 0.00076371
112 | 0.98824 | -0.22536 | 0.0027197 | 0.00068162
113 | 0.98689 | -0.25191 | 0.0017834 | 0.00044697
114 | 0.98719 | -0.24603 | 0.0043469 | 0.0010894
115 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.047728 | 0.012016 | -0.047686 | -0.011989 | 4.2278e-05 | 2.6783e-05 | 0.072124 | 0.072124 | 0.072124 | 0.98496 | -0.28883 | 0.98401 | -0.30738 | 19.8144
1 | -0.050172 | -0.012629 | 0.050186 | 0.012638 | 1.4788e-05 | 9.3773e-06 | 0.075816 | 0.075815 | 0.075816 | 0.98496 | -0.28883 | 0.98528 | -0.28267 | 20.8284
2 | 0.044972 | 0.011309 | -0.044969 | -0.011307 | 2.8522e-06 | 1.8045e-06 | 0.06802 | 0.06802 | 0.06802 | 0.98401 | -0.30738 | 0.98394 | -0.30871 | 18.6867
3 | 0.0072959 | 0.0018283 | -0.007295 | -0.001828 | 8.884e-07 | 3.201e-07 | 0.011019 | 0.011019 | 0.011019 | 0.98528 | -0.28267 | 0.98515 | -0.28522 | 3.0271
4 | -0.057482 | -0.014466 | 0.057493 | 0.014473 | 1.0795e-05 | 6.8604e-06 | 0.086834 | 0.086834 | 0.086834 | 0.98528 | -0.28267 | 0.98548 | -0.27874 | 23.8555
5 | 0.041639 | 0.010473 | -0.041607 | -0.010452 | 3.2713e-05 | 2.0657e-05 | 0.062985 | 0.062985 | 0.062985 | 0.98394 | -0.30871 | 0.9831 | -0.32517 | 17.3035
6 | 0.0047661 | 0.0011942 | -0.0047661 | -0.0011942 | 3.1032e-09 | -4.7369e-11 | 0.0071989 | 0.0071989 | 0.0071989 | 0.98515 | -0.28522 | 0.98515 | -0.28524 | 1.9777
7 | -0.063051 | -0.015866 | 0.063211 | 0.015968 | 0.00015995 | 0.00010177 | 0.095226 | 0.095225 | 0.095226 | 0.98548 | -0.27874 | 0.98821 | -0.2258 | 26.1609
8 | 0.039199 | 0.0098489 | -0.039189 | -0.0098428 | 9.7776e-06 | 6.1638e-06 | 0.059341 | 0.059341 | 0.059341 | 0.9831 | -0.32517 | 0.98283 | -0.3304 | 16.3025
9 | 0.0022208 | 0.00055628 | -0.0022206 | -0.00055654 | 1.1121e-07 | -2.6441e-07 | 0.0033542 | 0.0033544 | 0.0033544 | 0.98515 | -0.28524 | 0.98509 | -0.28629 | 0.92153
10 | 0.002492 | 0.00062444 | -0.002492 | -0.00062454 | 5.7078e-08 | -1.0196e-07 | 0.0037524 | 0.0037524 | 0.0037524 | 0.98821 | -0.2258 | 0.98818 | -0.22628 | 1.0309
11 | -0.065703 | -0.016592 | 0.065751 | 0.016623 | 4.7971e-05 | 3.0534e-05 | 0.098978 | 0.098978 | 0.098978 | 0.98821 | -0.2258 | 0.989 | -0.21057 | 27.1917
12 | 0.036878 | 0.0092635 | -0.036862 | -0.0092531 | 1.6584e-05 | 1.0434e-05 | 0.055842 | 0.055842 | 0.055842 | 0.98283 | -0.3304 | 0.98235 | -0.33982 | 15.3411
13 | 0.031332 | 0.0078627 | -0.03132 | -0.0078552 | 1.2007e-05 | 7.4998e-06 | 0.047144 | 0.047145 | 0.047145 | 0.989 | -0.21057 | 0.98858 | -0.21861 | 12.9518
14 | -0.097082 | -0.024486 | 0.097252 | 0.024594 | 0.00016969 | 0.00010833 | 0.14612 | 0.14612 | 0.14612 | 0.989 | -0.21057 | 0.99089 | -0.17413 | 40.1434
15 | 0.034523 | 0.0086669 | -0.034517 | -0.0086633 | 5.7147e-06 | 3.5869e-06 | 0.052299 | 0.052299 | 0.052299 | 0.98235 | -0.33982 | 0.98217 | -0.3433 | 14.3679
16 | 0.028387 | 0.0071202 | -0.02838 | -0.0071156 | 7.3103e-06 | 4.5417e-06 | 0.04273 | 0.04273 | 0.04273 | 0.98858 | -0.21861 | 0.98831 | -0.22402 | 11.739
17 | -0.10013 | -0.025314 | 0.10029 | 0.025417 | 0.0001614 | 0.00010305 | 0.15044 | 0.15044 | 0.15044 | 0.99089 | -0.17413 | 0.99263 | -0.14058 | 41.3296
18 | -0.025246 | -0.0063314 | 0.025248 | 0.0063327 | 2.1654e-06 | 1.3361e-06 | 0.038286 | 0.038286 | 0.038286 | 0.98126 | -0.36103 | 0.98135 | -0.35923 | 10.5181
19 | 0.022945 | 0.0057546 | -0.022942 | -0.0057528 | 2.917e-06 | 1.7857e-06 | 0.034796 | 0.034796 | 0.034796 | 0.98126 | -0.36103 | 0.98112 | -0.3637 | 9.5592
20 | -0.026396 | -0.0066203 | 0.026407 | 0.0066269 | 1.0636e-05 | 6.5833e-06 | 0.040026 | 0.040026 | 0.040026 | 0.98135 | -0.35923 | 0.98178 | -0.35078 | 10.9961
21 | 0.021524 | 0.0053974 | -0.021518 | -0.0053939 | 5.7897e-06 | 3.5225e-06 | 0.032645 | 0.032645 | 0.032645 | 0.98112 | -0.3637 | 0.98084 | -0.36935 | 8.9685
22 | -0.029402 | -0.0073776 | 0.029412 | 0.0073841 | 1.0503e-05 | 6.5436e-06 | 0.044565 | 0.044565 | 0.044565 | 0.98178 | -0.35078 | 0.98217 | -0.3433 | 12.2432
23 | 0.019318 | 0.0048425 | -0.019314 | -0.0048401 | 3.8904e-06 | 2.3374e-06 | 0.029307 | 0.029307 | 0.029307 | 0.98084 | -0.36935 | 0.98062 | -0.37357 | 8.0515
24 | 0.0051048 | 0.0012792 | -0.005104 | -0.0012791 | 7.9713e-07 | 6.0476e-08 | 0.0077338 | 0.007734 | 0.007734 | 0.98217 | -0.3433 | 0.982 | -0.34657 | 2.1247
25 | 0.0091138 | 0.0022832 | -0.0091118 | -0.0022822 | 2.0393e-06 | 9.4649e-07 | 0.013829 | 0.013829 | 0.013829 | 0.98062 | -0.37357 | 0.98038 | -0.37827 | 3.7993
26 | 0.0102 | 0.002557 | -0.010197 | -0.0025554 | 3.1925e-06 | 1.5951e-06 | 0.015478 | 0.015478 | 0.015478 | 0.98062 | -0.37357 | 0.98029 | -0.38014 | 4.2523
27 | 0.0028043 | 0.00070278 | -0.0028042 | -0.00070281 | 2.1826e-08 | -2.6811e-08 | 0.0042493 | 0.0042493 | 0.0042493 | 0.982 | -0.34657 | 0.98199 | -0.34674 | 1.1674
28 | 0.0050883 | 0.0012739 | -0.0050857 | -0.0012737 | 2.5645e-06 | 1.962e-07 | 0.0077225 | 0.007723 | 0.007723 | 0.98038 | -0.37827 | 0.97984 | -0.38886 | 2.1217
29 | 0.0058853 | 0.0014747 | -0.0058848 | -0.0014746 | 5.0845e-07 | 1.1125e-07 | 0.0089335 | 0.0089336 | 0.0089336 | 0.98029 | -0.38014 | 0.98019 | -0.38196 | 2.4543
30 | 0.0050857 | 0.0012737 | -0.0050831 | -0.0012735 | 2.5808e-06 | 1.9926e-07 | 0.007723 | 0.0077235 | 0.0077235 | 0.97984 | -0.38886 | 0.9793 | -0.39952 | 2.1218
31 | 0.0024856 | 0.00062272 | -0.0024855 | -0.00062293 | 1.2148e-07 | -2.0901e-07 | 0.0037733 | 0.0037734 | 0.0037734 | 0.98019 | -0.38196 | 0.98014 | -0.38298 | 1.0367
32 | -0.32174 | -0.082328 | 0.32188 | 0.082422 | 0.0001471 | 9.3941e-05 | 0.48 | 0.48 | 0.48 | 0.99864 | -0.025783 | 0.99914 | -0.016344 | 43.9563
33 | 0.32006 | 0.081908 | -0.31982 | -0.081753 | 0.0002435 | 0.0001555 | 0.47751 | 0.47751 | 0.47751 | 0.99864 | -0.025783 | 0.99781 | -0.041509 | 43.7277
34 | -0.32356 | -0.082842 | 0.32371 | 0.082937 | 0.00014863 | 9.4921e-05 | 0.4825 | 0.4825 | 0.4825 | 0.99914 | -0.016344 | 0.99964 | -0.0068652 | 44.1846
35 | 0.13552 | 0.034876 | -0.13534 | -0.034757 | 0.00018656 | 0.00011924 | 0.20243 | 0.20243 | 0.20243 | 0.99781 | -0.041509 | 0.99631 | -0.069858 | 55.6121
36 | 0.18429 | 0.046877 | -0.18422 | -0.04683 | 7.3622e-05 | 4.6813e-05 | 0.27508 | 0.27508 | 0.27508 | 0.99781 | -0.041509 | 0.99737 | -0.049804 | 25.1904
37 | -0.32538 | -0.083357 | 0.32549 | 0.083426 | 0.00010828 | 6.9157e-05 | 0.48499 | 0.48499 | 0.48499 | 0.99964 | -0.0068652 | 1 | 0 | 44.413
38 | 0.13366 | 0.034338 | -0.13311 | -0.033983 | 0.00055545 | 0.000355 | 0.19993 | 0.19993 | 0.19993 | 0.99631 | -0.069858 | 0.99179 | -0.15582 | 54.9254
39 | 0.1792 | 0.04557 | -0.179 | -0.045449 | 0.00019075 | 0.00012124 | 0.26758 | 0.26758 | 0.26758 | 0.99737 | -0.049804 | 0.99621 | -0.071923 | 24.5039
40 | 0.13311 | 0.033983 | -0.13288 | -0.033837 | 0.00022741 | 0.00014535 | 0.19993 | 0.19993 | 0.19993 | 0.99179 | -0.15582 | 0.98993 | -0.19124 | 54.9254
41 | 0.17647 | 0.044813 | -0.17637 | -0.04475 | 9.9752e-05 | 6.3394e-05 | 0.26379 | 0.26379 | 0.26379 | 0.99621 | -0.071923 | 0.9956 | -0.083676 | 24.1567
42 | 0.13094 | 0.033351 | -0.13069 | -0.033189 | 0.00025272 | 0.00016152 | 0.19701 | 0.19701 | 0.19701 | 0.98993 | -0.19124 | 0.98785 | -0.23133 | 54.1241
43 | 0.17398 | 0.044151 | -0.17391 | -0.04411 | 6.4089e-05 | 4.0722e-05 | 0.26022 | 0.26022 | 0.26022 | 0.9956 | -0.083676 | 0.9952 | -0.091338 | 23.8299
44 | 0.013366 | 0.003353 | -0.013365 | -0.0033527 | 5.9396e-07 | 3.3012e-07 | 0.020134 | 0.020134 | 0.020134 | 0.98785 | -0.23133 | 0.9878 | -0.23226 | 5.5315
45 | 0.11732 | 0.029836 | -0.11677 | -0.029485 | 0.00055013 | 0.00035149 | 0.17688 | 0.17688 | 0.17688 | 0.98785 | -0.23133 | 0.98279 | -0.32916 | 48.5928
46 | 0.17146 | 0.043496 | -0.17136 | -0.043433 | 9.9225e-05 | 6.3034e-05 | 0.25656 | 0.25656 | 0.25656 | 0.9952 | -0.091338 | 0.99457 | -0.10338 | 23.4944
47 | -0.054219 | -0.013668 | 0.054271 | 0.013701 | 5.1331e-05 | 3.2598e-05 | 0.082438 | 0.082438 | 0.082438 | 0.97901 | -0.40279 | 0.98002 | -0.38303 | 22.6477
48 | 0.05138 | 0.012957 | -0.051322 | -0.01292 | 5.7808e-05 | 3.668e-05 | 0.078122 | 0.078122 | 0.078122 | 0.97901 | -0.40279 | 0.97781 | -0.42632 | 21.4621
49 | -0.058312 | -0.014714 | 0.058326 | 0.014723 | 1.3882e-05 | 8.8251e-06 | 0.088573 | 0.088573 | 0.088573 | 0.98002 | -0.38303 | 0.98028 | -0.37806 | 24.3334
50 | 0.047205 | 0.011888 | -0.047104 | -0.011824 | 0.00010131 | 6.4181e-05 | 0.071857 | 0.071857 | 0.071857 | 0.97781 | -0.42632 | 0.97552 | -0.47131 | 19.7409
51 | -0.06113 | -0.015426 | 0.061274 | 0.015517 | 0.00014351 | 9.1288e-05 | 0.09283 | 0.09283 | 0.09283 | 0.98028 | -0.37806 | 0.98279 | -0.32916 | 25.5028
52 | 0.033946 | 0.0085252 | -0.033938 | -0.0085203 | 7.8072e-06 | 4.8997e-06 | 0.051787 | 0.051787 | 0.051787 | 0.97552 | -0.47131 | 0.97527 | -0.47613 | 14.2271
53 | 0.013158 | 0.003299 | -0.013151 | -0.0032956 | 6.1179e-06 | 3.4101e-06 | 0.020071 | 0.020071 | 0.020071 | 0.97552 | -0.47131 | 0.97502 | -0.48107 | 5.5139
54 | 0.055497 | 0.013968 | -0.055463 | -0.013947 | 3.3796e-05 | 2.1468e-05 | 0.084048 | 0.084048 | 0.084048 | 0.98279 | -0.32916 | 0.98214 | -0.34191 | 23.09
55 | 0.033938 | 0.0085203 | -0.033914 | -0.0085047 | 2.4845e-05 | 1.5593e-05 | 0.051787 | 0.051787 | 0.051787 | 0.97527 | -0.47613 | 0.97449 | -0.49149 | 14.2271
56 | 0.0052133 | 0.0013061 | -0.0052123 | -0.001306 | 1.0258e-06 | 1.1765e-07 | 0.007956 | 0.0079562 | 0.0079562 | 0.97502 | -0.48107 | 0.97481 | -0.4852 | 2.1858
57 | 0.052366 | 0.01317 | -0.052339 | -0.013153 | 2.7402e-05 | 1.739e-05 | 0.079355 | 0.079355 | 0.079355 | 0.98214 | -0.34191 | 0.98158 | -0.35287 | 21.8009
58 | 0.014722 | 0.0036948 | -0.014706 | -0.0036856 | 1.5893e-05 | 9.1282e-06 | 0.022482 | 0.022482 | 0.022482 | 0.97449 | -0.49149 | 0.97334 | -0.51415 | 6.1763
59 | 0.0022178 | 0.00055547 | -0.0022176 | -0.00055579 | 1.4025e-07 | -3.1706e-07 | 0.0033852 | 0.0033854 | 0.0033854 | 0.97481 | -0.4852 | 0.97474 | -0.48653 | 0.93005
60 | 0.013365 | 0.0033527 | -0.013355 | -0.0033472 | 9.8782e-06 | 5.4909e-06 | 0.020134 | 0.020135 | 0.020135 | 0.9878 | -0.23226 | 0.987 | -0.24778 | 5.5315
61 | 0.0090086 | 0.002258 | -0.0090066 | -0.0022571 | 2.0177e-06 | 9.2674e-07 | 0.013657 | 0.013657 | 0.013657 | 0.98158 | -0.35287 | 0.98134 | -0.35757 | 3.7518
62 | 0.04333 | 0.010895 | -0.043306 | -0.01088 | 2.3641e-05 | 1.4946e-05 | 0.065699 | 0.065699 | 0.065699 | 0.98158 | -0.35287 | 0.98099 | -0.3643 | 18.0491
63 | 0.0040106 | 0.0010048 | -0.0040099 | -0.001005 | 7.2742e-07 | -2.1076e-07 | 0.0060501 | 0.0060503 | 0.0060503 | 0.9864 | -0.26146 | 0.9862 | -0.26527 | 1.6622
64 | -0.0040106 | -0.0010048 | 0.0040113 | 0.0010046 | 6.7551e-07 | -1.9601e-07 | 0.0060501 | 0.0060498 | 0.0060501 | 0.9864 | -0.26146 | 0.98658 | -0.25792 | 1.6621
65 | -0.0040113 | -0.0010046 | 0.0040122 | 0.0010043 | 8.9375e-07 | -2.5976e-07 | 0.0060498 | 0.0060495 | 0.0060498 | 0.98658 | -0.25792 | 0.98682 | -0.25324 | 1.662
66 | 0.0011087 | 0.00027785 | -0.0011087 | -0.00027786 | 8.077e-10 | -8.8564e-09 | 0.0016925 | 0.0016925 | 0.0016925 | 0.97474 | -0.48653 | 0.97474 | -0.48655 | 0.46496
67 | -0.0060529 | -0.001517 | 0.0060534 | 0.0015171 | 5.5804e-07 | 1.3567e-07 | 0.0091961 | 0.009196 | 0.0091961 | 0.97942 | -0.39515 | 0.97952 | -0.39322 | 2.5264
68 | -0.0060534 | -0.0015171 | 0.0060544 | 0.0015174 | 1.0131e-06 | 2.4619e-07 | 0.009196 | 0.0091958 | 0.009196 | 0.97952 | -0.39322 | 0.97969 | -0.38971 | 2.5264
69 | -0.011117 | -0.0027863 | 0.01112 | 0.0027879 | 3.0662e-06 | 1.6011e-06 | 0.016886 | 0.016886 | 0.016886 | 0.97969 | -0.38971 | 0.97999 | -0.38392 | 4.6389
70 | 0.010322 | 0.0025882 | -0.010318 | -0.0025859 | 4.4834e-06 | 2.2592e-06 | 0.015691 | 0.015692 | 0.015692 | 0.97891 | -0.40503 | 0.97845 | -0.41415 | 4.3109
71 | -0.010322 | -0.0025882 | 0.010323 | 0.0025885 | 6.2772e-07 | 3.1627e-07 | 0.015691 | 0.015691 | 0.015691 | 0.97891 | -0.40503 | 0.97898 | -0.40376 | 4.3108
72 | -0.028825 | -0.0072255 | 0.028852 | 0.0072425 | 2.7276e-05 | 1.698e-05 | 0.043813 | 0.043813 | 0.043813 | 0.97898 | -0.40376 | 0.97999 | -0.38392 | 12.0366
73 | -0.039973 | -0.01003 | 0.04001 | 0.010054 | 3.7432e-05 | 2.3615e-05 | 0.060699 | 0.060699 | 0.060699 | 0.97999 | -0.38392 | 0.98099 | -0.3643 | 16.6755
74 | -0.0017232 | -0.00043187 | 0.0017232 | 0.00043182 | 1.274e-08 | -5.6355e-08 | 0.0025961 | 0.0025961 | 0.0025961 | 0.98768 | -0.23624 | 0.98769 | -0.23608 | 0.71322
75 | -0.0034502 | -0.00086464 | 0.0034502 | 0.00086462 | 2.896e-08 | -1.8047e-08 | 0.0051979 | 0.0051979 | 0.0051979 | 0.98769 | -0.23608 | 0.98769 | -0.23591 | 1.428
76 | -0.0034502 | -0.00086462 | 0.0034502 | 0.0008646 | 2.2164e-08 | -1.3813e-08 | 0.0051979 | 0.0051979 | 0.0051979 | 0.98769 | -0.23591 | 0.9877 | -0.23577 | 1.428
77 | -0.0026184 | -0.00065624 | 0.0026184 | 0.0006562 | 2.2846e-08 | -3.4165e-08 | 0.0039712 | 0.0039712 | 0.0039712 | 0.98113 | -0.36165 | 0.98114 | -0.36147 | 1.091
78 | -0.0050332 | -0.0012614 | 0.0050339 | 0.0012614 | 7.8286e-07 | 4.8477e-08 | 0.0076334 | 0.0076332 | 0.0076334 | 0.98114 | -0.36147 | 0.9813 | -0.35821 | 2.0971
79 | 0.0069944 | 0.0017528 | -0.0069942 | -0.0017527 | 2.1199e-07 | 7.218e-08 | 0.010606 | 0.010606 | 0.010606 | 0.98134 | -0.35757 | 0.9813 | -0.35821 | 2.9137
80 | 0.16816 | 0.042629 | -0.16812 | -0.042605 | 3.8045e-05 | 2.4162e-05 | 0.25176 | 0.25176 | 0.25176 | 0.99457 | -0.10338 | 0.99432 | -0.10809 | 23.055
81 | -0.0069005 | -0.0017293 | 0.0069009 | 0.0017294 | 3.5409e-07 | 1.1478e-07 | 0.010396 | 0.010396 | 0.010396 | 0.98773 | -0.2353 | 0.98778 | -0.23423 | 2.8559
82 | 0.0051735 | 0.0012965 | -0.0051734 | -0.0012965 | 1.1482e-07 | 8.9724e-09 | 0.0077939 | 0.007794 | 0.007794 | 0.98773 | -0.2353 | 0.9877 | -0.23577 | 2.1412
83 | -0.010236 | -0.0025654 | 0.010237 | 0.0025657 | 7.0831e-07 | 3.5163e-07 | 0.01542 | 0.01542 | 0.01542 | 0.98778 | -0.23423 | 0.98786 | -0.23278 | 4.2363
84 | -0.013388 | -0.0033554 | 0.013388 | 0.0033556 | 3.9043e-07 | 2.171e-07 | 0.020166 | 0.020166 | 0.020166 | 0.98786 | -0.23278 | 0.98789 | -0.23216 | 5.5402
85 | -0.016772 | -0.0042036 | 0.016774 | 0.0042048 | 2.0632e-06 | 1.2101e-06 | 0.025263 | 0.025263 | 0.025263 | 0.98789 | -0.23216 | 0.98802 | -0.22958 | 6.9404
86 | -0.019724 | -0.0049442 | 0.019725 | 0.0049447 | 8.8003e-07 | 5.2916e-07 | 0.029706 | 0.029706 | 0.029706 | 0.98802 | -0.22958 | 0.98807 | -0.22864 | 8.1609
87 | -0.022607 | -0.0056671 | 0.022611 | 0.0056693 | 3.5341e-06 | 2.1577e-06 | 0.034047 | 0.034047 | 0.034047 | 0.98807 | -0.22864 | 0.98824 | -0.22536 | 9.3535
88 | 0.0050831 | 0.0012735 | -0.0050803 | -0.0012732 | 2.8026e-06 | 2.1842e-07 | 0.0077235 | 0.0077241 | 0.0077241 | 0.9793 | -0.39952 | 0.97871 | -0.4111 | 2.122
89 | -0.0040392 | -0.0010123 | 0.0040396 | 0.0010122 | 3.8465e-07 | -1.1148e-07 | 0.006072 | 0.0060719 | 0.006072 | 0.98984 | -0.19445 | 0.98995 | -0.19245 | 1.6681
90 | -0.0068256 | -0.0017105 | 0.0068264 | 0.0017107 | 7.6705e-07 | 2.4104e-07 | 0.01026 | 0.01026 | 0.01026 | 0.98995 | -0.19245 | 0.99007 | -0.19009 | 2.8186
91 | -0.010993 | -0.002755 | 0.010997 | 0.0027571 | 4.1578e-06 | 2.1384e-06 | 0.016522 | 0.016522 | 0.016522 | 0.99007 | -0.19009 | 0.99048 | -0.18216 | 4.539
92 | -0.062269 | -0.015648 | 0.062393 | 0.015726 | 0.00012386 | 7.8783e-05 | 0.093563 | 0.093563 | 0.093563 | 0.99048 | -0.18216 | 0.99263 | -0.14058 | 25.7041
93 | 0.048865 | 0.012287 | -0.048855 | -0.012281 | 9.9295e-06 | 6.2917e-06 | 0.073425 | 0.073425 | 0.073425 | 0.99048 | -0.18216 | 0.99026 | -0.18641 | 20.1717
94 | 0.16576 | 0.042015 | -0.16571 | -0.041984 | 4.8502e-05 | 3.0796e-05 | 0.24823 | 0.24823 | 0.24823 | 0.99432 | -0.10809 | 0.994 | -0.11418 | 22.732
95 | -0.0086068 | -0.0021558 | 0.0086073 | 0.0021561 | 5.4774e-07 | 2.3975e-07 | 0.012978 | 0.012978 | 0.012978 | 0.98682 | -0.25324 | 0.98689 | -0.25191 | 3.5653
96 | 0.0050803 | 0.0012732 | -0.0050803 | -0.0012732 | 6.7238e-08 | 5.2663e-09 | 0.0077241 | 0.0077241 | 0.0077241 | 0.97871 | -0.4111 | 0.9787 | -0.41138 | 2.122
97 | -0.16268 | -0.041144 | 0.16289 | 0.041275 | 0.00020631 | 0.00013156 | 0.244 | 0.244 | 0.244 | 0.99263 | -0.14058 | 0.994 | -0.11418 | 33.5168
98 | 0.046415 | 0.011669 | -0.046398 | -0.011659 | 1.635e-05 | 1.0349e-05 | 0.069758 | 0.069758 | 0.069758 | 0.99026 | -0.18641 | 0.98988 | -0.19379 | 19.1644
99 | 0.044083 | 0.011079 | -0.044074 | -0.011073 | 8.6564e-06 | 5.4726e-06 | 0.066278 | 0.066278 | 0.066278 | 0.98988 | -0.19379 | 0.98967 | -0.19791 | 18.2081
100 | 0.04159 | 0.010451 | -0.041567 | -0.010436 | 2.3256e-05 | 1.468e-05 | 0.062543 | 0.062543 | 0.062543 | 0.98967 | -0.19791 | 0.98906 | -0.20963 | 17.1822
101 | 0.039237 | 0.0098519 | -0.03923 | -0.0098476 | 6.9282e-06 | 4.366e-06 | 0.059037 | 0.059037 | 0.059037 | 0.98906 | -0.20963 | 0.98887 | -0.21333 | 16.219
102 | 0.036635 | 0.0091972 | -0.036625 | -0.0091909 | 1.0075e-05 | 6.3348e-06 | 0.055132 | 0.055133 | 0.055133 | 0.98887 | -0.21333 | 0.98857 | -0.2191 | 15.1463
103 | 0.034297 | 0.0086075 | -0.034286 | -0.0086006 | 1.0988e-05 | 6.8913e-06 | 0.051629 | 0.051629 | 0.051629 | 0.98857 | -0.2191 | 0.98823 | -0.22582 | 14.1837
104 | 0.029357 | 0.0073654 | -0.029347 | -0.0073591 | 1.0162e-05 | 6.3262e-06 | 0.044207 | 0.044208 | 0.044208 | 0.98823 | -0.22582 | 0.98785 | -0.23308 | 12.1449
105 | 0.0052492 | 0.0013154 | -0.0052485 | -0.0013154 | 6.4821e-07 | 6.0933e-08 | 0.0079069 | 0.007907 | 0.007907 | 0.98785 | -0.23308 | 0.98772 | -0.23567 | 2.1722
106 | 0.024098 | 0.0060436 | -0.024092 | -0.0060398 | 6.3098e-06 | 3.8749e-06 | 0.036301 | 0.036301 | 0.036301 | 0.98785 | -0.23308 | 0.98757 | -0.23858 | 9.9727
107 | 0.0028311 | 0.0007095 | -0.0028311 | -0.00070954 | 2.8719e-08 | -3.5503e-08 | 0.0042651 | 0.0042651 | 0.0042651 | 0.98772 | -0.23567 | 0.98771 | -0.23589 | 1.1717
108 | 0.021821 | 0.0054705 | -0.021816 | -0.0054681 | 4.0595e-06 | 2.47e-06 | 0.032879 | 0.032879 | 0.032879 | 0.98757 | -0.23858 | 0.98737 | -0.24248 | 9.0326
109 | 0.013897 | 0.0034833 | -0.013894 | -0.0034817 | 2.9433e-06 | 1.6549e-06 | 0.020944 | 0.020944 | 0.020944 | 0.98737 | -0.24248 | 0.98714 | -0.24693 | 5.7538
110 | 0.0079195 | 0.0019848 | -0.0079189 | -0.0019845 | 6.4591e-07 | 2.5874e-07 | 0.011935 | 0.011935 | 0.011935 | 0.98737 | -0.24248 | 0.98728 | -0.24419 | 3.2789
111 | 0.010393 | 0.0026043 | -0.010391 | -0.002603 | 2.4653e-06 | 1.2354e-06 | 0.015666 | 0.015667 | 0.015667 | 0.98714 | -0.24693 | 0.98689 | -0.25191 | 4.304
112 | 0.0043473 | 0.0010894 | -0.0043469 | -0.0010894 | 3.8107e-07 | -5.8776e-08 | 0.0065521 | 0.0065522 | 0.0065522 | 0.98728 | -0.24419 | 0.98719 | -0.24603 | 1.8001
113 | 0.025332 | 0.0063519 | -0.025331 | -0.0063509 | 1.6271e-06 | 1.0031e-06 | 0.038142 | 0.038142 | 0.038142 | 0.98831 | -0.22402 | 0.98824 | -0.22536 | 10.4786

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.32838 | 0.083736

## res_load
| p_mw | q_mvar
0 | 0.0024433 | 0.00061236
1 | 0.0027144 | 0.0006803
2 | 0.0033293 | 0.0008344
3 | 0.0025289 | 0.0006338
4 | 0.0055576 | 0.0013929
5 | 0.0024074 | 0.00060336
6 | 0.0025454 | 0.00063793
7 | 0.0023113 | 0.00057927
8 | 0.0022206 | 0.00055654
9 | 0.002492 | 0.00062454
10 | 0.0023387 | 0.00058615
11 | 0.0029329 | 0.00073506
12 | 0.0028751 | 0.00072057
13 | 0.0023016 | 0.00057684
14 | 0.0011476 | 0.00028761
15 | 0.0014179 | 0.00035536
16 | 0.0029951 | 0.00075065
17 | 0.0022001 | 0.00055141
18 | 0.0022997 | 0.00057636
19 | 0.0040235 | 0.0010084
20 | 0.0043117 | 0.0010806
21 | 0.0028042 | 0.00070281
22 | 0.0033992 | 0.00085192
23 | 0.0016756 | 0.00041994
24 | 0.0016737 | 0.00041948
25 | 0.0016756 | 0.00041994
26 | 0.0016737 | 0.00041948
27 | 0.0050249 | 0.0012594
28 | 0.0012391 | 0.00031056
29 | 0.0025382 | 0.00063614
30 | 0.0019404 | 0.0004863
31 | 0.0023879 | 0.00059846
32 | 0.0024506 | 0.00061419
33 | 0.0028395 | 0.00071164
34 | 0.0040411 | 0.0010128
35 | 0.0041171 | 0.0010318
36 | 0.0028044 | 0.00070285
37 | 0.0079381 | 0.0019895
38 | 0.0030971 | 0.00077622
39 | 0.019192 | 0.0048099
40 | 0.0029945 | 0.00075049
41 | 0.014706 | 0.0036856
42 | 0.0040099 | 0.001005
43 | 0.001109 | 0.00027794
44 | 0.0060529 | 0.001517
45 | 0.0050629 | 0.0012689
46 | 0.0011087 | 0.00027786
47 | 0.010318 | 0.0025859
48 | 0.018502 | 0.004637
49 | 0.0032964 | 0.00082616
50 | 0.0017232 | 0.00043187
51 | 0.001727 | 0.00043282
52 | 0.0026184 | 0.00065624
53 | 0.0024147 | 0.00060519
54 | 0.013355 | 0.0033472
55 | 0.0020121 | 0.00050429
56 | 0.0019603 | 0.00049129
57 | 0.0032068 | 0.00080371
58 | 0.0024855 | 0.00062293
59 | 0.001727 | 0.00043282
60 | 0.0033355 | 0.00083595
61 | 0.0017232 | 0.00043187
62 | 0.0031508 | 0.00078967
63 | 0.0033836 | 0.00084802
64 | 0.00295 | 0.00073934
65 | 0.0028826 | 0.00072244
66 | 0.0040392 | 0.0010123
67 | 0.0027861 | 0.00069826
68 | 0.0041668 | 0.0010443
69 | 0.0024069 | 0.00060323
70 | 0.002357 | 0.00059072
71 | 0.0045946 | 0.0011515
72 | 0.0050803 | 0.0012732
73 | 0.0024403 | 0.00061159
74 | 0.0028267 | 0.00070844
75 | 0.0023155 | 0.00058032
76 | 0.0024837 | 0.00062248
77 | 0.0023305 | 0.00058407
78 | 0.0025948 | 0.00065033
79 | 0.0023278 | 0.00058339
80 | 0.0049287 | 0.0012352
81 | 0.0024174 | 0.00060586
82 | 0.0022712 | 0.00056922
83 | 0.0028311 | 0.00070954
84 | 0.0035008 | 0.00087739
85 | 0.0035716 | 0.00089512
86 | 0.0030472 | 0.00076371
87 | 0.0027197 | 0.00068162
88 | 0.0017834 | 0.00044697
89 | 0.0043469 | 0.0010894

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1